## CM
Assign | Work Order | Asset Number | Asset Group | Description | Target Time | Contractor | Parent Asset Group | Creation Date & Time | Target Response Date & Time | Target Resolution Date & Time | Target Duration (Hours) | Actual Response Date & Time | Actual Resolution Date & Time | Actual Duration (Minutes) | Actual Operation Time(Minutes) | Technicians Count | Owning Department | Work Order Department | Status | Priority | Location | Life & Safety Asset | Failure Code | Cause Code | Resolution Code | Created By | Last updated by | Update Work Order | Complete Work Order | Requestor Staff Id | Requestor Name | QA Review Comments | Remarks | Mode of Reporting
| CM-2022-10910218 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO COLD (MIST FORMING ON GLASS AFFECTING VISIBILITY) - (RAMP CONTROL TOWER) CONCOURSE A-FIFTH FLOOR AREA 01 |  | FM008 |  | 2022-08-05 21:49 | 2022-08-05 22:49 | 2022-08-06 22:49 | 24 | 2022-08-05 21:58 | 2022-08-05 23:55 | 117 | 57 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 55709 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10912161 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO WARM A5-01-02 |  | FM008 |  | 2022-08-06 05:31 | 2022-08-06 06:31 | 2022-08-07 06:31 | 24 | 2022-08-06 05:40 | 2022-08-06 08:00 | 140 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 55709 |  |  | 55137 | Lazaro, Mr. Mark Anthony Jocson | N - - - |  | Voice Communication
| CM-2022-11260138 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | RAMP CONTROL TOWER A 6TH FLOOR - AC TOO COLD |  | FM008 |  | 2022-12-11 01:53 | 2022-12-11 02:53 | 2022-12-12 02:53 | 24 | 2022-12-11 02:05 | 2022-12-11 03:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 89127 | 17053 |  |  | 60309 | Tuwei, Ms. Vivian Cheptoo | N - - - |  | Voice Communication
| CM-2023-12273960 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM AHU – RCT CON A |  | FM008 |  | 2023-10-10 08:50 | 2023-10-10 09:50 | 2023-10-11 09:50 | 24 | 2023-10-10 08:55 | 2023-10-10 12:30 | 215 | 645 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12507897 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AHU HEATER NOT WORKING :AHU-A1121-701 |  | FM008 |  | 2023-12-27 12:18 | 2023-12-27 13:18 | 2023-12-28 13:18 | 24 | 2023-12-27 12:25 | 2023-12-27 15:10 | 165 | 330 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2022-10913809 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO COLD (MIST FORMING ON GLASS AFFECTING VISIBILITY) - (RAMP CONTROL TOWER) CONCOURSE A-FIFTH FLOOR AREA 01 |  | FM008 |  | 2022-08-05 00:01 | 2022-08-05 01:01 | 2022-08-06 01:01 | 24 | 2022-08-05 00:05 | 2022-08-05 01:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 55709 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-11007931 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO HOT RAMP CONTROL TOWER - A |  | FM008 |  | 2022-09-11 05:30 | 2022-09-11 06:30 | 2022-09-12 06:30 | 24 | 2022-09-11 05:35 | 2022-09-11 08:00 | 145 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | 55084 | Onyango, Ms. Mary Emma | N - - - |  | Voice Communication
| CM-2023-11998116 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC IS TOO COLD-ROOM 2137(TAG NO: A6-01-01 (RAMP CONTROL TOWER))-CONCOURSE A-SIXTH FLOOR AREA 01 |  | FM008 |  | 2023-07-22 02:19 | 2023-07-22 03:19 | 2023-07-23 03:19 | 24 | 2023-07-22 02:29 | 2023-07-22 06:00 | 211 | 51 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 17053 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2024-12577298 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | FOUL SMELL COMING FROM UNKNOWN SOURCE - RCT A A5-01-02 |  | FM008 |  | 2024-01-19 22:49 | 2024-01-19 23:49 | 2024-01-20 23:49 | 24 | 2024-01-19 22:55 | 2024-01-19 23:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | BADSMELL | CLOGGED AIR FILTER | CLEANED/REPLACED | 106973 | 17053 |  |  | 128352 | Okogbo, Ms. Peace Awolowo | N - - - |  | Voice Communication
| CM-2022-10105777 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO COLD - RCT -A |  | FM008 |  | 2022-02-04 06:18 | 2022-02-04 07:18 | 2022-02-05 07:18 | 24 | 2022-02-04 06:25 | 2022-02-04 08:00 | 95 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 57956 | Zash, Mr. Raad Hussam Fuad | N - - - |  | Voice Communication
| CM-2022-10679595 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO HOT RCTA |  | FM008 |  | 2022-05-22 07:15 | 2022-05-22 08:15 | 2022-05-23 08:15 | 24 | 2022-05-22 07:20 | 2022-05-22 13:15 | 355 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 55709 |  |  | 55804 | Ochava, Mr. Carlito Jr Friginal | N - - - |  | Voice Communication
| CM-2022-10750214 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | AC TOO COLD - HEAVY MIST ON GLASS AFFECTING VISIBILITY. ROOM 2136(TAG NO: A5-01-01 (RAMP CONTROL TOWER))-AIRSIDE-CONCOURSE A-FIFTH FLOOR AREA 01 |  | FM008 |  | 2022-06-18 23:26 | 2022-06-19 00:26 | 2022-06-20 00:26 | 24 | 2022-06-18 23:30 | 2022-06-18 23:59 | 29 | 29 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10128582 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | RAMP CONTROL TOWER -A - AC IS TOO COLD- |  | FM008 |  | 2022-02-10 21:26 | 2022-02-10 22:26 | 2022-02-11 22:26 | 24 | 2022-02-10 21:30 | 2022-02-11 01:00 | 210 | 65 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94953 | 55709 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10235390 | ASD-COA-APR-AHU077 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1121-701-AIRSIDE-CONCOURSE A-APRON CONTROL TOWER |  | FM008 |  | 2022-03-10 16:07 | 2022-03-10 17:07 | 2022-03-11 17:07 | 24 | 2022-03-10 16:10 | 2022-03-10 18:15 | 125 | 375 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10746704 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | AC TOO HOT – RCT A, |  | FM008 |  | 2022-06-13 05:26 | 2022-06-13 06:26 | 2022-06-14 06:26 | 24 | 2022-06-13 05:30 | 2022-06-13 06:50 | 80 | 25 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2022-11157569 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | AC TOO COLD - RCT A |  | FM008 |  | 2022-11-02 04:53 | 2022-11-02 05:53 | 2022-11-03 05:53 | 24 | 2022-11-02 05:00 | 2022-11-02 06:40 | 100 | 35 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 107423 | Bouazizi, Ms. Weded | N - - - |  | Voice Communication
| CM-2022-11272019 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | RCTA AC IS TOO COLD |  | FM008 |  | 2022-12-16 21:47 | 2022-12-16 22:47 | 2022-12-17 22:47 | 24 | 2022-12-16 21:57 | 2022-12-16 22:57 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 87807 | 17053 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2023-12507907 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | AHU HEATER NOT WORKING -- TAG NO:AHU-A1121-702)-AIRSIDE-CONCOURSE A-APRON CONTROL TOWER |  | FM008 |  | 2023-12-27 12:54 | 2023-12-27 13:54 | 2023-12-28 13:54 | 24 | 2023-12-27 13:04 | 2023-12-27 18:00 | 296 | 335 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 138627 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12614689 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | TEMPERATURE IS TOO HOT IN THE TOWER -RCT A |  | FM008 |  | 2024-02-03 10:31 | 2024-02-03 11:31 | 2024-02-04 11:31 | 24 | 2024-02-03 10:40 | 2024-02-03 16:45 | 365 | 65 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17336 | 17053 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2022-10251317 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | AC TOO COLD - A5-01-01 (RAMP CONTROL TOWER - CM-2022-02-0553 |  | FM008 |  | 2022-03-13 22:38 | 2022-03-13 23:38 | 2022-03-14 23:38 | 24 | 2022-03-13 22:45 | 2022-03-13 23:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 17053 |  |  | 99323 | RAVITHEJA | - - - |  | Voice Communication
| CM-2022-10750008 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | AC TOO COLD - ROOM 2136(TAG NO: A5-01-01 (RAMP CONTROL TOWER))-AIRSIDE-CONCOURSE A-FIFTH FLOOR AREA 01 |  | FM008 |  | 2022-06-17 23:07 | 2022-06-18 00:07 | 2022-06-19 00:07 | 24 | 2022-06-17 23:10 | 2022-06-18 00:30 | 80 | 30 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10790865 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | A/C IS TOO HOT A6-01-01 |  | FM008 |  | 2022-06-30 05:10 | 2022-06-30 06:10 | 2022-07-01 06:10 | 24 | 2022-06-30 05:15 | 2022-06-30 06:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 95217 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2023-12278198 | ASD-COA-APR-AHU078 | AIR HANDLING UNIT-05 | AHU-A1121-702-ABNOMRL SOUND FROM AHU (APRON CONTROL TOWER) |  | FM008 |  | 2023-10-11 07:22 | 2023-10-11 08:22 | 2023-10-12 08:22 | 24 | 2023-10-11 07:30 | 2023-10-11 15:00 | 450 | 620 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 77406 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11301317 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AB-04-09 |  | FM008 |  | 2022-12-24 08:08 | 2022-12-24 09:08 | 2022-12-25 09:08 | 24 | 2022-12-24 08:15 | 2022-12-24 11:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11826939 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-05-27 19:30 | 2023-05-27 20:30 | 2023-05-28 20:30 | 24 | 2023-05-27 19:40 | 2023-05-27 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-11164980 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING – AB-04-09 |  | FM008 |  | 2022-11-06 22:27 | 2022-11-06 23:27 | 2022-11-07 23:27 | 24 | 2022-11-06 22:30 | 2022-11-06 23:55 | 85 | 170 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 105233 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11969863 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING – AB-04-09 |  | FM008 |  | 2023-07-13 03:34 | 2023-07-13 04:34 | 2023-07-14 04:34 | 24 | 2023-07-13 03:40 | 2023-07-13 05:39 | 119 | 238 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106914 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12347934 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1155-B01, AB-04-09 |  | FM008 |  | 2023-11-05 12:40 | 2023-11-05 13:40 | 2023-11-06 13:40 | 24 | 2023-11-05 12:45 | 2023-11-05 17:30 | 285 | 440 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10874271 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | AHU-A1155-B01 FILTER ALARM AB-04-09 |  | FM008 |  | 2022-07-27 20:04 | 2022-07-27 21:04 | 2022-07-28 21:04 | 24 | 2022-07-27 20:12 | 2022-07-27 21:15 | 63 | 126 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12207369 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | DP1 FILTER STATUS - PROJECT8.APPLICATIONVIEW:APPLICATIONVIEW.GRAPHICS.PTC-A1155-INBOUNDBAGGAGESCREENINGFACILITY-CONA.AHU-A1155-B01 / |  | FM008 |  | 2023-09-23 20:18 | 2023-09-23 21:18 | 2023-09-24 21:18 | 24 | 2023-09-23 20:25 | 2023-09-23 22:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10354353 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM AHU-A1155-B01 AB-04-09 |  | FM008 |  | 2022-04-11 08:42 | 2022-04-11 09:42 | 2022-04-12 09:42 | 24 | 2022-04-11 08:50 | 2022-04-11 16:30 | 460 | 305 | 4 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 85125 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11407159 | ASD-COA-BAS004-AHU182 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AB-04-09 |  | FM008 |  | 2023-01-28 20:24 | 2023-01-28 21:24 | 2023-01-29 21:24 | 24 | 2023-01-28 20:30 | 2023-01-28 22:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 94954 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2022-10082514 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 ;COOLING COIL DIRTY – AG-01-08 |  | FM008 |  | 2022-01-28 01:15 | 2022-01-28 02:15 | 2022-01-29 02:15 | 24 | 2022-01-28 01:20 | 2022-01-28 05:10 | 230 | 580 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10578876 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | COOILING COIL DIRTY |  | FM008 |  | 2022-04-23 10:07 | 2022-04-23 11:07 | 2022-04-24 11:07 | 24 | 2022-04-23 10:20 | 2022-04-23 15:15 | 295 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10712694 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AC TOO HOT - ROOM NUMBER AG-01-13 CONCOURSE A-GROUND FLOOR AREA 001 (CONTACT REQUESTOR TO CONFIRM RESOLUTION). |  | FM008 |  | 2022-06-02 07:29 | 2022-06-02 08:29 | 2022-06-03 08:29 | 24 | 2022-06-02 07:35 | 2022-06-02 18:00 | 625 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 17053 |  |  | 61264 | Mukherjee, Mr. Abhinava | N - - - |  | Voice Communication
| CM-2022-10831120 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - AHU-A1121-003 – AG-01-08 |  | FM008 |  | 2022-07-14 18:58 | 2022-07-14 19:58 | 2022-07-15 19:58 | 24 | 2022-07-14 19:00 | 2022-07-14 21:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 95217 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-11046257 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AIR FILTER IS BLOCKED |  | FM008 |  | 2022-09-25 10:50 | 2022-09-25 11:50 | 2022-09-26 11:50 | 24 | 2022-09-25 10:59 | 2022-09-25 12:00 | 61 | 122 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11116873 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 – CHILLED WATER LINE PAINT FADED– AG-01-08- |  | FM008 |  | 2022-10-21 19:32 | 2022-10-21 20:32 | 2022-10-22 20:32 | 24 | 2022-10-21 19:40 | 2022-10-21 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11131601 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-10-25 07:49 | 2022-10-25 08:49 | 2022-10-26 08:49 | 24 | 2022-10-25 07:55 | 2022-10-25 12:30 | 275 | 550 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11303188 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | SUPPLY DUCT CONVERSE AIR LEAKAGE |  | FM008 |  | 2022-12-24 02:18 | 2022-12-24 03:18 | 2022-12-25 03:18 | 24 | 2022-12-24 02:30 | 2022-12-24 05:30 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 68060 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11365176 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 CHILLED WATER LINE PAINT PILLED OFF |  | FM008 |  | 2023-01-12 02:12 | 2023-01-12 03:12 | 2023-01-13 03:12 | 24 | 2023-01-12 02:20 | 2023-01-12 05:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11849007 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | CABIN LAMB NOT WORKING-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-06-04 14:35 | 2023-06-04 15:35 | 2023-06-05 15:35 | 24 | 2023-06-04 14:45 | 2023-06-04 17:10 | 145 | 243 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | CIRCUIT TRIP DUE TO OVERLOAD | RESET THE BREAKER | 77406 | 89127 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11969906 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 DRAIN LINE PIT DIRTY AG-01-08 |  | FM008 |  | 2023-07-13 08:56 | 2023-07-13 09:56 | 2023-07-14 09:56 | 24 | 2023-07-13 09:00 | 2023-07-13 11:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12114916 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 SUPPLY DUCT INSULATION DAMAGED AG-01-08 |  | FM008 |  | 2023-08-25 00:06 | 2023-08-25 01:06 | 2023-08-26 01:06 | 24 | 2023-08-25 00:15 | 2023-08-25 02:30 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-12344311 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AG-01-08- DUCT INSULATION DAMAGED-AIR HANDLING UNIT 065 (TAG NO:AHU-A1121-003-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-11-03 03:04 | 2023-11-03 04:04 | 2023-11-04 04:04 | 24 | 2023-11-03 03:10 | 2023-11-03 05:00 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-12485044 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1121-003) – AG 01 08 |  | FM008 |  | 2023-12-18 07:27 | 2023-12-18 08:27 | 2023-12-19 08:27 | 24 | 2023-12-18 07:35 | 2023-12-18 10:30 | 175 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-11064532 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 – DP3 FILTER ALARM-- |  | FM008 |  | 2022-09-29 02:19 | 2022-09-29 03:19 | 2022-09-30 03:19 | 24 | 2022-09-29 02:25 | 2022-09-29 03:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11699759 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU NOISY |  | FM008 |  | 2023-04-27 08:36 | 2023-04-27 09:36 | 2023-04-28 09:36 | 24 | 2023-04-27 08:40 | 2023-04-27 18:30 | 590 | 785 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 17333 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11834165 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AG-01-08 |  | FM008 |  | 2023-05-28 21:48 | 2023-05-28 22:48 | 2023-05-29 22:48 | 24 | 2023-05-28 21:55 | 2023-05-28 23:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 106972 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12112281 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AG-01-08 |  | FM008 |  | 2023-08-24 13:20 | 2023-08-24 14:20 | 2023-08-25 14:20 | 24 | 2023-08-24 13:30 | 2023-08-24 16:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12200726 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | FILTER DIRTY-AG-01-08 |  | FM008 |  | 2023-09-18 07:00 | 2023-09-18 08:00 | 2023-09-19 08:00 | 24 | 2023-09-18 07:05 | 2023-09-18 10:00 | 175 | 115 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12341240 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | FLEXIBLE HOSE DAMAGE : -AIR HANDLING UNIT 065 (TAG NO:AHU-A1121-003)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-11-01 13:34 | 2023-11-01 14:34 | 2023-11-02 14:34 | 24 | 2023-11-01 13:44 | 2023-11-01 15:44 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 138627 | 87807 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2022-10956700 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-08-20 20:15 | 2022-08-20 21:15 | 2022-08-21 21:15 | 24 | 2022-08-20 20:20 | 2022-08-20 23:30 | 190 | 570 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-10965866 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1121-003 |  | FM008 |  | 2022-08-21 21:28 | 2022-08-21 22:28 | 2022-08-22 22:28 | 24 | 2022-08-21 21:35 | 2022-08-21 23:50 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 106972 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-11071062 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY AG-01-08 |  | FM008 |  | 2022-10-05 10:02 | 2022-10-05 11:02 | 2022-10-06 11:02 | 24 | 2022-10-05 10:10 | 2022-10-05 18:20 | 490 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2024-12595860 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED,AHU-A1121-003, AG-01-08 |  | FM008 |  | 2024-01-27 22:06 | 2024-01-27 23:06 | 2024-01-28 23:06 | 24 | 2024-01-27 22:10 | 2024-01-27 23:58 | 108 | 216 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12686193 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH FAULTY, AHU-A1121-003, AG-01-08 |  | FM008 |  | 2024-02-28 19:07 | 2024-02-28 20:07 | 2024-02-29 20:07 | 24 | 2024-02-28 19:17 | 2024-02-28 22:15 | 178 | 356 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 124475 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-12515314 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | DP2 FILTER ALARM |  | FM008 |  | 2023-12-29 03:07 | 2023-12-29 04:07 | 2023-12-30 04:07 | 24 | 2023-12-29 03:15 | 2023-12-29 04:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12325338 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | FILTER ALARM STATUS - AHU-A1121-003 - MECHANICAL ROOM AG-01-08 - PROJECT8.APPLICATIONVIEW:APPLICATIONVIEW.GRAPHICS.PTC-A1121-CONCOURSEA.AHU-A1121-003-CPMS / |  | FM008 |  | 2023-10-27 10:07 | 2023-10-27 11:07 | 2023-10-28 11:07 | 24 | 2023-10-27 10:15 | 2023-10-27 12:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10220001 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1121-003 – AG-01-08 |  | FM008 |  | 2022-03-06 10:53 | 2022-03-06 11:53 | 2022-03-07 11:53 | 24 | 2022-03-06 11:03 | 2022-03-06 13:30 | 147 | 441 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-9950875 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 RETURN ACCESS DOOR LEAKAGE |  | FM008 |  | 2022-01-01 22:07 | 2022-01-01 23:07 | 2022-01-02 23:07 | 24 | 2022-01-01 22:15 | 2022-01-01 23:40 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11149312 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | AHU-A1121-003 – COOLING COIL DIRTY |  | FM008 |  | 2022-10-29 19:13 | 2022-10-29 20:13 | 2022-10-30 20:13 | 24 | 2022-10-29 19:20 | 2022-10-29 23:20 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10208124 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-003 – AG-01-08 |  | FM008 |  | 2022-03-01 19:42 | 2022-03-01 20:42 | 2022-03-02 20:42 | 24 | 2022-03-01 19:50 | 2022-03-01 21:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11476458 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1121-003 |  | FM008 |  | 2023-02-22 11:08 | 2023-02-22 12:08 | 2023-02-23 12:08 | 24 | 2023-02-22 11:13 | 2023-02-22 14:00 | 167 | 352 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-12157050 | ASD-COA-GFL001-AHU065 | AIR HANDLING UNIT-05 | Beside LaVita Café,In Front of Women Washroom(A1 02 18) damaged/bend Return Air Grills/misaligned/missing |  | FM008 |  | 2023-09-06 13:53 | 2023-09-06 14:53 | 2023-09-07 14:53 | 24 | 2023-09-06 14:00 | 2023-09-06 16:30 | 150 | 185 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 89127 | 17053 |  |  | 88447 | Kho, Mr. Marino Pacana | N - - - |  | E-mail
| CM-2022-10749639 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU-A1121-004 RETURN MOTOR NOISY |  | FM008 |  | 2022-06-15 11:40 | 2022-06-15 12:40 | 2022-06-16 12:40 | 24 | 2022-06-15 11:50 | 2022-06-15 18:29 | 399 | 542 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68485 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-11116874 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU-A1121-004- CHILLED WATER LINE PAINT FADED – AG-01-08- - |  | FM008 |  | 2022-10-21 19:33 | 2022-10-21 20:33 | 2022-10-22 20:33 | 24 | 2022-10-21 19:40 | 2022-10-21 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11502768 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-02-28 21:08 | 2023-02-28 22:08 | 2023-03-01 22:08 | 24 | 2023-02-28 21:15 | 2023-02-28 23:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 94954 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-11698402 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU-A1121-004)-NOISY -CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-04-26 08:34 | 2023-04-26 09:34 | 2023-04-27 09:34 | 24 | 2023-04-26 08:45 | 2023-04-26 13:00 | 255 | 1020 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 77406 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12007643 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DRAIN LINE PIT DIRTY -AIR HANDLING UNIT 066 (TAG NO:AHU-A1121-004)-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-07-26 08:11 | 2023-07-26 09:11 | 2023-07-27 09:11 | 24 | 2023-07-26 08:15 | 2023-07-26 13:45 | 330 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2022-11015583 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU COIL IS DIRTY - AG-01-08 |  | FM008 |  | 2022-09-13 19:17 | 2022-09-13 20:17 | 2022-09-14 20:17 | 24 | 2022-09-13 19:25 | 2022-09-13 22:25 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11064533 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU-A1121-003 – DP3 FILTER ALARM-- |  | FM008 |  | 2022-09-29 02:20 | 2022-09-29 03:20 | 2022-09-30 03:20 | 24 | 2022-09-29 02:28 | 2022-09-29 05:00 | 152 | 187 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11835550 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | CHILL WATER LINE PIPE PAINT FADED - AHU-A1121-004 – MECHANICAL ROOM AG-01-08 |  | FM008 |  | 2023-05-29 21:15 | 2023-05-29 22:15 | 2023-05-30 22:15 | 24 | 2023-05-29 21:25 | 2023-05-29 23:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 17573 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12112280 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AG-01-08 |  | FM008 |  | 2023-08-24 13:19 | 2023-08-24 14:19 | 2023-08-25 14:19 | 24 | 2023-08-24 13:25 | 2023-08-24 16:00 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12186243 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1121-004 – AG-01-08 |  | FM008 |  | 2023-09-13 20:26 | 2023-09-13 21:26 | 2023-09-14 21:26 | 24 | 2023-09-13 20:35 | 2023-09-13 23:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12281403 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARAM - AIR HANDLING UNIT 066 (TAG NO:AHU-A1121-004)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-10-14 18:55 | 2023-10-14 19:55 | 2023-10-15 19:55 | 24 | 2023-10-14 19:00 | 2023-10-14 21:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 119320 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11028167 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-004 |  | FM008 |  | 2022-09-17 12:10 | 2022-09-17 13:10 | 2022-09-18 13:10 | 24 | 2022-09-17 12:15 | 2022-09-17 16:00 | 225 | 675 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-11071060 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY AG-01-08 |  | FM008 |  | 2022-10-05 10:01 | 2022-10-05 11:01 | 2022-10-06 11:01 | 24 | 2022-10-05 10:10 | 2022-10-05 16:50 | 400 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-11299867 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-12-23 07:36 | 2022-12-23 08:36 | 2022-12-24 08:36 | 24 | 2022-12-23 07:45 | 2022-12-23 13:00 | 315 | 500 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11328232 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT-RETURN SIDE DUCT CANVAS AIR LEAKAGE -AG-01- 08 |  | FM008 |  | 2022-12-28 19:31 | 2022-12-28 20:31 | 2022-12-29 20:31 | 24 | 2022-12-28 19:40 | 2022-12-28 23:00 | 200 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 77406 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11446018 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | RELIEF BLOWER NOISY – AG-01-08 |  | FM008 |  | 2023-02-12 11:46 | 2023-02-12 12:46 | 2023-02-13 12:46 | 24 | 2023-02-12 11:50 | 2023-02-12 17:15 | 325 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11766032 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AC TOO HOT INSIDE WASH ROOM , FFL2 MALE WASH ROOM |  | FM008 |  | 2023-05-06 07:17 | 2023-05-06 08:17 | 2023-05-07 08:17 | 24 | 2023-05-06 07:25 | 2023-05-06 17:00 | 575 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 87807 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2023-11879384 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DP1-A FINAL FILTER STATUS - MECHANICAL ROOM AG-01-08 (AHU-A1121-004) PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1121.GNDP1.CONA04.AHU004.SYSALM.DP1A / |  | FM008 |  | 2023-06-12 15:43 | 2023-06-12 16:43 | 2023-06-13 16:43 | 24 | 2023-06-12 15:50 | 2023-06-12 18:30 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2024-12800069 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY -AIR HANDLING UNIT 066 (TAG NO:AHU-A1121-004)-AG-01-08 |  | FM008 |  | 2024-04-07 09:26 | 2024-04-07 10:26 | 2024-04-08 10:26 | 24 | 2024-04-07 09:35 | 2024-04-07 14:00 | 265 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2024-12594128 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1121-004, AG-01-08 |  | FM008 |  | 2024-01-27 22:06 | 2024-01-27 23:06 | 2024-01-28 23:06 | 24 | 2024-01-27 22:10 | 2024-01-27 23:58 | 108 | 216 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12822306 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1121-004 |  | FM008 |  | 2024-04-11 19:29 | 2024-04-11 20:29 | 2024-04-12 20:29 | 24 | 2024-04-11 19:38 | 2024-04-11 23:30 | 232 | 928 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12833243 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED - AG-01-08 |  | FM008 |  | 2024-04-20 20:34 | 2024-04-20 21:34 | 2024-04-21 21:34 | 24 | 2024-04-20 20:40 | 2024-04-20 22:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12325339 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | FILTER ALARM STATUS - AHU-A1121-004 - MECHANICAL ROOM AG-01-08 - PROJECT8.APPLICATIONVIEW:APPLICATIONVIEW.GRAPHICS.PTC-A1121-CONCOURSEA.AHU-A1121-004-CPMS / |  | FM008 |  | 2023-10-27 10:15 | 2023-10-27 11:15 | 2023-10-28 11:15 | 24 | 2023-10-27 10:20 | 2023-10-27 12:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12346818 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU-A1121-004 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-04 01:34 | 2023-11-04 02:34 | 2023-11-05 02:34 | 24 | 2023-11-04 01:40 | 2023-11-04 03:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2024-12691244 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU LIGHTING SWITCH NOT WORKING AHU-A1121-004 -AG-01-08 |  | FM008 |  | 2024-03-01 19:08 | 2024-03-01 20:08 | 2024-03-02 20:08 | 24 | 2024-03-01 19:17 | 2024-03-01 22:01 | 164 | 328 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-10044594 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-01-13 18:50 | 2022-01-13 19:50 | 2022-01-14 19:50 | 24 | 2022-01-13 19:00 | 2022-01-13 23:00 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | BMS
| CM-2022-10220000 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1121-004 – AG-01-08 |  | FM008 |  | 2022-03-06 10:51 | 2022-03-06 11:51 | 2022-03-07 11:51 | 24 | 2022-03-06 11:00 | 2022-03-06 16:00 | 300 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10309452 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AG-01-08 |  | FM008 |  | 2022-03-29 19:12 | 2022-03-29 20:12 | 2022-03-30 20:12 | 24 | 2022-03-29 19:20 | 2022-03-29 23:00 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10327480 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS-ASD-COA-GFL001-AHU066-FIL819 AHU-A1121-004 FILTERS 819-AIR HANDLING UNIT 066 (TAG NO:AHU-A1121-004)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1121.GNDP1.CONA04.AHU00 |  | FM008 |  | 2022-04-06 09:19 | 2022-04-06 10:19 | 2022-04-07 10:19 | 24 | 2022-04-06 09:25 | 2022-04-06 11:30 | 125 | 375 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10655835 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | AHU-A1121-004 – DP1 FILTER ALARM |  | FM008 |  | 2022-05-14 09:05 | 2022-05-14 10:05 | 2022-05-15 10:05 | 24 | 2022-05-14 09:10 | 2022-05-14 12:00 | 170 | 265 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10672664 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1121-004) |  | FM008 |  | 2022-05-17 11:13 | 2022-05-17 12:13 | 2022-05-18 12:13 | 24 | 2022-05-17 11:20 | 2022-05-17 15:30 | 250 | 750 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10676796 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM CHILLED WATER LINE-AG-01-08 |  | FM008 |  | 2022-05-21 12:22 | 2022-05-21 13:22 | 2022-05-22 13:22 | 24 | 2022-05-21 12:30 | 2022-05-21 16:00 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106914 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11301318 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-12-24 08:09 | 2022-12-24 09:09 | 2022-12-25 09:09 | 24 | 2022-12-24 08:20 | 2022-12-24 11:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10074422 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AG-01-08 AHU-A1121-004 |  | FM008 |  | 2022-01-23 19:12 | 2022-01-23 20:12 | 2022-01-24 20:12 | 24 | 2022-01-23 19:15 | 2022-01-23 23:00 | 225 | 675 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10208125 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-004 - AG-01-08 |  | FM008 |  | 2022-03-01 19:44 | 2022-03-01 20:44 | 2022-03-02 20:44 | 24 | 2022-03-01 19:50 | 2022-03-01 21:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 106973 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10597997 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM- AHU-A1121-004- MECHANICAL ROOM AG-01-08 |  | FM008 |  | 2022-04-27 08:07 | 2022-04-27 09:07 | 2022-04-28 09:07 | 24 | 2022-04-27 08:15 | 2022-04-27 17:00 | 525 | 195 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10843685 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | FILTER BLOCKED - AHU-A1121-004) CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-07-17 08:03 | 2022-07-17 09:03 | 2022-07-18 09:03 | 24 | 2022-07-17 08:10 | 2022-07-17 09:45 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 121959 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10972207 | ASD-COA-GFL001-AHU066 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM TAG NO:AHU-A1121-004 |  | FM008 |  | 2022-08-27 08:04 | 2022-08-27 09:04 | 2022-08-28 09:04 | 24 | 2022-08-27 08:10 | 2022-08-27 11:00 | 170 | 355 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10578877 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOILING COIL DIRTY |  | FM008 |  | 2022-04-23 10:09 | 2022-04-23 11:09 | 2022-04-24 11:09 | 24 | 2022-04-23 10:15 | 2022-04-23 15:15 | 300 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10831121 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - AHU-A1121-009 – AG-01-08 |  | FM008 |  | 2022-07-14 19:00 | 2022-07-14 20:00 | 2022-07-15 20:00 | 24 | 2022-07-14 19:05 | 2022-07-14 23:00 | 235 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 95217 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | E-mail
| CM-2022-11027691 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1121-009 |  | FM008 |  | 2022-09-14 19:13 | 2022-09-14 20:13 | 2022-09-15 20:13 | 24 | 2022-09-14 19:20 | 2022-09-14 21:20 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11046256 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AIR FILTER IS BLOCKED |  | FM008 |  | 2022-09-25 10:48 | 2022-09-25 11:48 | 2022-09-26 11:48 | 24 | 2022-09-25 10:57 | 2022-09-25 12:00 | 63 | 126 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11177055 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | RETURN SIDE MOTOR COOLING FAN DAMAGED |  | FM008 |  | 2022-11-12 14:26 | 2022-11-12 15:26 | 2022-11-13 15:26 | 24 | 2022-11-12 14:30 | 2022-11-12 18:30 | 240 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 87807 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2023-11364257 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 COOLING COIL DIRTY |  | FM008 |  | 2023-01-11 19:53 | 2023-01-11 20:53 | 2023-01-12 20:53 | 24 | 2023-01-11 20:00 | 2023-01-11 23:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11886067 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AG-01-08 COOLING COIL DIRTY AHU-A1121-009 |  | FM008 |  | 2023-06-18 07:30 | 2023-06-18 08:30 | 2023-06-19 08:30 | 24 | 2023-06-18 07:35 | 2023-06-18 11:30 | 235 | 940 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-11887857 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-06-18 10:45 | 2023-06-18 11:45 | 2023-06-19 11:45 | 24 | 2023-06-18 10:50 | 2023-06-18 15:30 | 280 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11969905 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 DRAIN LINE PIT DIRTY AG-01-08 |  | FM008 |  | 2023-07-13 08:55 | 2023-07-13 09:55 | 2023-07-14 09:55 | 24 | 2023-07-13 09:00 | 2023-07-13 11:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12047571 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-009 - AG 01 08 |  | FM008 |  | 2023-08-05 21:39 | 2023-08-05 22:39 | 2023-08-06 22:39 | 24 | 2023-08-05 21:45 | 2023-08-05 23:30 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12114984 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED,AHU-A1121-009, AG-01-08 |  | FM008 |  | 2023-08-25 07:46 | 2023-08-25 08:46 | 2023-08-26 08:46 | 24 | 2023-08-25 07:50 | 2023-08-25 14:05 | 375 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12186242 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1121-009 - AG-01-08 |  | FM008 |  | 2023-09-13 20:26 | 2023-09-13 21:26 | 2023-09-14 21:26 | 24 | 2023-09-13 20:35 | 2023-09-13 23:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11113808 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | FILTER DIRTY-AHU-A1121-009)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-10-20 09:47 | 2022-10-20 10:47 | 2022-10-21 10:47 | 24 | 2022-10-20 09:55 | 2022-10-20 14:30 | 275 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-11176163 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOL DIRTY |  | FM008 |  | 2022-11-08 19:25 | 2022-11-08 20:25 | 2022-11-09 20:25 | 24 | 2022-11-08 19:30 | 2022-11-08 23:30 | 240 | 960 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11302225 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | SUPLLY SIDE DUCT CANVAS AIR LEAKAGE - AHU-A1121-009 – AG-01-08 |  | FM008 |  | 2022-12-23 19:28 | 2022-12-23 20:28 | 2022-12-24 20:28 | 24 | 2022-12-23 19:35 | 2022-12-23 23:05 | 210 | 725 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-12201291 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1121-009 – AG-01-08 |  | FM008 |  | 2023-09-18 13:31 | 2023-09-18 14:31 | 2023-09-19 14:31 | 24 | 2023-09-18 13:40 | 2023-09-18 17:00 | 200 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-12348172 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | LIGHTING SWITCH FAULTY - AHU-A1121-009 – AG-01-08 |  | FM008 |  | 2023-11-06 12:05 | 2023-11-06 13:05 | 2023-11-07 13:05 | 24 | 2023-11-06 12:10 | 2023-11-06 15:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | FAULTY CONTROL THERMOSTAT | REPLACED THE THERMOSTAT | 106973 | 17053 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2023-12383113 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-11-15 20:01 | 2023-11-15 21:01 | 2023-11-16 21:01 | 24 | 2023-11-15 20:10 | 2023-11-15 22:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2022-11165868 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 – AHU CABIN LAMP NOT WORKING- AG-01-08 |  | FM008 |  | 2022-11-08 15:08 | 2022-11-08 16:08 | 2022-11-09 16:08 | 24 | 2022-11-08 15:15 | 2022-11-08 16:42 | 87 | 174 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11715549 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU NOISY -AG-1-08 |  | FM008 |  | 2023-04-28 07:23 | 2023-04-28 08:23 | 2023-04-29 08:23 | 24 | 2023-04-28 07:30 | 2023-04-28 13:30 | 360 | 800 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12101321 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 SUPPLY DUCT INSULATION DAMAGED -A0-01-08 |  | FM008 |  | 2023-08-21 22:49 | 2023-08-21 23:49 | 2023-08-22 23:49 | 24 | 2023-08-21 23:00 | 2023-08-22 01:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2024-12833242 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED - AG-01-08 |  | FM008 |  | 2024-04-20 20:33 | 2024-04-20 21:33 | 2024-04-21 21:33 | 24 | 2024-04-20 20:35 | 2024-04-20 22:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12655951 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE - AIR HANDLING UNIT 071 (TAG NO:AHU-A1121-009)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2024-02-19 19:25 | 2024-02-19 20:25 | 2024-02-20 20:25 | 24 | 2024-02-19 19:35 | 2024-02-19 21:30 | 115 | 345 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12712624 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – (AHU-A1121-009) - |  | FM008 |  | 2024-03-07 12:45 | 2024-03-07 13:45 | 2024-03-08 13:45 | 24 | 2024-03-07 12:50 | 2024-03-07 15:30 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 132112 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10044444 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AG NO:AHU-A1121-009) AG-01-08 |  | FM008 |  | 2022-01-12 18:54 | 2022-01-12 19:54 | 2022-01-13 19:54 | 24 | 2022-01-12 19:00 | 2022-01-12 23:30 | 270 | 540 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10084586 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AG-01-08 |  | FM008 |  | 2022-01-28 14:06 | 2022-01-28 15:06 | 2022-01-29 15:06 | 24 | 2022-01-28 14:10 | 2022-01-28 18:45 | 275 | 620 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10202817 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AG-01-08 |  | FM008 |  | 2022-03-02 20:22 | 2022-03-02 21:22 | 2022-03-03 21:22 | 24 | 2022-03-02 20:30 | 2022-03-02 23:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10262310 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | MAJOR LEAKAGE FROM UNKNOWN SOURCE (FLOOR FLOODED WITH WATER) – MECHANICAL ROOM A0-01-08 |  | FM008 |  | 2022-03-18 19:04 | 2022-03-18 19:34 | 2022-03-18 23:34 | 4 | 2022-03-18 19:10 | 2022-03-18 21:55 | 165 | 495 | 3 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 001 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 106973 | 87807 |  |  | FM9724 | Khan, Mr. Waseem | N - - - |  | Voice Communication
| CM-2022-10277258 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-03-25 21:41 | 2022-03-25 22:41 | 2022-03-26 22:41 | 24 | 2022-03-25 21:45 | 2022-03-25 23:25 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | BMS
| CM-2022-10084296 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AIR HANDLING UNIT 071 (TAG NO:AHU-A1121-009)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-01-27 19:11 | 2022-01-27 20:11 | 2022-01-28 20:11 | 24 | 2022-01-27 19:20 | 2022-01-27 23:00 | 220 | 835 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10307268 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 - COOLING COIL DIRTY AG-01-08 |  | FM008 |  | 2022-03-28 19:20 | 2022-03-28 20:20 | 2022-03-29 20:20 | 24 | 2022-03-28 19:25 | 2022-03-28 22:30 | 185 | 555 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10154649 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | DAMAGED ALUMINIUM LOUVRE / DUCT AT CON A, AREA1 AHU-A1121-009 |  | FM008 |  | 2022-02-22 12:00 | 2022-02-22 13:00 | 2022-02-23 13:00 | 24 | 2022-02-22 12:10 | 2022-02-22 14:25 | 135 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 85125 | 55709 |  |  | CT11214 | Christoph Meyer | N - - - |  | E-mail
| CM-2022-10652352 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – AG-01-08 |  | FM008 |  | 2022-05-11 03:36 | 2022-05-11 04:36 | 2022-05-12 04:36 | 24 | 2022-05-11 03:40 | 2022-05-11 06:00 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10954700 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 – COOLING COIL DIRTY |  | FM008 |  | 2022-08-20 00:14 | 2022-08-20 01:14 | 2022-08-21 01:14 | 24 | 2022-08-20 00:20 | 2022-08-20 03:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2023-11429718 | ASD-COA-GFL001-AHU071 | AIR HANDLING UNIT-05 | AHU-A1121-009 CHILLED WATER LINE PAINT FADED AG-01-08 |  | FM008 |  | 2023-02-05 01:50 | 2023-02-05 02:50 | 2023-02-06 02:50 | 24 | 2023-02-05 01:55 | 2023-02-05 05:30 | 215 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 133396 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-10275541 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AG-02-05 |  | FM008 |  | 2022-03-22 19:00 | 2022-03-22 20:00 | 2022-03-23 20:00 | 24 | 2022-03-22 19:10 | 2022-03-22 23:00 | 230 | 570 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17053 | 17053 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10912271 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY - AHU-A1121-005 – AG-02-05 |  | FM008 |  | 2022-08-06 20:04 | 2022-08-06 21:04 | 2022-08-07 21:04 | 24 | 2022-08-06 20:10 | 2022-08-06 23:30 | 200 | 600 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-11038440 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005- COOLING COIL DIRTY AG-02-05 |  | FM008 |  | 2022-09-19 19:32 | 2022-09-19 20:32 | 2022-09-20 20:32 | 24 | 2022-09-19 19:35 | 2022-09-19 23:30 | 235 | 705 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11327926 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005- SUPPLY DUCT CANVAS AIR LEAKAGE – AG-02-05- |  | FM008 |  | 2022-12-29 19:56 | 2022-12-29 20:56 | 2022-12-30 20:56 | 24 | 2022-12-29 20:05 | 2022-12-29 23:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11350302 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1121-005, AG-02-05 |  | FM008 |  | 2023-01-05 19:34 | 2023-01-05 20:34 | 2023-01-06 20:34 | 24 | 2023-01-05 19:45 | 2023-01-05 23:45 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11691193 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - (AHU-A1121-005) - AG 02 04 |  | FM008 |  | 2023-04-21 07:29 | 2023-04-21 08:29 | 2023-04-22 08:29 | 24 | 2023-04-21 07:35 | 2023-04-21 10:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 132112 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-11818851 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | FILTER BLOCKED, AHU-A1121-005, AG-02-05 |  | FM008 |  | 2023-05-24 01:01 | 2023-05-24 02:01 | 2023-05-25 02:01 | 24 | 2023-05-24 01:10 | 2023-05-24 02:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11845984 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | DAMAGED/BEND RETURN AIR GRILLS - IN FRONT OF WOMEN WASHROOM (A1 02 18) |  | FM008 |  | 2023-06-05 14:34 | 2023-06-05 15:34 | 2023-06-06 15:34 | 24 | 2023-06-05 14:40 | 2023-06-05 18:40 | 240 | 85 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | 88447 | Kho, Mr. Marino Pacana | N - - - |  | E-mail
| CM-2023-11948310 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | PTC Con A-level 1 Near LaVita Café damaged/bend Return Air Grills/misaligned |  | FM008 |  | 2023-07-05 12:31 | 2023-07-05 13:30 | 2023-07-06 13:30 | 24 | 2023-07-05 12:35 | 2023-07-05 16:15 | 220 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOISY | MISALIGNMENT | RECTIFIED | 89127 | 17053 |  |  | 88447 | Kho, Mr. Marino Pacana | N - - - |  | E-mail
| CM-2023-11949395 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005-CHILLED WATER LINE PAINTS FADED-CONCOURSE A-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-07-06 07:54 | 2023-07-06 08:54 | 2023-07-07 08:54 | 24 | 2023-07-06 08:00 | 2023-07-06 09:45 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 77406 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12057056 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM THE UNIT – AG-02-05 |  | FM008 |  | 2023-08-07 08:35 | 2023-08-07 09:35 | 2023-08-08 09:35 | 24 | 2023-08-07 08:40 | 2023-08-07 14:20 | 340 | 1020 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12344247 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU COIL DIRTY |  | FM008 |  | 2023-11-02 19:58 | 2023-11-02 20:58 | 2023-11-03 20:58 | 24 | 2023-11-02 20:05 | 2023-11-02 23:30 | 205 | 615 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12507564 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | 1.CON-A LEVEL ONE 3RD COMMON AREA WALL AC GRILL METAL PANELS DETACH (NEARBY LOCATION A1 02 16 PARENTS ROOM) |  | FM008 |  | 2023-12-26 08:42 | 2023-12-26 09:42 | 2023-12-27 09:42 | 24 | 2023-12-26 08:50 | 2023-12-26 15:00 | 370 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | BLOCKAGE OF AIR FLOW | REPAIR/REPLACE | 132112 | 87807 |  |  | FM5770 | Khan, Mr. Md Ratan | N - - - |  | E-mail
| CM-2024-12615402 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2024-02-03 19:12 | 2024-02-03 20:12 | 2024-02-04 20:12 | 24 | 2024-02-03 19:20 | 2024-02-03 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-10877579 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005- FILTER DIRTY |  | FM008 |  | 2022-07-28 13:19 | 2022-07-28 14:19 | 2022-07-29 14:19 | 24 | 2022-07-28 13:25 | 2022-07-28 16:50 | 205 | 85 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10953958 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU COOLING COIL IS DIRTY |  | FM008 |  | 2022-08-17 03:23 | 2022-08-17 04:23 | 2022-08-18 04:23 | 24 | 2022-08-17 03:30 | 2022-08-17 06:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11078552 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-10-05 18:59 | 2022-10-05 19:59 | 2022-10-06 19:59 | 24 | 2022-10-05 19:05 | 2022-10-05 20:00 | 55 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-11116353 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT IS FADED - AHU-A1121005 – AG-02-05 |  | FM008 |  | 2022-10-18 21:14 | 2022-10-18 22:14 | 2022-10-19 22:14 | 24 | 2022-10-18 21:20 | 2022-10-18 23:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 17573 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12115292 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-005 – AG-02-05 |  | FM008 |  | 2023-08-26 12:41 | 2023-08-26 13:41 | 2023-08-27 13:41 | 24 | 2023-08-26 12:45 | 2023-08-26 15:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12485602 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AIR HANDLING UNIT 067 (TAG NO:AHU-A1121-005)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-12-17 19:58 | 2023-12-17 20:58 | 2023-12-18 20:58 | 24 | 2023-12-17 20:08 | 2023-12-17 23:30 | 202 | 606 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 119320 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12522023 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE,AHU-A1121-005, AG-02-05 |  | FM008 |  | 2024-01-03 12:37 | 2024-01-03 13:37 | 2024-01-04 13:37 | 24 | 2024-01-03 12:45 | 2024-01-03 16:00 | 195 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10931793 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AC TOO WARM - GATE A6 |  | FM008 |  | 2022-08-11 23:19 | 2022-08-12 00:19 | 2022-08-13 00:19 | 24 | 2022-08-11 23:25 | 2022-08-12 01:00 | 95 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 55709 |  |  | 106774 | Israel, Mr. Janeef Michael Johnson | N - - - |  | Voice Communication
| CM-2022-11175846 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AG-02-05- AHU-A1121-005- COOLING COIL DIRTY |  | FM008 |  | 2022-11-08 10:26 | 2022-11-08 11:26 | 2022-11-09 11:26 | 24 | 2022-11-08 10:30 | 2022-11-08 13:00 | 150 | 475 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 17053 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-11348651 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - (AHU-A1121010) - AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-01-07 12:39 | 2023-01-07 13:39 | 2023-01-08 13:39 | 24 | 2023-01-07 12:45 | 2023-01-07 17:00 | 255 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12179069 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005 COOLING COIL DIRTY AG-02-05 |  | FM008 |  | 2023-09-14 12:11 | 2023-09-14 13:11 | 2023-09-15 13:11 | 24 | 2023-09-14 12:15 | 2023-09-14 15:20 | 185 | 555 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | E-mail
| CM-2024-12690533 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING, AHU-A1121-005, AG-02-05 |  | FM008 |  | 2024-02-27 19:06 | 2024-02-27 20:06 | 2024-02-28 20:06 | 24 | 2024-02-27 19:15 | 2024-02-27 22:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 124475 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12362319 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AC VENT DAMAGE IN CONCOURSE A NEAR COMMON AREA A A8 BOARDING GATE NEAR LATVIA CAFE PLEASE CONTACT @ 55948635 MERIAM |  | FM008 |  | 2023-11-09 02:12 | 2023-11-09 03:12 | 2023-11-10 03:12 | 24 | 2023-11-09 02:20 | 2023-11-09 04:00 | 100 | 115 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 119320 | 17053 |  |  | 17967 | Manzon, Ms. Meriam Salazar | N - - - |  | Voice Communication
| CM-2023-12422493 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | DUCP INSULATION DAMAGE -- AG-02-05 |  | FM008 |  | 2023-11-28 19:52 | 2023-11-28 20:52 | 2023-11-29 20:52 | 24 | 2023-11-28 20:00 | 2023-11-28 22:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 87807 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2024-12712623 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | SUPPLY DUCT AIR LEAKAGE – (AHU-A1121-005) - |  | FM008 |  | 2024-03-07 12:40 | 2024-03-07 13:40 | 2024-03-08 13:40 | 24 | 2024-03-07 12:45 | 2024-03-07 15:20 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 132112 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10098591 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-01-31 02:25 | 2022-01-31 03:25 | 2022-02-01 03:25 | 24 | 2022-01-31 02:30 | 2022-01-31 05:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10201110 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT IS DAMAGED - AHU-A1121-005 – AG-02-05 |  | FM008 |  | 2022-02-27 20:14 | 2022-02-27 21:14 | 2022-02-28 21:14 | 24 | 2022-02-27 20:20 | 2022-02-27 22:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17573 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10225395 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005 –FILTER BLOCKED – AG-02-05 |  | FM008 |  | 2022-03-09 01:08 | 2022-03-09 02:08 | 2022-03-10 02:08 | 24 | 2022-03-09 01:15 | 2022-03-09 02:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17154 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10227464 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY –AG-02-05 |  | FM008 |  | 2022-03-09 20:07 | 2022-03-09 21:07 | 2022-03-10 21:07 | 24 | 2022-03-09 20:15 | 2022-03-09 23:55 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 17053 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-9959196 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-005 – AG-02-05 |  | FM008 |  | 2022-01-04 19:48 | 2022-01-04 20:48 | 2022-01-05 20:48 | 24 | 2022-01-04 19:55 | 2022-01-04 22:30 | 155 | 620 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10066382 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | AHU-A1121-005 COOLING COIL DIRTY – AG-02-05 |  | FM008 |  | 2022-01-19 19:00 | 2022-01-19 20:00 | 2022-01-20 20:00 | 24 | 2022-01-19 19:05 | 2022-01-19 23:00 | 235 | 470 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10728228 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AG-02-05 |  | FM008 |  | 2022-06-08 00:32 | 2022-06-08 01:32 | 2022-06-09 01:32 | 24 | 2022-06-08 00:40 | 2022-06-08 04:00 | 200 | 800 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2022-10862151 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY - AHU-A1121-005 - AG-02-05 |  | FM008 |  | 2022-07-21 19:10 | 2022-07-21 20:10 | 2022-07-22 20:10 | 24 | 2022-07-21 19:20 | 2022-07-21 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 95217 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10208075 | ASD-COA-GFL002-AHU067 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1121-005)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 002- AHU-A1121- |  | FM008 |  | 2022-03-01 12:44 | 2022-03-01 13:44 | 2022-03-02 13:44 | 24 | 2022-03-01 12:50 | 2022-03-01 16:00 | 190 | 570 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10162234 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FAILED -CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-02-23 21:39 | 2022-02-23 22:39 | 2022-02-24 22:39 | 24 | 2022-02-23 21:45 | 2022-02-23 23:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106914 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10652556 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-AHU-A1121-002)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-05-12 00:23 | 2022-05-12 01:23 | 2022-05-13 01:23 | 24 | 2022-05-12 00:30 | 2022-05-12 03:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2022-10691920 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AC VENT PAINT FADED URINAL AND CUBICLE AREA AG-02-22 |  | FM008 |  | 2022-05-25 16:05 | 2022-05-25 17:05 | 2022-05-26 17:05 | 24 | 2022-05-25 16:10 | 2022-05-25 23:00 | 410 | 440 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 55709 |  |  | FM11003 | Khan, Mr. Mashuque Ali | N - - - |  | Voice Communication
| CM-2022-10973088 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU-A1121-002 COOLING COIL DIRTY -AG-02-05 |  | FM008 |  | 2022-08-27 02:29 | 2022-08-27 03:29 | 2022-08-28 03:29 | 24 | 2022-08-27 02:35 | 2022-08-27 05:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2023-11806393 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU NOISY - AHU-A1121-002 – AG-02-05 |  | FM008 |  | 2023-05-19 07:03 | 2023-05-19 08:03 | 2023-05-20 08:03 | 24 | 2023-05-19 07:10 | 2023-05-19 11:10 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 133396 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11806427 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AC TOO HOT – A0-01-03 |  | FM008 |  | 2023-05-19 10:07 | 2023-05-19 11:07 | 2023-05-20 11:07 | 24 | 2023-05-19 10:15 | 2023-05-19 17:20 | 425 | 20 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 74126 | Sikdar, Mr. Kajal | N - - - |  | Voice Communication
| CM-2023-12383704 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU-A1121-002 ABNORMAL NOISE – AG-02-05 |  | FM008 |  | 2023-11-15 07:09 | 2023-11-15 08:09 | 2023-11-16 08:09 | 24 | 2023-11-15 07:15 | 2023-11-15 09:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12650457 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU-A1121-002 AG-02-05 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2024-02-13 17:09 | 2024-02-13 18:09 | 2024-02-14 18:09 | 24 | 2024-02-13 17:18 | 2024-02-13 18:35 | 77 | 154 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 138627 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11138418 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AG-02-05 |  | FM008 |  | 2022-10-28 19:39 | 2022-10-28 20:39 | 2022-10-29 20:39 | 24 | 2022-10-28 19:45 | 2022-10-28 23:45 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11931952 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – AG-02-05 |  | FM008 |  | 2023-06-29 12:55 | 2023-06-29 13:55 | 2023-06-30 13:55 | 24 | 2023-06-29 13:00 | 2023-06-29 16:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12429558 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | SUPPLY AIR FLOW LOW ALARM – (AHU-A1121-002) – |  | FM008 |  | 2023-12-01 07:32 | 2023-12-01 08:32 | 2023-12-02 08:32 | 24 | 2023-12-01 07:45 | 2023-12-01 17:30 | 585 | 1065 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 132112 | 87807 |  |  | FM7343 | Azad Hussain Ansari, | N - - - |  | Voice Communication
| CM-2024-12522024 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE,AHU-A1121-002, AG-02-05 |  | FM008 |  | 2024-01-03 12:38 | 2024-01-03 13:38 | 2024-01-04 13:38 | 24 | 2024-01-03 12:45 | 2024-01-03 18:15 | 330 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12584501 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1121-002)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2024-01-21 20:02 | 2024-01-21 21:02 | 2024-01-22 21:02 | 24 | 2024-01-21 20:10 | 2024-01-21 23:00 | 170 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM12447 | Vijaykumar Murugaiyan, | N - - - |  | E-mail
| CM-2024-12589788 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY - AHU-A1121-002 - AG-02-05 |  | FM008 |  | 2024-01-22 14:17 | 2024-01-22 15:17 | 2024-01-23 15:17 | 24 | 2024-01-22 14:25 | 2024-01-22 21:00 | 395 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10972901 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-08-26 03:19 | 2022-08-26 04:19 | 2022-08-27 04:19 | 24 | 2022-08-26 03:25 | 2022-08-26 06:30 | 185 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11113590 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AG-02-05 |  | FM008 |  | 2022-10-19 12:56 | 2022-10-19 13:56 | 2022-10-20 13:56 | 24 | 2022-10-19 13:05 | 2022-10-19 17:00 | 235 | 340 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11131283 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1121-002 AG-02-05 |  | FM008 |  | 2022-10-23 19:24 | 2022-10-23 20:24 | 2022-10-24 20:24 | 24 | 2022-10-23 19:30 | 2022-10-23 23:30 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11327064 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1121-002 – AG-02-05 |  | FM008 |  | 2022-12-28 07:48 | 2022-12-28 08:48 | 2022-12-29 08:48 | 24 | 2022-12-28 07:55 | 2022-12-28 11:00 | 185 | 555 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11787884 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1121-002 - GROUND FLOOR AREA 003 |  | FM008 |  | 2023-05-14 13:53 | 2023-05-14 14:53 | 2023-05-15 14:53 | 24 | 2023-05-14 14:00 | 2023-05-14 17:45 | 225 | 280 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11805497 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AC TOO WARM-AG-02-17 |  | FM008 |  | 2023-05-19 11:31 | 2023-05-19 12:31 | 2023-05-20 12:31 | 24 | 2023-05-19 11:40 | 2023-05-19 18:25 | 405 | 20 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 17053 |  |  | 103235 | Kumar, Mr. Pardeep | N - - - |  | Voice Communication
| CM-2023-12098747 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION FAMAGED - AHU-A1121-002 – AG-02-05 |  | FM008 |  | 2023-08-18 22:06 | 2023-08-18 23:06 | 2023-08-19 23:06 | 24 | 2023-08-18 22:10 | 2023-08-19 01:10 | 180 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12112396 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU-A1121-002 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-24 21:38 | 2023-08-24 22:38 | 2023-08-25 22:38 | 24 | 2023-08-24 21:45 | 2023-08-24 23:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2023-12235155 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AC TOO COLD – OPEN AREA FFL1 |  | FM008 |  | 2023-10-01 03:24 | 2023-10-01 04:24 | 2023-10-02 04:24 | 24 | 2023-10-01 03:30 | 2023-10-01 05:40 | 130 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | 103922 | Istiak, Mr. Shamim | N - - - |  | Voice Communication
| CM-2023-12488550 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AG-02-05 |  | FM008 |  | 2023-12-19 23:56 | 2023-12-20 00:56 | 2023-12-21 00:56 | 24 | 2023-12-20 00:05 | 2023-12-20 03:50 | 225 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 17053 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2024-12689611 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH NOT WORKING, AHU-A1121-002, AG-02-05 |  | FM008 |  | 2024-02-27 22:04 | 2024-02-27 23:04 | 2024-02-28 23:04 | 24 | 2024-02-27 22:14 | 2024-02-28 01:00 | 166 | 332 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2024-12667297 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AC TOO COLD - OPEN AREA ( SEATING) - FFL1 |  | FM008 |  | 2024-02-21 03:04 | 2024-02-21 04:04 | 2024-02-22 04:04 | 24 | 2024-02-21 03:10 | 2024-02-21 04:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 39356 | Alde, Ms. Katrina Cuasay | N - - - |  | Voice Communication
| CM-2022-10066383 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU-A1121-002 COOLING COIL DIRTY – AIR HANDLING UNIT 064 (TAG NO:AHU-A1121-002)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-01-19 19:02 | 2022-01-19 20:02 | 2022-01-20 20:02 | 24 | 2022-01-19 19:05 | 2022-01-19 23:00 | 235 | 470 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10578353 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED - AG-02-05 |  | FM008 |  | 2022-04-22 07:49 | 2022-04-22 08:50 | 2022-04-23 08:50 | 24 | 2022-04-22 07:55 | 2022-04-22 14:45 | 410 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10777500 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED TAG NO:AHU-A1121-002 |  | FM008 |  | 2022-06-25 21:35 | 2022-06-25 22:35 | 2022-06-26 22:35 | 24 | 2022-06-25 21:40 | 2022-06-25 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 106972 | 87807 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2023-11353366 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIRLEAKAGE – AHU-A1121-002 – AG-02-05 |  | FM008 |  | 2023-01-07 19:29 | 2023-01-07 20:29 | 2023-01-08 20:29 | 24 | 2023-01-07 19:40 | 2023-01-07 23:00 | 200 | 800 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10028525 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | AHU-A1121-002 RETURN BLOWER NOISY |  | FM008 |  | 2022-01-06 07:04 | 2022-01-06 08:04 | 2022-01-07 08:04 | 24 | 2022-01-06 07:10 | 2022-01-06 09:15 | 125 | 375 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 55709 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-10568549 | ASD-COA-GFL003-AHU064 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-04-19 16:20 | 2022-04-19 17:20 | 2022-04-20 17:20 | 24 | 2022-04-19 16:25 | 2022-04-19 18:30 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10160473 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED - AHU-A1121-006 – AG-02-05 |  | FM008 |  | 2022-02-21 22:24 | 2022-02-21 23:24 | 2022-02-22 23:24 | 24 | 2022-02-21 22:34 | 2022-02-21 23:55 | 81 | 243 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10223417 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 FILTER BLOCKED AG-02-05 |  | FM008 |  | 2022-03-06 19:22 | 2022-03-06 20:22 | 2022-03-07 20:22 | 24 | 2022-03-06 19:30 | 2022-03-06 21:00 | 90 | 265 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | E-mail
| CM-2022-10820722 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 – FILTER IS BLOCKED – AG-02-05 |  | FM008 |  | 2022-07-05 21:28 | 2022-07-05 22:28 | 2022-07-06 22:28 | 24 | 2022-07-05 21:35 | 2022-07-05 23:30 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 94954 | 95217 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11801197 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 ABNORMAL SOUNDS AG-02-05 |  | FM008 |  | 2023-05-18 07:16 | 2023-05-18 08:16 | 2023-05-19 08:16 | 24 | 2023-05-18 07:25 | 2023-05-18 12:00 | 275 | 1375 | 5 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 89127 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11949394 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006-CHILLED WATER LINE PAINTS FADED -CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-07-06 07:51 | 2023-07-06 08:51 | 2023-07-07 08:51 | 24 | 2023-07-06 08:00 | 2023-07-06 10:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 77406 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12386891 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 ABNORMAL NOISE |  | FM008 |  | 2023-11-17 14:15 | 2023-11-17 15:15 | 2023-11-18 15:15 | 24 | 2023-11-17 14:20 | 2023-11-17 18:00 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68485 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12829708 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2024-04-19 19:18 | 2024-04-19 20:18 | 2024-04-20 20:18 | 24 | 2024-04-19 19:25 | 2024-04-19 23:30 | 245 | 490 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-10956328 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | water leakage from ceiling & ceiling tile detached -CORRIDOR AREA OF AG-02-19 |  | FM008 |  | 2022-08-19 12:26 | 2022-08-19 13:26 | 2022-08-20 13:26 | 24 | 2022-08-19 12:35 | 2022-08-19 14:40 | 125 | 500 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95216 | 55709 |  |  | FM11003 | Khan, Mr. Mashuque Ali | N - - - |  | Voice Communication
| CM-2022-11133358 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1121-006) |  | FM008 |  | 2022-10-24 19:51 | 2022-10-24 20:51 | 2022-10-25 20:51 | 24 | 2022-10-24 20:00 | 2022-10-24 23:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-12390463 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 DUCT INSULATION DAMAGED AG-02-05 |  | FM008 |  | 2023-11-19 20:10 | 2023-11-19 21:10 | 2023-11-20 21:10 | 24 | 2023-11-19 20:15 | 2023-11-19 23:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 95217 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2024-12557395 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AG-02-05 |  | FM008 |  | 2024-01-13 02:54 | 2024-01-13 03:54 | 2024-01-14 03:54 | 24 | 2024-01-13 03:05 | 2024-01-13 05:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM12447 | Vijaykumar Murugaiyan, | N - - - |  | Voice Communication
| CM-2022-10969572 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-08-27 20:09 | 2022-08-27 21:09 | 2022-08-28 21:09 | 24 | 2022-08-27 20:15 | 2022-08-27 23:00 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-11113589 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AG-02-05 |  | FM008 |  | 2022-10-19 12:54 | 2022-10-19 13:54 | 2022-10-20 13:54 | 24 | 2022-10-19 13:00 | 2022-10-19 15:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11255153 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006-SUPPLY DUCT CANVAS AIR LEAKAGE |  | FM008 |  | 2022-12-06 19:31 | 2022-12-06 20:31 | 2022-12-07 20:31 | 24 | 2022-12-06 19:40 | 2022-12-06 22:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95217 | 17053 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | BMS
| CM-2023-12099047 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSOLATION DAMAGED, AHU-A1121-006,AG-02-05 |  | FM008 |  | 2023-08-19 20:24 | 2023-08-19 21:24 | 2023-08-20 21:24 | 24 | 2023-08-19 20:30 | 2023-08-19 22:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12163467 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU CABIN LAMP HOLDER FAULTY - AHU-A1121-006 - MECHANICAL ROOM AG-02-05 |  | FM008 |  | 2023-09-07 13:10 | 2023-09-07 14:10 | 2023-09-08 14:10 | 24 | 2023-09-07 13:20 | 2023-09-07 15:10 | 110 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | TIMER FAULTY | TIMER NOT WORKING | SWITCH HAS BEEN REPLACED | 17573 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12254584 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | DAMAGED/BEND/MISALLIGHN/MISSING RETURN AIR GRILLS - BESIDE LAVITA CAFÉ,IN FRONT OF WOMEN WASHROOM(A1 02 18) AND INFRONT OF STAIRS(A A101) |  | FM008 |  | 2023-10-05 15:37 | 2023-10-05 16:37 | 2023-10-06 16:37 | 24 | 2023-10-05 15:45 | 2023-10-06 00:35 | 530 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 105233 | 87807 |  |  | 88447 | Kho, Mr. Marino Pacana | N - - - |  | E-mail
| CM-2024-12532723 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE, AHU-A1121-006, AG-02-05 |  | FM008 |  | 2024-01-03 07:58 | 2024-01-03 08:58 | 2024-01-04 08:58 | 24 | 2024-01-03 08:05 | 2024-01-03 10:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12319847 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-24 14:52 | 2023-10-24 15:52 | 2023-10-25 15:52 | 24 | 2023-10-24 15:00 | 2023-10-24 17:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2023-12363715 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 CHILLED WATER LINE PAINT FADED – AG-02-05 |  | FM008 |  | 2023-11-07 08:33 | 2023-11-07 09:33 | 2023-11-08 09:33 | 24 | 2023-11-07 08:40 | 2023-11-07 13:00 | 260 | 530 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2024-12671638 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 FILTER DIRTY AG-02-05 |  | FM008 |  | 2024-02-22 08:23 | 2024-02-22 09:23 | 2024-02-23 09:23 | 24 | 2024-02-22 08:30 | 2024-02-22 18:30 | 600 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10147387 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY – AHU-A1121-006 – AG-02-05 |  | FM008 |  | 2022-02-18 11:05 | 2022-02-18 12:05 | 2022-02-19 12:05 | 24 | 2022-02-18 11:10 | 2022-02-18 14:30 | 200 | 765 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10252922 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 – COOLING COIL IS DIRTY – AG-02-05 |  | FM008 |  | 2022-03-16 19:29 | 2022-03-16 20:29 | 2022-03-17 20:29 | 24 | 2022-03-16 19:35 | 2022-03-16 23:00 | 205 | 615 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94954 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10568553 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-006 – AG-02-05 |  | FM008 |  | 2022-04-19 16:39 | 2022-04-19 17:39 | 2022-04-20 17:39 | 24 | 2022-04-19 16:45 | 2022-04-19 18:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10593048 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | Low duct support ( MS- Angle ) can cause injury to someone's head if not noticed. Cover with some soft removable covering. |  | FM008 |  | 2022-04-28 13:46 | 2022-04-28 14:46 | 2022-04-29 14:46 | 24 | 2022-04-28 13:55 | 2022-04-28 16:00 | 125 | 70 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 17053 |  |  | 116311 | Ansari, Mr. Mohammad Ziaul Haque | N - - - |  | E-mail
| CM-2022-10714617 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT IS FADED - AHU-A1121-006 – AG -02-05 |  | FM008 |  | 2022-06-03 19:25 | 2022-06-03 20:25 | 2022-06-04 20:25 | 24 | 2022-06-03 19:30 | 2022-06-03 23:00 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 17573 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2022-10934632 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 COOLING COIL DIRTY |  | FM008 |  | 2022-08-12 19:22 | 2022-08-12 20:22 | 2022-08-13 20:22 | 24 | 2022-08-12 19:30 | 2022-08-12 23:00 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-11015561 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – AG-02-05 |  | FM008 |  | 2022-09-13 16:34 | 2022-09-13 17:34 | 2022-09-14 17:34 | 24 | 2022-09-13 16:40 | 2022-09-13 18:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 105233 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2022-11330514 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE-AG-02-05 |  | FM008 |  | 2022-12-31 00:01 | 2022-12-31 01:01 | 2023-01-01 01:01 | 24 | 2022-12-31 00:10 | 2022-12-31 02:00 | 110 | 440 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | WATER LEAKAGE | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11668221 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 CHILLED WATER LINE PAINT FADED AG-02-05 |  | FM008 |  | 2023-04-16 07:54 | 2023-04-16 08:54 | 2023-04-17 08:54 | 24 | 2023-04-16 08:00 | 2023-04-16 11:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-10032806 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | AHU-A1121-006 COOLING COIL DIRTY |  | FM008 |  | 2022-01-08 19:14 | 2022-01-08 20:14 | 2022-01-09 20:14 | 24 | 2022-01-08 19:20 | 2022-01-08 23:20 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10067386 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-01-20 18:53 | 2022-01-20 19:53 | 2022-01-21 19:53 | 24 | 2022-01-20 19:00 | 2022-01-20 23:00 | 240 | 480 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | BMS
| CM-2022-10157889 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AG-02-05 |  | FM008 |  | 2022-02-23 01:29 | 2022-02-23 02:29 | 2022-02-24 02:29 | 24 | 2022-02-23 01:35 | 2022-02-23 04:30 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10672398 | ASD-COA-GFL003-AHU068 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY-AHU-A1121-006-AG-02-05 - AG-02-05 (CM-2022-04-1952) |  | FM008 |  | 2022-05-15 23:58 | 2022-05-16 00:58 | 2022-05-17 00:58 | 24 | 2022-05-16 00:05 | 2022-05-16 01:30 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 55709 |  |  | FM5676 | ROSHIN | - - - |  | Voice Communication
| CM-2022-10223418 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 FILTER BLOCKED AG-02-05 |  | FM008 |  | 2022-03-06 19:24 | 2022-03-06 20:24 | 2022-03-07 20:24 | 24 | 2022-03-06 19:30 | 2022-03-06 23:30 | 240 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10253141 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-010 – AG-02-05 |  | FM008 |  | 2022-03-17 19:16 | 2022-03-17 20:16 | 2022-03-18 20:16 | 24 | 2022-03-17 19:25 | 2022-03-17 23:00 | 215 | 645 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10672624 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | MOTOR BELT WOBBLING-AIR HANDLING UNIT 072 (TAG NO:AHU-A1121-010)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-05-17 08:55 | 2022-05-17 09:55 | 2022-05-18 09:55 | 24 | 2022-05-17 09:05 | 2022-05-17 11:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10923581 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | SUPPLY VFD DISPLAY ERROR- AG-02-05 |  | FM008 |  | 2022-08-09 08:01 | 2022-08-09 09:01 | 2022-08-10 09:01 | 24 | 2022-08-09 08:05 | 2022-08-09 09:34 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | VFD FAILURE | VFD HAS BEEN REPLACED | 17333 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11210819 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010-CHILLED WATER LINIE PAINT FADED-AG-02-05 |  | FM008 |  | 2022-11-21 20:35 | 2022-11-21 21:35 | 2022-11-22 21:35 | 24 | 2022-11-21 20:40 | 2022-11-21 22:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95217 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11818855 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | FILTER BLOCKED, AHU-A1121-010, AG-02-05 |  | FM008 |  | 2023-05-24 01:03 | 2023-05-24 02:03 | 2023-05-25 02:03 | 24 | 2023-05-24 01:10 | 2023-05-24 04:25 | 195 | 335 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12035540 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | FILTER DIRTY -AG-02-05 |  | FM008 |  | 2023-08-02 08:08 | 2023-08-02 09:08 | 2023-08-03 09:08 | 24 | 2023-08-02 08:10 | 2023-08-02 10:00 | 110 | 274 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-12183706 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010-DUCT INSULATION DAMAGE -AG-02-05 |  | FM008 |  | 2023-09-11 22:27 | 2023-09-11 23:27 | 2023-09-12 23:27 | 24 | 2023-09-11 22:30 | 2023-09-12 00:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2023-12229565 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | CANVAS AIR LEAKAGE - AHU-A1121-010 -AG-02-05 |  | FM008 |  | 2023-09-29 07:09 | 2023-09-29 08:09 | 2023-09-30 08:09 | 24 | 2023-09-29 07:12 | 2023-09-29 09:30 | 138 | 276 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106914 | 87807 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12534012 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE, AHU-A1121-010, AG-02-05 |  | FM008 |  | 2024-01-03 07:58 | 2024-01-03 08:58 | 2024-01-04 08:58 | 24 | 2024-01-03 08:05 | 2024-01-03 10:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10973050 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010- COOLING COIL DIRTY |  | FM008 |  | 2022-08-26 19:34 | 2022-08-26 20:34 | 2022-08-27 20:34 | 24 | 2022-08-26 19:40 | 2022-08-26 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11009680 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 COOLING COIL DIRTY |  | FM008 |  | 2022-09-11 06:59 | 2022-09-11 07:59 | 2022-09-12 07:59 | 24 | 2022-09-11 07:10 | 2022-09-11 11:00 | 230 | 405 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 17053 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-11015269 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 AHU LAMP IS NOT ILLUMINATING |  | FM008 |  | 2022-09-12 19:04 | 2022-09-12 20:04 | 2022-09-13 20:04 | 24 | 2022-09-12 19:14 | 2022-09-12 22:24 | 190 | 188 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11579099 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU072 DP1 FILTER ALARM -AG-02-05 |  | FM008 |  | 2023-03-21 13:25 | 2023-03-21 14:25 | 2023-03-22 14:25 | 24 | 2023-03-21 13:30 | 2023-03-21 15:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11784285 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 – UNUSUAL NOISE FROM AHU – AG-02-05 |  | FM008 |  | 2023-05-11 08:06 | 2023-05-11 09:06 | 2023-05-12 09:06 | 24 | 2023-05-11 08:15 | 2023-05-11 13:35 | 320 | 1505 | 5 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94954 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12110209 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | SUPPLY AIR FLOW NOT ACHIEVING AS PER DESIGN - AHU-A1121-002 - AG-02-05 |  | FM008 |  | 2023-08-22 08:27 | 2023-08-22 09:27 | 2023-08-23 09:27 | 24 | 2023-08-22 08:35 | 2023-08-22 18:30 | 595 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | E-mail
| CM-2023-12390462 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 DUCT INSULATION DAMAGED AG-02-05 |  | FM008 |  | 2023-11-19 20:08 | 2023-11-19 21:08 | 2023-11-20 21:08 | 24 | 2023-11-19 20:15 | 2023-11-19 23:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 95217 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2024-12557396 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AG-02-05 |  | FM008 |  | 2024-01-13 02:56 | 2024-01-13 03:56 | 2024-01-14 03:56 | 24 | 2024-01-13 03:00 | 2024-01-13 05:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 17053 |  |  | FM12447 | Vijaykumar Murugaiyan, | N - - - |  | Voice Communication
| CM-2023-12112397 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-24 21:40 | 2023-08-24 22:40 | 2023-08-25 22:40 | 24 | 2023-08-24 21:45 | 2023-08-24 23:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2024-12625229 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2024-02-04 20:27 | 2024-02-04 21:27 | 2024-02-05 21:27 | 24 | 2024-02-04 20:35 | 2024-02-04 23:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12358530 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | CABIN LAMP NOT WORKING - AHU-A1121-010 - AG-02-05 |  | FM008 |  | 2023-11-07 01:32 | 2023-11-07 02:32 | 2023-11-08 02:32 | 24 | 2023-11-07 01:40 | 2023-11-07 04:35 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12326094 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-10-29 01:14 | 2023-10-29 02:14 | 2023-10-30 02:14 | 24 | 2023-10-29 01:20 | 2023-10-29 02:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2023-12363716 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 CHILLED WATER LINE PAINT FADED – AG-02-05 |  | FM008 |  | 2023-11-07 08:36 | 2023-11-07 09:36 | 2023-11-08 09:36 | 24 | 2023-11-07 08:40 | 2023-11-07 13:00 | 260 | 530 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12364115 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AIR HANDLING UNIT 072 (TAG NO:AHU-A1121-010)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-11-09 00:59 | 2023-11-09 01:59 | 2023-11-10 01:59 | 24 | 2023-11-09 01:05 | 2023-11-09 03:00 | 115 | 345 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 119320 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12532416 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM RELEASE SIDE, AHU-A1121-010,AG-02-05 |  | FM008 |  | 2024-01-02 07:39 | 2024-01-02 08:39 | 2024-01-03 08:39 | 24 | 2024-01-02 07:45 | 2024-01-02 16:30 | 525 | 590 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 124475 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-10048538 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 SUPPLY AND RETURN SENSOR TUBE FAULTY - AG-02-05 |  | FM008 |  | 2022-01-14 02:15 | 2022-01-14 03:15 | 2022-01-15 03:15 | 24 | 2022-01-14 02:20 | 2022-01-14 04:00 | 100 | 100 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 17154 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10208098 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU072 COOLING COIL BLOCKED – AG-02-05 |  | FM008 |  | 2022-03-01 16:06 | 2022-03-01 17:06 | 2022-03-02 17:06 | 24 | 2022-03-01 16:10 | 2022-03-01 18:50 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106976 | 87807 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10364322 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY - AHU-A1121-010 – AG-02-05 |  | FM008 |  | 2022-04-15 08:06 | 2022-04-15 09:06 | 2022-04-16 09:06 | 24 | 2022-04-15 08:15 | 2022-04-15 12:15 | 240 | 480 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11041593 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 – FILTER DIRTY |  | FM008 |  | 2022-09-24 20:46 | 2022-09-24 21:46 | 2022-09-25 21:46 | 24 | 2022-09-24 20:50 | 2022-09-24 21:50 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11570439 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | DP1-B FINAL FILTER STATUS ALARM AHU-A1121-010 |  | FM008 |  | 2023-03-20 15:34 | 2023-03-20 16:34 | 2023-03-21 16:34 | 24 | 2023-03-20 15:40 | 2023-03-20 17:30 | 110 | 115 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11668220 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 CHILLED WATER LINE PAINT FADED AG-02-05 |  | FM008 |  | 2023-04-16 07:52 | 2023-04-16 08:52 | 2023-04-17 08:52 | 24 | 2023-04-16 08:00 | 2023-04-16 11:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-10042158 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | AHU-A1121-010 – COIL IS DIRTY – AG-02-05 |  | FM008 |  | 2022-01-11 20:15 | 2022-01-11 21:15 | 2022-01-12 21:15 | 24 | 2022-01-11 20:20 | 2022-01-11 23:45 | 205 | 615 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10573821 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY- AHU-A1121-010 –AG-02-05 |  | FM008 |  | 2022-04-19 07:53 | 2022-04-19 08:53 | 2022-04-20 08:53 | 24 | 2022-04-19 08:00 | 2022-04-19 14:00 | 360 | 355 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10843687 | ASD-COA-GFL003-AHU072 | AIR HANDLING UNIT-05 | FILTER BLOCKED - AHU-A1121-010) -CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-07-17 08:05 | 2022-07-17 09:05 | 2022-07-18 09:05 | 24 | 2022-07-17 08:10 | 2022-07-17 11:30 | 200 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 121959 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10060067 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-012 – AG-02-05 |  | FM008 |  | 2022-01-20 21:13 | 2022-01-20 22:13 | 2022-01-21 22:13 | 24 | 2022-01-20 21:20 | 2022-01-20 23:55 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 55709 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10275369 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | AHU-A1121-012 - COOLING COIL DIRTY - AG-02-05 |  | FM008 |  | 2022-03-21 18:55 | 2022-03-21 19:55 | 2022-03-22 19:55 | 24 | 2022-03-21 19:00 | 2022-03-21 22:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10949960 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | AHU-A1121-012- CHILLED WATER LINE PAINT FADED AG-02-05 |  | FM008 |  | 2022-08-15 19:59 | 2022-08-15 20:59 | 2022-08-16 20:59 | 24 | 2022-08-15 20:04 | 2022-08-15 23:10 | 186 | 306 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 17154 | 55709 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2022-10954316 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY-AG-02-05 |  | FM008 |  | 2022-08-18 21:57 | 2022-08-18 22:57 | 2022-08-19 22:57 | 24 | 2022-08-18 22:05 | 2022-08-18 23:55 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 55709 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-11691192 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AG 02 04 |  | FM008 |  | 2023-04-21 07:25 | 2023-04-21 08:25 | 2023-04-22 08:25 | 24 | 2023-04-21 07:30 | 2023-04-21 10:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12189299 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – AG-02-05 |  | FM008 |  | 2023-09-16 09:21 | 2023-09-16 10:21 | 2023-09-17 10:21 | 24 | 2023-09-16 09:25 | 2023-09-16 17:30 | 485 | 310 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 105233 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12321660 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | AHU-A1121-012 FILTER BLOCKED |  | FM008 |  | 2023-10-24 19:35 | 2023-10-24 20:35 | 2023-10-25 20:35 | 24 | 2023-10-24 19:40 | 2023-10-24 22:50 | 190 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11103444 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-AHU-A1121-012)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-10-14 19:29 | 2022-10-14 20:29 | 2022-10-15 20:29 | 24 | 2022-10-14 19:35 | 2022-10-14 22:30 | 175 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12103349 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION BROKEN – AG-02-05 |  | FM008 |  | 2023-08-21 19:18 | 2023-08-21 20:18 | 2023-08-22 20:18 | 24 | 2023-08-21 19:25 | 2023-08-21 22:00 | 155 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-12199798 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY -AG-02-05 |  | FM008 |  | 2023-09-18 07:37 | 2023-09-18 08:37 | 2023-09-19 08:37 | 24 | 2023-09-18 07:45 | 2023-09-18 14:00 | 375 | 595 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-12209051 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | INSULATION DAMAGED AHU-A1121-012 |  | FM008 |  | 2023-09-23 07:37 | 2023-09-23 08:37 | 2023-09-24 08:37 | 24 | 2023-09-23 07:40 | 2023-09-23 12:00 | 260 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-12380731 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2023-11-13 10:30 | 2023-11-13 11:29 | 2023-11-14 11:29 | 24 | 2023-11-13 10:35 | 2023-11-13 15:00 | 265 | 965 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12406501 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -- AG-02-05 |  | FM008 |  | 2023-11-22 19:38 | 2023-11-22 20:38 | 2023-11-23 20:38 | 24 | 2023-11-22 19:45 | 2023-11-22 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 138627 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12525063 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1121-012 – AG-02-05 |  | FM008 |  | 2023-12-31 23:28 | 2024-01-01 00:28 | 2024-01-02 00:28 | 24 | 2023-12-31 23:35 | 2024-01-01 01:35 | 120 | 205 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-10995286 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AIR HANDLING UNIT 074 (TAG NO:AHU-A1121-012)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-09-05 10:02 | 2022-09-05 11:02 | 2022-09-06 11:02 | 24 | 2022-09-05 10:10 | 2022-09-05 12:30 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17154 | 94954 |  |  | FM8202 | SHREE | N - - - |  | Voice Communication
| CM-2022-11064348 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | AHU-A1121-012 – FILTER BLOCKED- - |  | FM008 |  | 2022-09-28 02:03 | 2022-09-28 03:03 | 2022-09-29 03:03 | 24 | 2022-09-28 02:10 | 2022-09-28 03:10 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 94953 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11247926 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE - AHU-A1121-012 – AG-02-05 |  | FM008 |  | 2022-12-05 19:42 | 2022-12-05 20:42 | 2022-12-06 20:42 | 24 | 2022-12-05 19:50 | 2022-12-05 23:05 | 195 | 730 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17573 | 17053 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-11797188 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | ABNORMAL SOUND-AHU-A1121-012)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-05-16 07:41 | 2023-05-16 08:41 | 2023-05-17 08:41 | 24 | 2023-05-16 07:45 | 2023-05-16 12:00 | 255 | 1275 | 5 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11823641 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | FILTER BLOCKED, AHU-A1121-012, AG-02-05 |  | FM008 |  | 2023-05-24 01:02 | 2023-05-24 02:02 | 2023-05-25 02:02 | 24 | 2023-05-24 01:10 | 2023-05-24 06:15 | 305 | 320 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12850478 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | ABNORMAL SOUND -AHU-A1121-012 (AG-02-05) |  | FM008 |  | 2024-04-27 07:35 | 2024-04-27 08:35 | 2024-04-28 08:35 | 24 | 2024-04-27 07:45 | 2024-04-27 15:00 | 435 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 77406 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12361387 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – AHU-A1121-012 – AG-02-05 |  | FM008 |  | 2023-11-05 20:11 | 2023-11-05 21:11 | 2023-11-06 21:11 | 24 | 2023-11-05 20:15 | 2023-11-06 00:15 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12479931 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | :(AHU-A1121-012)-COOLING COIL DIRTY (AG-02-05) |  | FM008 |  | 2023-12-16 01:42 | 2023-12-16 02:42 | 2023-12-17 02:42 | 24 | 2023-12-16 01:50 | 2023-12-16 05:30 | 220 | 725 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-10308701 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-29 14:46 | 2022-03-29 15:46 | 2022-03-30 15:46 | 24 | 2022-03-29 14:55 | 2022-03-29 16:45 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 55709 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10171487 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1121-012 AG-02-05 |  | FM008 |  | 2022-02-25 00:23 | 2022-02-25 01:23 | 2022-02-26 01:23 | 24 | 2022-02-25 00:30 | 2022-02-25 03:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 85125 | 55709 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2022-10924528 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-08-08 22:08 | 2022-08-08 23:08 | 2022-08-09 23:08 | 24 | 2022-08-08 22:15 | 2022-08-08 23:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | BMS
| CM-2022-10949610 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AG-02-05 |  | FM008 |  | 2022-08-15 16:16 | 2022-08-15 17:17 | 2022-08-16 17:17 | 24 | 2022-08-15 16:25 | 2022-08-15 18:45 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 55709 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10031566 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-01-06 19:32 | 2022-01-06 20:32 | 2022-01-07 20:32 | 24 | 2022-01-06 19:40 | 2022-01-06 23:40 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10573822 | ASD-COA-GFL003-AHU074 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY- AHU-A1121-012–AG-02-05 |  | FM008 |  | 2022-04-19 07:55 | 2022-04-19 08:55 | 2022-04-20 08:55 | 24 | 2022-04-19 08:00 | 2022-04-19 11:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10202376 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT DIRTY AIR HANDLING UNIT 183 (TAG NO:AHU-A1155-001)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-02-28 20:28 | 2022-02-28 21:28 | 2022-03-01 21:28 | 24 | 2022-02-28 20:35 | 2022-02-28 22:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17154 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10568901 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU-A1155-001 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-04-21 12:52 | 2022-04-21 13:52 | 2022-04-22 13:52 | 24 | 2022-04-21 13:00 | 2022-04-21 16:30 | 210 | 590 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10831340 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | FILTER DIRTY -AG-02-40 |  | FM008 |  | 2022-07-16 19:03 | 2022-07-16 20:03 | 2022-07-17 20:03 | 24 | 2022-07-16 19:10 | 2022-07-16 23:00 | 230 | 370 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 95217 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-11041423 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU-A1155-001 - DP1 FILTER IS DIRTY – AG-02-40 |  | FM008 |  | 2022-09-23 22:05 | 2022-09-23 23:05 | 2022-09-24 23:05 | 24 | 2022-09-23 22:15 | 2022-09-23 23:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94954 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11696588 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1155-001, AG-02-40 |  | FM008 |  | 2023-04-21 11:07 | 2023-04-21 12:07 | 2023-04-22 12:07 | 24 | 2023-04-21 11:15 | 2023-04-21 14:00 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 124475 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12017202 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | CHILL WATER LINE PIPE PAINT FADED – AHU-1155-001 – AG-02-40 |  | FM008 |  | 2023-07-29 13:17 | 2023-07-29 14:17 | 2023-07-30 14:17 | 24 | 2023-07-29 13:25 | 2023-07-29 17:00 | 215 | 355 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12325564 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1155-001 – AG-02-40 |  | FM008 |  | 2023-10-27 16:08 | 2023-10-27 17:08 | 2023-10-28 17:08 | 24 | 2023-10-27 16:15 | 2023-10-27 18:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 87807 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2023-12345546 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU-A1155-001 COIL DIRTY AG-02-40 |  | FM008 |  | 2023-11-03 20:51 | 2023-11-03 21:51 | 2023-11-04 21:51 | 24 | 2023-11-03 21:00 | 2023-11-04 01:00 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12366355 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY - AHU-A1155-001 – AG-02-40 |  | FM008 |  | 2023-11-11 09:20 | 2023-11-11 10:20 | 2023-11-12 10:20 | 24 | 2023-11-11 09:25 | 2023-11-11 10:25 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 133396 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12410796 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AG-02-40 |  | FM008 |  | 2023-11-26 03:01 | 2023-11-26 04:01 | 2023-11-27 04:01 | 24 | 2023-11-26 03:10 | 2023-11-26 05:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM12447 | Vijaykumar Murugaiyan, | N - - - |  | Voice Communication
| CM-2023-12112124 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU-A1155-001 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-23 22:27 | 2023-08-23 23:27 | 2023-08-24 23:27 | 24 | 2023-08-23 22:35 | 2023-08-24 00:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-11162310 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU COIL DIRTY - AHU-A1155-001 |  | FM008 |  | 2022-11-06 00:29 | 2022-11-06 01:29 | 2022-11-07 01:29 | 24 | 2022-11-06 00:35 | 2022-11-06 04:30 | 235 | 705 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11459561 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1155-001 , AG-02-40 |  | FM008 |  | 2023-02-14 07:26 | 2023-02-14 08:26 | 2023-02-15 08:26 | 24 | 2023-02-14 07:30 | 2023-02-14 11:00 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 95217 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2024-12591801 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU-A1155-001 FILTER DIRTY |  | FM008 |  | 2024-01-24 00:22 | 2024-01-24 01:22 | 2024-01-25 01:22 | 24 | 2024-01-24 00:30 | 2024-01-24 03:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 95217 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12488506 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-19 20:31 | 2023-12-19 21:31 | 2023-12-20 21:31 | 24 | 2023-12-19 20:35 | 2023-12-19 23:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12769197 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | Mechanical room is negatively pressurized impacting room door closing and may have equal impact to AHU/FCU panels. AG-02-40 |  | FM008 |  | 2024-03-26 13:59 | 2024-03-26 14:59 | 2024-03-27 14:59 | 24 | 2024-03-26 14:05 | 2024-03-26 16:30 | 145 | 195 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 95217 |  |  | 107414 | Kabuusu, Mr. Ronald Tonny | N - - - |  | E-mail
| CM-2022-10708871 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS FILTERS 936-AIR HANDLING UNIT 183 (TAG NO:AHU-A1155-001)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1155.GNDP1.IBFE02.AHU001.SYSALM.DP1 / |  | FM008 |  | 2022-05-30 16:33 | 2022-05-30 17:33 | 2022-05-31 17:33 | 24 | 2022-05-30 16:40 | 2022-05-30 18:50 | 130 | 75 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2022-10142251 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY -AG-02-40 |  | FM008 |  | 2022-02-14 19:31 | 2022-02-14 20:31 | 2022-02-15 20:31 | 24 | 2022-02-14 19:40 | 2022-02-14 22:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10578652 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | CHILL WATER LINE PIPE PAINT IS FADED - AHU-A1155-001 - MECHANICAL ROOM AG-02-40 |  | FM008 |  | 2022-04-22 15:20 | 2022-04-22 16:20 | 2022-04-23 16:20 | 24 | 2022-04-22 15:25 | 2022-04-22 18:15 | 170 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10677398 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR IS DAMAGED |  | FM008 |  | 2022-05-20 14:29 | 2022-05-20 15:29 | 2022-05-21 15:29 | 24 | 2022-05-20 14:40 | 2022-05-20 16:04 | 84 | 168 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10713810 | ASD-COA-GFL003-AHU183 | AIR HANDLING UNIT-05 | DRAIN LINE PIT DIRTY –AG-02-40-HU-A1155-001)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-06-04 21:58 | 2022-06-04 22:58 | 2022-06-05 22:58 | 24 | 2022-06-04 22:05 | 2022-06-04 23:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2022-10305411 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1155-002 – AG-02-40 |  | FM008 |  | 2022-03-28 10:19 | 2022-03-28 11:19 | 2022-03-29 11:19 | 24 | 2022-03-28 10:25 | 2022-03-28 13:15 | 170 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | E-mail
| CM-2022-10661342 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 – DP1 FILTER ALARM ACTIVATED-- |  | FM008 |  | 2022-05-14 06:20 | 2022-05-14 07:20 | 2022-05-15 07:20 | 24 | 2022-05-14 06:25 | 2022-05-14 09:00 | 155 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10713010 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-AHU-A1155-002)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-06-04 19:23 | 2022-06-04 20:23 | 2022-06-05 20:23 | 24 | 2022-06-04 19:25 | 2022-06-04 21:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2022-11041424 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 - DP1 FILTER IS DIRTY – AG-02-40 |  | FM008 |  | 2022-09-23 22:07 | 2022-09-23 23:07 | 2022-09-24 23:07 | 24 | 2022-09-23 22:15 | 2022-09-23 23:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11611955 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-04-01 20:02 | 2023-04-01 21:02 | 2023-04-02 21:02 | 24 | 2023-04-01 20:10 | 2023-04-01 23:00 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-11654867 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY - AHU-A11155.002 - A1 03A 02 |  | FM008 |  | 2023-04-13 07:23 | 2023-04-13 08:23 | 2023-04-14 08:23 | 24 | 2023-04-13 07:25 | 2023-04-13 12:40 | 315 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-11696589 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1155-002, AG-02-40 |  | FM008 |  | 2023-04-21 11:09 | 2023-04-21 12:09 | 2023-04-22 12:09 | 24 | 2023-04-21 11:15 | 2023-04-21 14:30 | 195 | 390 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12017203 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | CHILL WATER LINE PIPE PAINT FADED – AHU-1155-002 – AG-02-40 |  | FM008 |  | 2023-07-29 13:20 | 2023-07-29 14:20 | 2023-07-30 14:20 | 24 | 2023-07-29 13:25 | 2023-07-29 17:00 | 215 | 355 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 17573 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12281864 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | BELT WOBBLING-AIR HANDLING UNIT 184 (TAG NO:AHU-A1155-002)-AG-02-14 |  | FM008 |  | 2023-10-13 14:26 | 2023-10-13 15:26 | 2023-10-14 15:26 | 24 | 2023-10-13 14:35 | 2023-10-13 17:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | VIBRATION OF EQUIPMENT DUE TO LOOSE PARTS | RECTIFIED | 17336 | 87807 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-12325565 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1155-002 – AG-02-40 |  | FM008 |  | 2023-10-27 16:09 | 2023-10-27 17:09 | 2023-10-28 17:09 | 24 | 2023-10-27 16:15 | 2023-10-27 18:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 87807 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2023-12364349 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | LIGHTING SWITCH FAULTY |  | FM008 |  | 2023-11-09 15:23 | 2023-11-09 16:23 | 2023-11-10 16:23 | 24 | 2023-11-09 15:27 | 2023-11-09 17:50 | 143 | 286 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68485 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12366893 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY A1-03A-03 |  | FM008 |  | 2023-11-10 13:24 | 2023-11-10 14:24 | 2023-11-11 14:24 | 24 | 2023-11-10 13:27 | 2023-11-10 17:30 | 243 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12651997 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY, A1-03A-02 |  | FM008 |  | 2024-02-17 13:06 | 2024-02-17 14:06 | 2024-02-18 14:06 | 24 | 2024-02-17 13:15 | 2024-02-17 18:00 | 285 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-11177877 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORING-AG-02-40 |  | FM008 |  | 2022-11-12 13:12 | 2022-11-12 14:12 | 2022-11-13 14:12 | 24 | 2022-11-12 13:18 | 2022-11-12 15:00 | 102 | 187 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11244734 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY -A1-03A-03 |  | FM008 |  | 2022-12-04 14:16 | 2022-12-04 15:16 | 2022-12-05 15:16 | 24 | 2022-12-04 14:20 | 2022-12-04 17:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11303594 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE – AG-02-40 |  | FM008 |  | 2022-12-25 19:10 | 2022-12-25 20:10 | 2022-12-26 20:10 | 24 | 2022-12-25 19:20 | 2022-12-25 22:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106914 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11762817 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1155-002 - AG-02-40 |  | FM008 |  | 2023-05-06 22:24 | 2023-05-06 23:24 | 2023-05-07 23:24 | 24 | 2023-05-06 22:30 | 2023-05-06 23:50 | 80 | 160 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12062935 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - AHU-A1155-002 – AG-02-40 |  | FM008 |  | 2023-08-09 14:50 | 2023-08-09 15:50 | 2023-08-10 15:50 | 24 | 2023-08-09 14:58 | 2023-08-09 18:20 | 202 | 177 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 87807 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2023-12057244 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU LIGHTING SWITCH AHU-A1155-002 AG-02-04 |  | FM008 |  | 2023-08-07 19:18 | 2023-08-07 20:18 | 2023-08-08 20:18 | 24 | 2023-08-07 19:27 | 2023-08-07 22:25 | 178 | 356 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 87807 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-12112125 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-23 22:33 | 2023-08-23 23:33 | 2023-08-24 23:33 | 24 | 2023-08-23 22:40 | 2023-08-24 00:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12366895 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY A1-03A-02 |  | FM008 |  | 2023-11-10 13:25 | 2023-11-10 14:25 | 2023-11-11 14:25 | 24 | 2023-11-10 13:30 | 2023-11-10 17:30 | 240 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106972 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12585810 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 ABNORMAL NOISE AG-02-40 |  | FM008 |  | 2024-01-23 08:40 | 2024-01-23 09:40 | 2024-01-24 09:40 | 24 | 2024-01-23 08:45 | 2024-01-23 18:30 | 585 | 425 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 89127 | 95217 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12592014 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY-A1-03A-02 |  | FM008 |  | 2024-01-24 13:48 | 2024-01-24 14:48 | 2024-01-25 14:48 | 24 | 2024-01-24 13:55 | 2024-01-24 16:00 | 125 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 95217 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12592016 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY-A1-03A-03 |  | FM008 |  | 2024-01-24 13:50 | 2024-01-24 14:50 | 2024-01-25 14:50 | 24 | 2024-01-24 13:55 | 2024-01-24 16:13 | 138 | 284 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 95217 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10932911 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 – DRAIN BIT IS BLOCKED – AG-02-40 |  | FM008 |  | 2022-08-13 12:24 | 2022-08-13 13:24 | 2022-08-14 13:24 | 24 | 2022-08-13 12:34 | 2022-08-13 15:32 | 178 | 356 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 94954 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11077262 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS |  | FM008 |  | 2022-10-03 15:36 | 2022-10-03 16:36 | 2022-10-04 16:36 | 24 | 2022-10-03 15:40 | 2022-10-03 20:00 | 260 | 120 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11180006 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 – RETURN SIDE MOTOR COOLING FAN DAMAGED-AG-02-40 |  | FM008 |  | 2022-11-13 07:51 | 2022-11-13 08:51 | 2022-11-14 08:51 | 24 | 2022-11-13 08:00 | 2022-11-13 13:00 | 300 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11469561 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE – AHU-A1155-002 ,AG-02-40 |  | FM008 |  | 2023-02-17 20:31 | 2023-02-17 21:31 | 2023-02-18 21:31 | 24 | 2023-02-17 20:40 | 2023-02-17 23:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11993888 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | FILTER ALARM - AHU-A1155-002 - AG 02 40 |  | FM008 |  | 2023-07-18 08:48 | 2023-07-18 09:48 | 2023-07-19 09:48 | 24 | 2023-07-18 08:55 | 2023-07-18 13:15 | 260 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 132112 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12278448 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | ABNORMAL SOUND - AHU-A1155-002 --AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-10-12 07:38 | 2023-10-12 08:38 | 2023-10-13 08:38 | 24 | 2023-10-12 07:45 | 2023-10-12 14:00 | 375 | 1125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 87807 |  |  | FM8044 | Rajesh Janardhanan Chettiyar, | N - - - |  | Voice Communication
| CM-2024-12655114 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY, A1-03A-03 |  | FM008 |  | 2024-02-17 13:06 | 2024-02-17 14:06 | 2024-02-18 14:06 | 24 | 2024-02-17 13:15 | 2024-02-17 15:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2024-12767982 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | SUPPLY AIR LOW ALARM (TAG NO:AHU-A1155-002)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2024-03-25 08:01 | 2024-03-25 09:01 | 2024-03-26 09:01 | 24 | 2024-03-25 08:05 | 2024-03-25 10:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12462166 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY A1-03A-03 |  | FM008 |  | 2023-12-12 07:35 | 2023-12-12 08:35 | 2023-12-13 08:35 | 24 | 2023-12-12 07:40 | 2023-12-12 14:05 | 385 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12462167 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY A1-03A-02 |  | FM008 |  | 2023-12-12 07:37 | 2023-12-12 08:37 | 2023-12-13 08:37 | 24 | 2023-12-12 07:45 | 2023-12-12 10:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12488508 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-19 20:32 | 2023-12-19 21:32 | 2023-12-20 21:32 | 24 | 2023-12-19 20:35 | 2023-12-19 23:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-10074838 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 COOLING COIL DIRTY AG-02-40 |  | FM008 |  | 2022-01-26 03:06 | 2022-01-26 04:06 | 2022-01-27 04:06 | 24 | 2022-01-26 03:10 | 2022-01-26 06:00 | 170 | 680 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10188430 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 CHILLED WATER LINE PAINT DIRTY AG-02-40 |  | FM008 |  | 2022-02-26 00:23 | 2022-02-26 01:23 | 2022-02-27 01:23 | 24 | 2022-02-26 00:30 | 2022-02-26 03:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10820247 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-07-06 10:41 | 2022-07-06 11:41 | 2022-07-07 11:41 | 24 | 2022-07-06 10:45 | 2022-07-06 17:00 | 375 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-11112934 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002-CHILLED WATER LINE PAINT FADED-AG-02-40 |  | FM008 |  | 2022-10-20 20:00 | 2022-10-20 21:00 | 2022-10-21 21:00 | 24 | 2022-10-20 20:05 | 2022-10-20 22:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95217 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11347216 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AC VENT DIRTY - A1-03A-03 (QUIET ROOM) |  | FM008 |  | 2023-01-04 19:58 | 2023-01-04 20:58 | 2023-01-05 20:58 | 24 | 2023-01-04 20:10 | 2023-01-04 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11360711 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AG-02-40 |  | FM008 |  | 2023-01-08 21:44 | 2023-01-08 22:44 | 2023-01-09 22:44 | 24 | 2023-01-08 21:50 | 2023-01-09 01:50 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10951435 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS FILTERS 937-AIR HANDLING UNIT 184 (TAG NO:AHU-A1155-002)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-08-16 01:12 | 2022-08-16 02:12 | 2022-08-17 02:12 | 24 | 2022-08-16 01:20 | 2022-08-16 03:30 | 130 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10967749 | ASD-COA-GFL003-AHU184 | AIR HANDLING UNIT-05 | AHU-A1155-002 – CHILLED WATER LINE PAINT FADED – AG-02-40 |  | FM008 |  | 2022-08-22 19:35 | 2022-08-22 20:35 | 2022-08-23 20:35 | 24 | 2022-08-22 19:40 | 2022-08-22 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 17154 | 55709 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2022-10070631 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001 COOLING COIL DIRTY AG-04-04 |  | FM008 |  | 2022-01-22 18:51 | 2022-01-22 19:51 | 2022-01-23 19:51 | 24 | 2022-01-22 19:00 | 2022-01-22 23:00 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10213274 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU063 CHILLED WATER LINE PAINT FADED – AG-04-04 |  | FM008 |  | 2022-03-04 19:37 | 2022-03-04 20:37 | 2022-03-05 20:37 | 24 | 2022-03-04 19:45 | 2022-03-04 22:15 | 150 | 405 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 106976 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10696465 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001 – SUPPLY DUCT CANVAS AIR LEAKAGE – AG-04-04 |  | FM008 |  | 2022-05-26 19:23 | 2022-05-26 20:23 | 2022-05-27 20:23 | 24 | 2022-05-26 19:30 | 2022-05-26 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94954 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10831341 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | FILTER DIRTY -AG-04-04 |  | FM008 |  | 2022-07-16 19:04 | 2022-07-16 20:04 | 2022-07-17 20:04 | 24 | 2022-07-16 19:10 | 2022-07-16 21:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 95217 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10996187 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU RETURN SIDE BLOWER BEARING NOISY - AG-04-04 |  | FM008 |  | 2022-09-04 08:26 | 2022-09-04 09:26 | 2022-09-05 09:26 | 24 | 2022-09-04 08:30 | 2022-09-04 10:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17053 | 55709 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-11038607 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | HU INSIDE LAMP NOT WORKING |  | FM008 |  | 2022-09-21 03:48 | 2022-09-21 04:48 | 2022-09-22 04:48 | 24 | 2022-09-21 04:00 | 2022-09-21 05:29 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95216 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12116456 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1121-001,AG-04-04 |  | FM008 |  | 2023-08-25 12:25 | 2023-08-25 13:25 | 2023-08-26 13:25 | 24 | 2023-08-25 12:30 | 2023-08-25 17:10 | 280 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12229567 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | INSULATION DAMAGED -AG-04-04 |  | FM008 |  | 2023-09-29 07:11 | 2023-09-29 08:11 | 2023-09-30 08:11 | 24 | 2023-09-29 07:15 | 2023-09-29 14:00 | 405 | 310 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 87807 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-11118211 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001- COOLING COIL DIRTY -AG-04-04 |  | FM008 |  | 2022-10-22 19:38 | 2022-10-22 20:38 | 2022-10-23 20:38 | 24 | 2022-10-22 19:45 | 2022-10-22 23:45 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11179642 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | CHILLED WATER LINED PAINTS FADED- AG-04-04 |  | FM008 |  | 2022-11-11 22:15 | 2022-11-11 23:15 | 2022-11-12 23:15 | 24 | 2022-11-11 22:20 | 2022-11-11 23:55 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 77406 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11344999 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED- AG-04-04 |  | FM008 |  | 2023-01-02 19:39 | 2023-01-02 20:39 | 2023-01-03 20:39 | 24 | 2023-01-02 19:45 | 2023-01-02 21:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11524390 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1121-001 |  | FM008 |  | 2023-03-07 10:23 | 2023-03-07 11:23 | 2023-03-08 11:23 | 24 | 2023-03-07 10:30 | 2023-03-07 17:10 | 400 | 123 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12114450 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | SUPPLY & RETURN INSULATION DUCTS DAMAGED - AG-04-04 |  | FM008 |  | 2023-08-23 20:23 | 2023-08-23 21:23 | 2023-08-24 21:23 | 24 | 2023-08-23 20:30 | 2023-08-23 22:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM7453 | Nyabere, Mr. Daniel Oeri | N - - - |  | Voice Communication
| CM-2023-12326250 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1121-001, AG-04-04 |  | FM008 |  | 2023-10-29 11:40 | 2023-10-29 12:40 | 2023-10-30 12:40 | 24 | 2023-10-29 11:45 | 2023-10-29 16:30 | 285 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2024-12538762 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001-DUCT INSULATION DAMAGE -GROUND FLOOR AREA 004 |  | FM008 |  | 2024-01-07 20:25 | 2024-01-07 21:25 | 2024-01-08 21:25 | 24 | 2024-01-07 20:30 | 2024-01-07 23:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-11041143 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | FILTER BLOCKED -AG-04-04 |  | FM008 |  | 2022-09-24 07:48 | 2022-09-24 08:48 | 2022-09-25 08:48 | 24 | 2022-09-24 08:00 | 2022-09-24 12:00 | 240 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2023-11934607 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-001 – AG-04-04 |  | FM008 |  | 2023-06-29 07:42 | 2023-06-29 08:42 | 2023-06-30 08:42 | 24 | 2023-06-29 07:50 | 2023-06-29 11:45 | 235 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | WATER LEAKAGE | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12488548 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AG-04-04 |  | FM008 |  | 2023-12-19 23:54 | 2023-12-20 00:54 | 2023-12-21 00:54 | 24 | 2023-12-20 00:05 | 2023-12-20 03:00 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 17053 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2023-12367874 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING-AHU-A1121-001)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-11-10 19:07 | 2023-11-10 20:07 | 2023-11-11 20:07 | 24 | 2023-11-10 19:15 | 2023-11-10 22:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17336 | 17053 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2023-12409654 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | ABNORMAL NOISE FROM AHU –(AHU-A1121-0010) – AG 04 04 |  | FM008 |  | 2023-11-24 07:31 | 2023-11-24 08:31 | 2023-11-25 08:31 | 24 | 2023-11-24 07:40 | 2023-11-24 12:00 | 260 | 780 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 132112 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-10225396 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001- FILTER BLOCKED AG-04-04 |  | FM008 |  | 2022-03-09 01:10 | 2022-03-09 02:10 | 2022-03-10 02:10 | 24 | 2022-03-09 01:15 | 2022-03-09 04:30 | 195 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17154 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10309009 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY - AHU-A1121-001 - MECHANICAL ROOM AG-04-04 |  | FM008 |  | 2022-03-31 19:09 | 2022-03-31 20:09 | 2022-04-01 20:09 | 24 | 2022-03-31 19:15 | 2022-03-31 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-10731299 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – AG-04-04 |  | FM008 |  | 2022-06-11 21:50 | 2022-06-11 22:50 | 2022-06-12 22:50 | 24 | 2022-06-11 21:55 | 2022-06-11 23:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 105233 | 87807 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2022-10972861 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001-COOLING COIL DIRTY |  | FM008 |  | 2022-08-25 19:19 | 2022-08-25 20:19 | 2022-08-26 20:19 | 24 | 2022-08-25 19:25 | 2022-08-25 23:00 | 215 | 645 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95217 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11076837 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1121-001 |  | FM008 |  | 2022-10-04 19:24 | 2022-10-04 20:24 | 2022-10-05 20:24 | 24 | 2022-10-04 19:30 | 2022-10-04 22:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 87807 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-11658042 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-AHU-A1121-001)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-04-14 10:17 | 2023-04-14 11:17 | 2023-04-15 11:17 | 24 | 2023-04-14 10:20 | 2023-04-14 13:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2022-10023383 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-01-04 16:16 | 2022-01-04 17:16 | 2022-01-05 17:16 | 24 | 2022-01-04 16:20 | 2022-01-04 18:00 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10141101 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-001 – AG-04-04 |  | FM008 |  | 2022-02-13 23:04 | 2022-02-14 00:04 | 2022-02-15 00:04 | 24 | 2022-02-13 23:10 | 2022-02-14 01:45 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10567799 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001- COOLING COIL DIRTY-- |  | FM008 |  | 2022-04-21 07:18 | 2022-04-21 08:18 | 2022-04-22 08:18 | 24 | 2022-04-21 07:25 | 2022-04-21 10:30 | 185 | 555 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-11975050 | ASD-COA-GFL004-AHU063 | AIR HANDLING UNIT-05 | AHU-A1121-001-DRAIN LINE BLOCKED- |  | FM008 |  | 2023-07-14 09:02 | 2023-07-14 10:02 | 2023-07-15 10:02 | 24 | 2023-07-14 09:10 | 2023-07-14 12:30 | 200 | 445 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 77406 | 87807 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10048819 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU-A1121-007 COOLING COIL DIRTY |  | FM008 |  | 2022-01-15 18:52 | 2022-01-15 19:52 | 2022-01-16 19:52 | 24 | 2022-01-15 19:00 | 2022-01-15 23:00 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 55709 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10100042 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AG-04-04 |  | FM008 |  | 2022-02-02 22:30 | 2022-02-02 23:30 | 2022-02-03 23:30 | 24 | 2022-02-02 22:35 | 2022-02-03 01:45 | 190 | 570 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10209369 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AG-04-04 |  | FM008 |  | 2022-03-03 00:08 | 2022-03-03 01:08 | 2022-03-04 01:08 | 24 | 2022-03-03 00:54 | 2022-03-03 02:45 | 111 | 222 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10310346 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU-A1121-007 – COOLING COIL DIRTY-- |  | FM008 |  | 2022-03-30 19:06 | 2022-03-30 20:06 | 2022-03-31 20:06 | 24 | 2022-03-30 19:10 | 2022-03-30 23:00 | 230 | 690 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 55709 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2022-11329009 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | RETURN DUCT CONVERSE AIR LEAKAGE |  | FM008 |  | 2022-12-31 19:19 | 2022-12-31 20:19 | 2023-01-01 20:19 | 24 | 2022-12-31 19:25 | 2022-12-31 22:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11667707 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU-A1121-007 – CHILLED WATER PAINT FADED |  | FM008 |  | 2023-04-14 07:28 | 2023-04-14 08:28 | 2023-04-15 08:28 | 24 | 2023-04-14 07:35 | 2023-04-14 10:15 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 87807 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-11968979 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1121-007, AG-04-04 |  | FM008 |  | 2023-07-09 15:29 | 2023-07-09 16:29 | 2023-07-10 16:29 | 24 | 2023-07-09 15:35 | 2023-07-09 18:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 124475 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12114985 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED ,AHU-A1121-007,AG-04-04 |  | FM008 |  | 2023-08-25 07:46 | 2023-08-25 08:46 | 2023-08-26 08:46 | 24 | 2023-08-25 07:55 | 2023-08-25 11:00 | 185 | 555 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12156882 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU DUCT INSOLATION DAMAGED, AHU-A1121-007,AG-04-04 |  | FM008 |  | 2023-09-06 00:05 | 2023-09-06 01:05 | 2023-09-07 01:05 | 24 | 2023-09-06 00:10 | 2023-09-06 04:00 | 230 | 355 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2024-12685402 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AG-04-04 |  | FM008 |  | 2024-02-25 22:01 | 2024-02-25 23:01 | 2024-02-26 23:01 | 24 | 2024-02-25 22:10 | 2024-02-26 00:30 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-10877580 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU-A1121-007-FILTER DIRTY |  | FM008 |  | 2022-07-28 13:21 | 2022-07-28 14:21 | 2022-07-29 14:21 | 24 | 2022-07-28 13:30 | 2022-07-28 17:30 | 240 | 75 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11696771 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU NOISY-AHU-A1121-007)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-04-22 08:27 | 2023-04-22 09:27 | 2023-04-23 09:27 | 24 | 2023-04-22 08:35 | 2023-04-22 15:30 | 415 | 1065 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 17336 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12111798 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU-A1121-007 SUPLY DUCT INSULATION DAMAGED-AG-04-04 |  | FM008 |  | 2023-08-22 22:26 | 2023-08-22 23:26 | 2023-08-23 23:26 | 24 | 2023-08-22 22:30 | 2023-08-23 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-12326249 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1121-007, AG-04-04 |  | FM008 |  | 2023-10-29 11:40 | 2023-10-29 12:40 | 2023-10-30 12:40 | 24 | 2023-10-29 11:45 | 2023-10-29 14:20 | 155 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2024-12532583 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1121-007 |  | FM008 |  | 2024-01-02 19:58 | 2024-01-02 20:58 | 2024-01-03 20:58 | 24 | 2024-01-02 20:05 | 2024-01-02 23:00 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-12361909 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-11-07 10:19 | 2023-11-07 11:19 | 2023-11-08 11:19 | 24 | 2023-11-07 10:25 | 2023-11-07 18:00 | 455 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | E-mail
| CM-2022-11041141 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | FILTER BLOCKED -AG-04-04 |  | FM008 |  | 2022-09-24 07:46 | 2022-09-24 08:46 | 2022-09-25 08:46 | 24 | 2022-09-24 08:00 | 2022-09-24 10:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2023-11354625 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AG-04-04- AHU-A1121-007 – FILTER DIRTY-- |  | FM008 |  | 2023-01-08 11:23 | 2023-01-08 12:23 | 2023-01-09 12:23 | 24 | 2023-01-08 11:25 | 2023-01-08 15:00 | 215 | 355 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-10567800 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | AHU-A1121-007- COOLING COIL DIRTY-- |  | FM008 |  | 2022-04-21 07:18 | 2022-04-21 08:18 | 2022-04-22 08:18 | 24 | 2022-04-21 07:25 | 2022-04-21 13:30 | 365 | 530 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-11421500 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – AG-04-04 AIR HANDLING UNIT 069 (TAG NO:AHU-A1121-007)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-01-30 00:03 | 2023-01-30 01:03 | 2023-01-31 01:03 | 24 | 2023-01-30 00:10 | 2023-01-30 02:00 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17154 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11476460 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1121-007 |  | FM008 |  | 2023-02-22 11:10 | 2023-02-22 12:10 | 2023-02-23 12:10 | 24 | 2023-02-22 11:15 | 2023-02-22 16:00 | 285 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-11937215 | ASD-COA-GFL004-AHU069 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - MEC ROOM -AG-04-04 |  | FM008 |  | 2023-06-30 19:22 | 2023-06-30 20:22 | 2023-07-01 20:22 | 24 | 2023-06-30 19:30 | 2023-06-30 21:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10058272 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008 - COOLING COIL DIRTY - AG-04-04 - CM-2022-01-1313 |  | FM008 |  | 2022-01-16 22:30 | 2022-01-16 23:30 | 2022-01-17 23:30 | 24 | 2022-01-16 22:40 | 2022-01-16 23:55 | 75 | 225 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17053 | 55709 |  |  | FM5676 | ROSHAN | - - - |  | Voice Communication
| CM-2022-10208683 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008-CILLED WATERLINE PAINT FADED |  | FM008 |  | 2022-03-03 03:07 | 2022-03-03 04:07 | 2022-03-04 04:07 | 24 | 2022-03-03 03:15 | 2022-03-03 05:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95217 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11039151 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1121-008 |  | FM008 |  | 2022-09-23 10:31 | 2022-09-23 11:31 | 2022-09-24 11:31 | 24 | 2022-09-23 10:35 | 2022-09-23 13:00 | 145 | 274 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-11365452 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AG-04A-04, AHU-A1110-008 |  | FM008 |  | 2023-01-13 19:22 | 2023-01-13 20:22 | 2023-01-14 20:22 | 24 | 2023-01-13 19:30 | 2023-01-13 23:30 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-11667708 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008 – CHILLED WATER PAINT FADED |  | FM008 |  | 2023-04-14 07:30 | 2023-04-14 08:30 | 2023-04-15 08:30 | 24 | 2023-04-14 07:35 | 2023-04-14 10:15 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-11968978 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1121-008, AG-04-04 |  | FM008 |  | 2023-07-09 15:28 | 2023-07-09 16:28 | 2023-07-10 16:28 | 24 | 2023-07-09 15:35 | 2023-07-09 18:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12115223 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-008 – AG-04-04 |  | FM008 |  | 2023-08-26 07:38 | 2023-08-26 08:38 | 2023-08-27 08:38 | 24 | 2023-08-26 07:45 | 2023-08-26 11:00 | 195 | 390 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12114917 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008 SUPPLY DUCT INSULATION DAMAGED AG-04-04 |  | FM008 |  | 2023-08-25 00:07 | 2023-08-25 01:07 | 2023-08-26 01:07 | 24 | 2023-08-25 00:15 | 2023-08-25 02:30 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-12204867 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1121-008 - AG-04-04 |  | FM008 |  | 2023-09-19 19:14 | 2023-09-19 20:14 | 2023-09-20 20:14 | 24 | 2023-09-19 19:20 | 2023-09-19 23:58 | 278 | 945 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12327124 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU FILTER BLOCKED – AG-04-04 |  | FM008 |  | 2023-10-28 20:00 | 2023-10-28 21:00 | 2023-10-29 21:00 | 24 | 2023-10-28 20:05 | 2023-10-28 21:30 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12685403 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AG-04-04 |  | FM008 |  | 2024-02-25 22:02 | 2024-02-25 23:02 | 2024-02-26 23:02 | 24 | 2024-02-25 22:10 | 2024-02-26 00:30 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-11332929 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AG-04-04- -RETURN DUCT CANVAS AIR LEAKAGE -AHU-A1121-008)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-01-01 22:25 | 2023-01-01 23:25 | 2023-01-02 23:25 | 24 | 2023-01-01 22:35 | 2023-01-02 01:30 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11823326 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU FILTER BLOCKED – AG-04-04 |  | FM008 |  | 2023-05-22 19:32 | 2023-05-22 20:32 | 2023-05-23 20:32 | 24 | 2023-05-22 19:40 | 2023-05-22 21:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 105233 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11934946 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING |  | FM008 |  | 2023-06-29 19:03 | 2023-06-29 20:03 | 2023-06-30 20:03 | 24 | 2023-06-29 19:10 | 2023-06-29 23:58 | 288 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 121959 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12115785 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | FILTER ALARM - AHU-A1121-008 – AG-04-04 |  | FM008 |  | 2023-08-26 00:17 | 2023-08-26 01:17 | 2023-08-27 01:17 | 24 | 2023-08-26 00:25 | 2023-08-26 02:45 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-12421993 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1121-008 – AG-04-04 |  | FM008 |  | 2023-11-27 07:30 | 2023-11-27 08:30 | 2023-11-28 08:30 | 24 | 2023-11-27 07:35 | 2023-11-27 14:00 | 385 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM12499 | ANEESH JOY, | N - - - |  | BMS
| CM-2023-12448604 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | SENSOR TUBE DAMAGED,AHU-A11121-008,AG-04-04 |  | FM008 |  | 2023-12-08 10:17 | 2023-12-08 11:17 | 2023-12-09 11:17 | 24 | 2023-12-08 10:25 | 2023-12-08 18:35 | 490 | 485 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM8044 | Rajesh Janardhanan Chettiyar, | N - - - |  | Voice Communication
| CM-2023-12113532 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-007 -RETURN DUCT INSULATION DAMAGED - AG-04-04 |  | FM008 |  | 2023-08-22 22:31 | 2023-08-22 23:31 | 2023-08-23 23:31 | 24 | 2023-08-22 22:35 | 2023-08-23 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2024-12750705 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008 AHU LIGHTING SWITCH DAMAGE |  | FM008 |  | 2024-03-23 07:23 | 2024-03-23 08:23 | 2024-03-24 08:23 | 24 | 2024-03-23 07:30 | 2024-03-23 10:15 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 119320 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12361910 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-11-07 10:20 | 2023-11-07 11:20 | 2023-11-08 11:20 | 24 | 2023-11-07 10:25 | 2023-11-07 18:00 | 455 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95216 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10885712 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | FILTER ALARM CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-07-28 19:51 | 2022-07-28 20:51 | 2022-07-29 20:51 | 24 | 2022-07-28 19:55 | 2022-07-28 23:58 | 243 | 241 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | E-mail
| CM-2022-11014733 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU LAMP NOT WORKING |  | FM008 |  | 2022-09-11 20:16 | 2022-09-11 21:16 | 2022-09-12 21:16 | 24 | 2022-09-11 20:20 | 2022-09-11 22:10 | 110 | 181 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | SUPPLY POWER FAILURE | RESET THE BREAKER | 95216 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11354624 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AG-04-04- AHU-A1121-008 – FILTER DIRTY-- |  | FM008 |  | 2023-01-08 11:22 | 2023-01-08 12:22 | 2023-01-09 12:22 | 24 | 2023-01-08 11:25 | 2023-01-08 17:00 | 335 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-11695501 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM AHU |  | FM008 |  | 2023-04-23 08:14 | 2023-04-23 09:14 | 2023-04-24 09:14 | 24 | 2023-04-23 08:15 | 2023-04-23 15:00 | 405 | 465 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 106972 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-10049365 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008 – RAD OPEN FAIL ALARM – AG -04-04 |  | FM008 |  | 2022-01-14 12:52 | 2022-01-14 13:52 | 2022-01-15 13:52 | 24 | 2022-01-14 13:00 | 2022-01-14 14:25 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOISY | MISALIGNMENT | RECTIFIED | 94954 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10780942 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1121-008 – AG-04-04 |  | FM008 |  | 2022-06-27 13:26 | 2022-06-27 14:26 | 2022-06-28 14:26 | 24 | 2022-06-27 13:30 | 2022-06-27 18:30 | 300 | 110 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11422320 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-02-02 19:35 | 2023-02-02 20:35 | 2023-02-03 20:35 | 24 | 2023-02-02 19:45 | 2023-02-02 22:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 132112 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-11975052 | ASD-COA-GFL004-AHU070 | AIR HANDLING UNIT-05 | AHU-A1121-008-DRAIN LINE BLOCKED . |  | FM008 |  | 2023-07-14 09:24 | 2023-07-14 10:24 | 2023-07-15 10:24 | 24 | 2023-07-14 09:30 | 2023-07-14 17:30 | 480 | 355 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10696604 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE - AG-04-04 |  | FM008 |  | 2022-05-27 02:26 | 2022-05-27 03:26 | 2022-05-28 03:26 | 24 | 2022-05-27 02:35 | 2022-05-27 05:30 | 175 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 94954 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11786390 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AC TOO WARM - NEAR A2-04-06 CORRIDOR |  | FM008 |  | 2023-05-14 04:14 | 2023-05-14 05:14 | 2023-05-15 05:14 | 24 | 2023-05-14 04:20 | 2023-05-14 06:10 | 110 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | R13184 | Khan, Mr. Tousif | N - - - |  | Voice Communication
| CM-2023-12116049 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY – AHU-A1121-011 - MECHANICAL ROOM AG-04-04 |  | FM008 |  | 2023-08-26 20:30 | 2023-08-26 21:30 | 2023-08-27 21:30 | 24 | 2023-08-26 20:40 | 2023-08-26 23:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12280968 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | ABNORMAL NOISE-AHU-A1121-011)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004-AG-04-04- |  | FM008 |  | 2023-10-13 13:25 | 2023-10-13 14:25 | 2023-10-14 14:25 | 24 | 2023-10-13 13:30 | 2023-10-13 17:45 | 255 | 599 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 17336 | 87807 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2023-12327125 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU FILTER BLOCKED – AG-04-04 |  | FM008 |  | 2023-10-28 20:01 | 2023-10-28 21:01 | 2023-10-29 21:01 | 24 | 2023-10-28 20:05 | 2023-10-28 23:00 | 175 | 175 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 105233 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12343915 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU-A1121-008 FILTER DIRTY |  | FM008 |  | 2023-11-02 08:33 | 2023-11-02 09:33 | 2023-11-03 09:33 | 24 | 2023-11-02 08:40 | 2023-11-02 12:00 | 200 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-11078551 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-10-05 18:57 | 2022-10-05 19:57 | 2022-10-06 19:57 | 24 | 2022-10-05 19:05 | 2022-10-05 21:00 | 115 | 170 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2023-11698894 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU-A1121-011-NOISY- AG-04-04 |  | FM008 |  | 2023-04-25 08:21 | 2023-04-25 09:21 | 2023-04-26 09:21 | 24 | 2023-04-25 08:30 | 2023-04-25 13:00 | 270 | 1080 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 77406 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11823327 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU-A1121-011 – FILTER BLOCKED – AG-04-04 |  | FM008 |  | 2023-05-22 19:33 | 2023-05-22 20:33 | 2023-05-23 20:33 | 24 | 2023-05-22 19:42 | 2023-05-22 23:40 | 238 | 353 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 105233 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12093687 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED – AHU-A1121-011 - AG 04 05 |  | FM008 |  | 2023-08-14 19:55 | 2023-08-14 20:55 | 2023-08-15 20:55 | 24 | 2023-08-14 20:05 | 2023-08-14 22:35 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 132112 | 17053 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2023-12114266 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1121-011 - AG-04-04 |  | FM008 |  | 2023-08-26 07:39 | 2023-08-26 08:39 | 2023-08-27 08:39 | 24 | 2023-08-26 07:45 | 2023-08-26 11:00 | 195 | 390 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12541088 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU-A1121-011-DUCT INSULATION DAMAGE-GROUND FLOOR AREA 004 |  | FM008 |  | 2024-01-07 20:05 | 2024-01-07 21:05 | 2024-01-08 21:05 | 24 | 2024-01-07 20:10 | 2024-01-07 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-11041142 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | FILTER BLOCKED -AG-04-04 |  | FM008 |  | 2022-09-24 07:47 | 2022-09-24 08:47 | 2022-09-25 08:47 | 24 | 2022-09-24 08:00 | 2022-09-24 13:00 | 300 | 175 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 87807 |  |  | FM5676 | ROSHIN ARUKETTY RAMAKRISHNAN, | N - - - |  | Voice Communication
| CM-2023-12464910 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-AIR HANDLING UNIT 073 (TAG NO:AHU-A1121-011)-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-12-12 19:38 | 2023-12-12 20:38 | 2023-12-13 20:38 | 24 | 2023-12-12 19:45 | 2023-12-12 21:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-10147344 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1121-011)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-02-18 07:18 | 2022-02-18 08:18 | 2022-02-19 08:18 | 24 | 2022-02-18 07:25 | 2022-02-18 10:30 | 185 | 740 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM0016 | Paramasamy, Mr. Jeyaram | N - - - |  | Voice Communication
| CM-2022-10217856 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY AHU-A1121-011 AG-04-04 |  | FM008 |  | 2022-03-07 19:44 | 2022-03-07 20:44 | 2022-03-08 20:44 | 24 | 2022-03-07 19:50 | 2022-03-07 22:00 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 17053 |  |  | FM5676 | Ramakrishnan Roshin , Mr. Aruketty | N - - - |  | Voice Communication
| CM-2022-10311861 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | COILING COIL IS DIRTY – AHU-A1121-011 - MECHANICAL ROOM AG-04-04 |  | FM008 |  | 2022-04-01 19:12 | 2022-04-01 20:12 | 2022-04-02 20:12 | 24 | 2022-04-01 19:20 | 2022-04-01 23:00 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10578350 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – AG-04-04 |  | FM008 |  | 2022-04-22 07:48 | 2022-04-22 08:48 | 2022-04-23 08:48 | 24 | 2022-04-22 07:55 | 2022-04-22 12:00 | 245 | 490 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11014735 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU LAMP NOT WORKING |  | FM008 |  | 2022-09-11 20:18 | 2022-09-11 21:18 | 2022-09-12 21:18 | 24 | 2022-09-11 20:22 | 2022-09-11 23:45 | 203 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | BLOCKAGE OF AIR FLOW | REPAIR/REPLACE | 95216 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11658039 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AHU-A1121-011)-AIRSIDE-CONCOURSE A-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-04-14 10:14 | 2023-04-14 11:14 | 2023-04-15 11:14 | 24 | 2023-04-14 10:20 | 2023-04-14 13:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 87807 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2022-10201959 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU073 - CHILLED WATER LINE PAINT FADED – AG-04-04 |  | FM008 |  | 2022-03-03 19:25 | 2022-03-03 20:25 | 2022-03-04 20:25 | 24 | 2022-03-03 19:30 | 2022-03-03 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106976 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12756142 | ASD-COA-GFL004-AHU073 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH DAMAGED – (AHU-A1121-011) – AG 04 04 |  | FM008 |  | 2024-03-23 08:27 | 2024-03-23 09:27 | 2024-03-24 09:27 | 24 | 2024-03-23 08:35 | 2024-03-23 13:05 | 270 | 333 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 132112 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2022-11232343 | ASD-COA-SFL004-AHU075 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING -AHU-A1121-201)-AIRSIDE-CONCOURSE A-SECOND FLOOR AREA 004 |  | FM008 |  | 2022-11-29 13:23 | 2022-11-29 14:23 | 2022-11-30 14:23 | 24 | 2022-11-29 13:30 | 2022-11-29 16:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17336 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11841795 | ASD-COA-SFL004-AHU075 | AIR HANDLING UNIT-05 | AHU-A1121-201 CABIN LAMP NOT WORKING |  | FM008 |  | 2023-06-02 10:05 | 2023-06-02 11:05 | 2023-06-03 11:05 | 24 | 2023-06-02 10:10 | 2023-06-02 11:33 | 83 | 166 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 004 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 68485 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12014998 | ASD-COA-SFL004-AHU075 | AIR HANDLING UNIT-05 | FL1 FAMILY AREA AC TO COLD |  | FM008 |  | 2023-07-29 02:34 | 2023-07-29 03:34 | 2023-07-30 03:34 | 24 | 2023-07-29 02:40 | 2023-07-29 04:30 | 110 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 004 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | Voice Communication
| CM-2024-12608656 | ASD-COA-SFL004-AHU075 | AIR HANDLING UNIT-05 | CHILLED WATER LINE INSULATION DAMAGED – A2-04-26 |  | FM008 |  | 2024-01-30 13:03 | 2024-01-30 14:02 | 2024-01-31 14:02 | 24 | 2024-01-30 13:15 | 2024-01-30 16:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12130039 | ASD-COA-SFL004-AHU075 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTTING SWITCH FAULTY - A2-04-26 |  | FM008 |  | 2023-08-29 11:04 | 2023-08-29 12:04 | 2023-08-30 12:04 | 24 | 2023-08-29 11:10 | 2023-08-29 14:50 | 220 | 305 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 004 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17053 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-10932294 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 AC TOO HOT OPEN AREA NEAR BAR COUNTER |  | FM008 |  | 2022-08-14 00:08 | 2022-08-14 01:08 | 2022-08-15 01:08 | 24 | 2022-08-14 00:15 | 2022-08-14 06:30 | 375 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 55709 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-11134707 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2- DINING AREA |  | FM008 |  | 2022-10-25 23:35 | 2022-10-26 00:35 | 2022-10-27 00:35 | 24 | 2022-10-25 23:40 | 2022-10-26 00:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 87807 |  |  | 109304 | Mahajani, Mr. Amit Ravindra | N - - - |  | Voice Communication
| CM-2022-11177455 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | No maintenance space for fire dampers for return duct penetrating to mechanical room - AHU-A1121-202 - A2-FFL2-10*Email@Thu 11/10/2022 2:57 PM* |  | FM008 |  | 2022-11-10 08:21 | 2022-11-10 09:21 | 2022-11-11 09:21 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING |  |  | 106973 | 95217 |  |  | 107414 | Kabuusu, Mr. Ronald Tonny | N - - - | ASSET NOT HANDED OVER | E-mail
| CM-2022-11232430 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -FFL 2 OPEN LOUNGE |  | FM008 |  | 2022-11-30 04:07 | 2022-11-30 05:07 | 2022-12-01 05:07 | 24 | 2022-11-30 04:10 | 2022-11-30 05:30 | 80 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 87522 | Ouacif, Mr. Isslam | N - - - |  | Voice Communication
| CM-2022-11289658 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - ENTIRE FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2022-12-21 17:43 | 2022-12-21 18:43 | 2022-12-22 18:43 | 24 | 2022-12-21 17:50 | 2022-12-21 19:30 | 100 | 40 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | Voice Communication
| CM-2023-11502766 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD OPEN LOUNGE AREA INFRONT OF BAR FFL2 |  | FM008 |  | 2023-02-28 20:52 | 2023-02-28 21:52 | 2023-03-01 21:52 | 24 | 2023-02-28 21:00 | 2023-02-28 23:30 | 150 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 94954 |  |  | 108575 | Perabattula, Mr. Anil | N - - - |  | Voice Communication
| CM-2023-11570393 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TEMPERATURE TOO HOT -FFL2 PLATINUM LOUNGE RECEPTION |  | FM008 |  | 2023-03-20 11:21 | 2023-03-20 12:21 | 2023-03-21 12:21 | 24 | 2023-03-20 11:30 | 2023-03-20 14:45 | 195 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 127466 | Koduvayur Subramanian, Mr. Vaidyanathan | N - - - |  | Voice Communication
| CM-2023-11843368 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C IS TOO HOT IN THE OPEN AREA |  | FM008 |  | 2023-06-02 01:04 | 2023-06-02 02:04 | 2023-06-03 02:04 | 24 | 2023-06-02 01:10 | 2023-06-02 03:25 | 135 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-11843393 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC NOT COOLING (TOO WARM) – FFL2 LOUNGE QUIET ROOM |  | FM008 |  | 2023-06-02 05:35 | 2023-06-02 06:35 | 2023-06-03 06:35 | 24 | 2023-06-02 05:40 | 2023-06-02 18:05 | 745 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106973 | 87807 |  |  | 71476 | Kaur Hargit Singh, Ms. Mangeet | N - - - |  | Voice Communication
| CM-2023-11842569 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | MOTOR FLEX CONNECTOR DAMAGED – (A1121-202) |  | FM008 |  | 2023-06-02 13:40 | 2023-06-02 14:40 | 2023-06-03 14:40 | 24 | 2023-06-02 13:45 | 2023-06-02 15:13 | 88 | 176 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 132112 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11885093 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) - FFL2 LOUNGE BAR COUNTER AREA |  | FM008 |  | 2023-06-15 17:41 | 2023-06-15 18:41 | 2023-06-16 18:41 | 24 | 2023-06-15 17:50 | 2023-06-15 20:00 | 130 | 60 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | Voice Communication
| CM-2023-11910733 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD IN OPEN LOUNGE AREA - FFL2 LOUNGE |  | FM008 |  | 2023-06-22 09:55 | 2023-06-22 10:55 | 2023-06-23 10:55 | 24 | 2023-06-22 10:05 | 2023-06-22 16:35 | 390 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 106973 | 17053 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2023-11998707 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 SEATING AREA AC TOO COLD |  | FM008 |  | 2023-07-23 03:53 | 2023-07-23 04:53 | 2023-07-24 04:53 | 24 | 2023-07-23 04:00 | 2023-07-23 05:50 | 110 | 45 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 89127 | 17053 |  |  | 127062 | Ronoh, Ms. Sarah Chepchumba | N - - - |  | Voice Communication
| CM-2023-12016580 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC VENT DIRTY ADMIN OFFICE - A-FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-07-29 12:51 | 2023-07-29 13:51 | 2023-07-30 13:51 | 24 | 2023-07-29 13:00 | 2023-07-29 15:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12015533 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 DINING RAEA |  | FM008 |  | 2023-07-29 12:52 | 2023-07-29 13:52 | 2023-07-30 13:52 | 24 | 2023-07-29 13:00 | 2023-07-29 18:05 | 305 | 70 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 111588 | Badar, Mr. Rahis | N - - - |  | Voice Communication
| CM-2023-12042445 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -FFL2 |  | FM008 |  | 2023-08-04 00:47 | 2023-08-04 01:47 | 2023-08-05 01:47 | 24 | 2023-08-04 00:55 | 2023-08-04 02:30 | 95 | 60 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17333 | 17053 |  |  | 134565 | Mayanja, Mr. Elvis Manga | N - - - |  | Voice Communication
| CM-2023-12126000 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO HOT IN MALE TOILET FFL2 |  | FM008 |  | 2023-08-27 15:09 | 2023-08-27 16:09 | 2023-08-28 16:09 | 24 | 2023-08-27 15:15 | 2023-08-27 17:10 | 115 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | Fm11425 | Dinesh Nalaka | N - - - |  | Voice Communication
| CM-2023-12131880 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD IN OPEN AREA - FFL2 LOUNGE |  | FM008 |  | 2023-08-28 21:25 | 2023-08-28 22:25 | 2023-08-29 22:25 | 24 | 2023-08-28 21:30 | 2023-08-28 23:05 | 95 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-12179365 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) – FFL2 LOUNGE DINING AREA |  | FM008 |  | 2023-09-11 12:36 | 2023-09-11 13:36 | 2023-09-12 13:36 | 24 | 2023-09-11 12:40 | 2023-09-11 15:10 | 150 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2023-12281932 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 OPEN & DINING A2-FFL2-01 |  | FM008 |  | 2023-10-13 19:53 | 2023-10-13 20:53 | 2023-10-14 20:53 | 24 | 2023-10-13 20:00 | 2023-10-13 21:00 | 60 | 50 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 63097 | Surve, Mr. Mudassir Liyakat | N - - - |  | E-mail
| CM-2023-12281458 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - COMMON SEATING AREA FFL2 |  | FM008 |  | 2023-10-15 02:09 | 2023-10-15 03:09 | 2023-10-16 03:09 | 24 | 2023-10-15 02:15 | 2023-10-15 04:00 | 105 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-12325693 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL1 OPEN AREA |  | FM008 |  | 2023-10-27 02:33 | 2023-10-27 03:33 | 2023-10-28 03:33 | 24 | 2023-10-27 02:40 | 2023-10-27 03:30 | 50 | 50 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 77496 | Falul, Mrs. Fathima Shazra | N - - - |  | Voice Communication
| CM-2023-12342220 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL1 SOUTH OPEN LOUNGE |  | FM008 |  | 2023-11-01 01:53 | 2023-11-01 02:53 | 2023-11-02 02:53 | 24 | 2023-11-01 02:00 | 2023-11-01 04:45 | 165 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 129908 | Federico, Ms. Lovely Amor Tarzona | N - - - |  | Voice Communication
| CM-2023-12385827 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -ALL AREA |  | FM008 |  | 2023-11-17 19:21 | 2023-11-17 20:21 | 2023-11-18 20:21 | 24 | 2023-11-17 19:30 | 2023-11-17 21:35 | 125 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 125945 | Shan, Mr. Muhammad Waqar | N - - - |  | Voice Communication
| CM-2023-12383154 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD IN FFL2 LOBBY AREA |  | FM008 |  | 2023-11-16 02:23 | 2023-11-16 03:23 | 2023-11-17 03:23 | 24 | 2023-11-16 02:28 | 2023-11-16 05:00 | 152 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | 83643 | Vazhayil Kandoth, Mr. Safran | N - - - |  | Voice Communication
| CM-2023-12448552 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 LOUNGE, COMMON AREA - AC TEMPERATURE IS TOO COLD |  | FM008 |  | 2023-12-08 00:23 | 2023-12-08 01:23 | 2023-12-09 01:23 | 24 | 2023-12-08 00:30 | 2023-12-08 06:30 | 360 | 35 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94954 | 17053 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | Voice Communication
| CM-2023-12452650 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD FFL2 OPEN AREA |  | FM008 |  | 2023-12-09 00:26 | 2023-12-09 01:26 | 2023-12-10 01:26 | 24 | 2023-12-09 00:30 | 2023-12-09 06:30 | 360 | 35 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 77406 | 17053 |  |  | 13456 | Pokharel, Mr. Shoyamvu Raj | N - - - |  | Voice Communication
| CM-2023-12484178 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 LOUNGE DINING & OPEN AREA |  | FM008 |  | 2023-12-18 04:23 | 2023-12-18 05:23 | 2023-12-19 05:23 | 24 | 2023-12-18 04:30 | 2023-12-18 05:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 83643 | Vazhayil Kandoth, Mr. Safran | N - - - |  | Voice Communication
| CM-2023-12507514 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO HOT - ROOM 1-AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 2 - DINING AREA |  | FM008 |  | 2023-12-26 04:39 | 2023-12-26 05:39 | 2023-12-27 05:39 | 24 | 2023-12-26 04:45 | 2023-12-26 05:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | 134953 | Milanes, Ms. Pamela | N - - - |  | Voice Communication
| CM-2024-12606551 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 LOUNGE OPEN AREA – AC TOO COLD |  | FM008 |  | 2024-01-29 01:14 | 2024-01-29 02:14 | 2024-01-30 02:14 | 24 | 2024-01-29 01:20 | 2024-01-29 05:35 | 255 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 84522 | Pimentel, Ms. Danica Mae Casino | N - - - |  | Voice Communication
| CM-2024-12655253 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | SEATING AREA AC TEMP TOO COLD -FFL2 |  | FM008 |  | 2024-02-18 04:15 | 2024-02-18 05:15 | 2024-02-19 05:15 | 24 | 2024-02-18 04:25 | 2024-02-18 06:30 | 125 | 90 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | Voice Communication
| CM-2024-12705224 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | OPEN BAR COUNTER AC VENT COVER PAINT FADED FLL2 OPEN AREA |  | FM008 |  | 2024-03-08 09:03 | 2024-03-08 10:03 | 2024-03-09 10:03 | 24 | 2024-03-08 09:10 | 2024-03-08 16:00 | 410 | 175 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DAMAGED | UNIT IS RUSTED | CLEANED & REPAINT THE UNIT | 138627 | 17053 |  |  | FM7799 | Mugambi, Mr. Antony | N - - - |  | Voice Communication
| CM-2024-12844779 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 OPEN SEATING AREA - AC TOO COLD |  | FM008 |  | 2024-04-22 00:52 | 2024-04-22 01:52 | 2024-04-23 01:52 | 24 | 2024-04-22 01:00 | 2024-04-22 06:20 | 320 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2022-11250914 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FAULTY – A2-05-31- AIR HANDLING UNIT 076 (TAG NO:AHU-A1121-202)-AIRSIDE-CONCOURSE A-SECOND FLOOR AREA 005 |  | FM008 |  | 2022-12-05 21:04 | 2022-12-05 22:04 | 2022-12-06 22:04 | 24 | 2022-12-05 21:10 | 2022-12-06 | 170 | 340 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11250939 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2(PLATINUM LOUNGE) – OPEN AREA |  | FM008 |  | 2022-12-06 02:39 | 2022-12-06 03:39 | 2022-12-07 03:39 | 24 | 2022-12-06 02:45 | 2022-12-06 03:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 84522 | Pimentel, Ms. Danica Mae Casino | N - - - |  | Voice Communication
| CM-2023-11384701 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO HOT - FFL2 DINING AND SEATING AREA |  | FM008 |  | 2023-01-19 22:28 | 2023-01-19 23:28 | 2023-01-20 23:28 | 24 | 2023-01-19 22:35 | 2023-01-19 23:35 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 94954 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-11763372 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD SEATING AREA FFL2 |  | FM008 |  | 2023-05-04 03:17 | 2023-05-04 04:17 | 2023-05-05 04:17 | 24 | 2023-05-04 03:25 | 2023-05-04 04:00 | 35 | 35 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | 61871 | Kaluarachchige Don, Ms. Nuradha | N - - - |  | Voice Communication
| CM-2023-11842314 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 SEATING AND DINING AREA – AC IS TOO HOT-- |  | FM008 |  | 2023-06-01 14:20 | 2023-06-01 15:20 | 2023-06-02 15:20 | 24 | 2023-06-01 14:25 | 2023-06-01 18:10 | 225 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94953 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-11846053 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD FFL2 BAR AREA |  | FM008 |  | 2023-06-05 23:45 | 2023-06-06 00:45 | 2023-06-07 00:45 | 24 | 2023-06-05 23:50 | 2023-06-06 00:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 68485 | 95217 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-11895957 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 SEATING COMMON AREA AC IS TOO COLD |  | FM008 |  | 2023-06-19 01:53 | 2023-06-19 02:53 | 2023-06-20 02:53 | 24 | 2023-06-19 02:00 | 2023-06-19 03:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94953 | 121959 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | Voice Communication
| CM-2023-11959421 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD |  | FM008 |  | 2023-07-08 05:52 | 2023-07-08 06:52 | 2023-07-09 06:52 | 24 | 2023-07-08 06:00 | 2023-07-08 06:30 | 30 | 30 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 103922 | Istiak, Mr. Shamim | N - - - |  | Voice Communication
| CM-2023-11972823 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO HOT – OPEN ARAE FFL2 |  | FM008 |  | 2023-07-13 05:26 | 2023-07-13 06:26 | 2023-07-14 06:26 | 24 | 2023-07-13 05:35 | 2023-07-13 08:00 | 145 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | 29477 | Bowen, Mr. Michael Martin | N - - - |  | Voice Communication
| CM-2023-12017191 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FCU-A1153-EK-002-AC VENT DIRTY -FFL2 KITCHEN |  | FM008 |  | 2023-07-29 12:58 | 2023-07-29 13:58 | 2023-07-30 13:58 | 24 | 2023-07-29 13:00 | 2023-07-29 15:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12099590 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -DINING AREA BY BAR |  | FM008 |  | 2023-08-19 09:08 | 2023-08-19 10:08 | 2023-08-20 10:08 | 24 | 2023-08-19 09:15 | 2023-08-19 16:35 | 440 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 134565 | Mayanja, Mr. Elvis Manga | N - - - |  | Voice Communication
| CM-2023-12180030 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 OPEN LOUNGE AREA |  | FM008 |  | 2023-09-11 19:35 | 2023-09-11 20:35 | 2023-09-12 20:35 | 24 | 2023-09-11 19:40 | 2023-09-11 21:00 | 80 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17573 | 17053 |  |  | 100626 | Nissanka Arachchilage, Mr. Amila Nissanka | N - - - |  | Voice Communication
| CM-2023-12188424 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 SITTING AREA- AC TOO HOT |  | FM008 |  | 2023-09-15 18:08 | 2023-09-15 19:08 | 2023-09-16 19:08 | 24 | 2023-09-15 18:15 | 2023-09-16 00:30 | 375 | 60 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106914 | 17053 |  |  | 71476 | Kaur Hargit Singh, Ms. Mangeet | N - - - |  | Voice Communication
| CM-2023-12229615 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD – FFL1 NEXT TO A1 GATE |  | FM008 |  | 2023-09-29 09:42 | 2023-09-29 10:42 | 2023-09-30 10:42 | 24 | 2023-09-29 09:50 | 2023-09-29 15:02 | 312 | 70 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | 77496 | Falul, Mrs. Fathima Shazra | N - - - |  | Voice Communication
| CM-2023-12257511 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD IN OPEN AREA - FFL2 LOUNGE |  | FM008 |  | 2023-10-08 02:24 | 2023-10-08 03:24 | 2023-10-09 03:24 | 24 | 2023-10-08 02:30 | 2023-10-08 05:00 | 150 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 29674 | Tangilan, Ms. Mary Jane Ignacio | N - - - |  | Voice Communication
| CM-2023-12485890 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD – FFL2 SEATING AREA |  | FM008 |  | 2023-12-19 01:16 | 2023-12-19 02:16 | 2023-12-20 02:16 | 24 | 2023-12-19 01:20 | 2023-12-19 04:00 | 160 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2024-12558297 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - GL1 PASSENGER SEATING AREA |  | FM008 |  | 2024-01-12 16:07 | 2024-01-12 17:07 | 2024-01-13 17:07 | 24 | 2024-01-12 16:15 | 2024-01-12 18:40 | 145 | 35 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 87515 | Baulete, Ms. Rhea Mae Lumatap | N - - - |  | Voice Communication
| CM-2024-12713253 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AHU-A1121-202 FILTER DIRTY AIRSIDE-CONCOURSE A-SECOND FLOOR AREA 005 |  | FM008 |  | 2024-03-09 14:32 | 2024-03-09 15:32 | 2024-03-10 15:32 | 24 | 2024-03-09 14:40 | 2024-03-09 20:00 | 320 | 115 | 3 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2024-12768267 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AHU-A1121-202-ABNORMAL NOSY-A2-05-31 |  | FM008 |  | 2024-03-26 08:36 | 2024-03-26 09:36 | 2024-03-27 09:36 | 24 | 2024-03-26 08:45 | 2024-03-26 14:50 | 365 | 365 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 95217 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-10934643 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 OPEN LOUNGE AC TOO COLD |  | FM008 |  | 2022-08-12 22:16 | 2022-08-12 23:16 | 2022-08-13 23:16 | 24 | 2022-08-12 22:20 | 2022-08-12 23:45 | 85 | 45 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 55709 |  |  | 83643 | Vazhayil Kandoth, Mr. Safran | N - - - |  | Voice Communication
| CM-2022-10988678 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD SITTING AREA |  | FM008 |  | 2022-08-29 04:14 | 2022-08-29 05:14 | 2022-08-30 05:14 | 24 | 2022-08-29 04:20 | 2022-08-29 06:15 | 115 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | 87515 | Baulete, Ms. Rhea Mae Lumatap | N - - - |  | Voice Communication
| CM-2022-10997990 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | Male shower area and corridor ac is not effective (too warm) - FFL1 |  | FM008 |  | 2022-09-05 02:40 | 2022-09-05 03:40 | 2022-09-06 03:40 | 24 | 2022-09-05 02:45 | 2022-09-05 04:00 | 75 | 60 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 94954 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | E-mail
| CM-2022-11101322 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -SEATING AREA |  | FM008 |  | 2022-10-12 23:30 | 2022-10-13 00:30 | 2022-10-14 00:30 | 24 | 2022-10-12 23:35 | 2022-10-12 23:58 | 23 | 23 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 122228 | Tsiri, Ms. Lerato Martinah | N - - - |  | Voice Communication
| CM-2022-11103124 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | MALE SHOWER ROOM EXHAUST GRILL DUSTY FFL2 |  | FM008 |  | 2022-10-16 01:57 | 2022-10-16 02:57 | 2022-10-17 02:57 | 24 | 2022-10-16 02:00 | 2022-10-16 06:00 | 240 | 175 | 3 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | E-mail
| CM-2022-11313297 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN FFL1 |  | FM008 |  | 2022-12-26 08:45 | 2022-12-26 09:45 | 2022-12-27 09:45 | 24 | 2022-12-26 08:50 | 2022-12-26 10:00 | 70 | 70 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 121140 | Hemba Thanthirige, Ms. Dilini Vishdhika Sammani Perera | N - - - |  | Voice Communication
| CM-2023-11495443 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO WARM - FREQUENT FLYER LOUNGE 2 ENTIRE LOUNGE |  | FM008 |  | 2023-03-03 00:08 | 2023-03-03 01:08 | 2023-03-04 01:08 | 24 | 2023-03-03 00:15 | 2023-03-03 01:00 | 45 | 45 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | Voice Communication
| CM-2023-11603126 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | ACTEMPERATURE TOO WARM (PASSENGER SEATING AREA )-FREQUENT FLYER LOUNGE 1 |  | FM008 |  | 2023-03-27 18:31 | 2023-03-27 19:31 | 2023-03-28 19:31 | 24 | 2023-03-27 18:35 | 2023-03-27 20:00 | 85 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 87530 | Sriwilai, Ms. Nittaya | N - - - |  | Voice Communication
| CM-2023-11691158 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -OPEN AREA FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-04-20 23:51 | 2023-04-21 00:51 | 2023-04-22 00:51 | 24 | 2023-04-20 23:55 | 2023-04-21 04:00 | 245 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 124340 | Zulueta, Ms. Emely Labrador | N - - - |  | Voice Communication
| CM-2023-11805764 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD FFL2 RECEPTION AREA |  | FM008 |  | 2023-05-19 17:06 | 2023-05-19 18:06 | 2023-05-20 18:06 | 24 | 2023-05-19 17:10 | 2023-05-19 23:00 | 350 | 60 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 17053 |  |  | 130067 | Nanjirah, Ms. Rosemary Ayanga | N - - - |  | Voice Communication
| CM-2023-11836801 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC IS NOT WORKING -FFL2 -LOUNGE -OPEN SEATING AREA -FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-05-31 06:53 | 2023-05-31 07:53 | 2023-06-01 07:53 | 24 | 2023-05-31 07:00 | 2023-05-31 10:00 | 180 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17336 | 87807 |  |  | 100398 | Chatterjee, Mr. Sanjib | N - - - |  | Voice Communication
| CM-2023-11886196 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO HOT IN FFL2 OPEN DINING AREA |  | FM008 |  | 2023-06-15 13:36 | 2023-06-15 14:36 | 2023-06-16 14:36 | 24 | 2023-06-15 13:40 | 2023-06-15 16:15 | 155 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | R14962 | Ganeshan , Mr. Arunkumar | N - - - |  | Voice Communication
| CM-2023-11883735 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C IS TOO HOT ENTIRE FFL2 |  | FM008 |  | 2023-06-15 13:17 | 2023-06-15 14:17 | 2023-06-16 14:17 | 24 | 2023-06-15 13:25 | 2023-06-15 16:15 | 170 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 68060 | 87807 |  |  | 130067 | Nanjirah, Ms. Rosemary Ayanga | N - - - |  | Voice Communication
| CM-2023-11886595 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC IS TOO WARM- FFL2 DEATING AND DINING AREA- ALSO FFL1 |  | FM008 |  | 2023-06-17 06:48 | 2023-06-17 07:48 | 2023-06-18 07:48 | 24 | 2023-06-17 06:55 | 2023-06-17 11:35 | 280 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 87807 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-11909086 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD SEATING AREA FFL2 |  | FM008 |  | 2023-06-22 04:10 | 2023-06-22 05:10 | 2023-06-23 05:10 | 24 | 2023-06-22 04:15 | 2023-06-22 06:30 | 135 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106972 | 17053 |  |  | 28329 | Gutierrez, Mr. Ronnie Natac | N - - - |  | Voice Communication
| CM-2023-11972697 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | OPEN AREA (BAR COUNTER) AC TOO HOT - FFL2 |  | FM008 |  | 2023-07-12 16:48 | 2023-07-12 17:48 | 2023-07-13 17:48 | 24 | 2023-07-12 16:50 | 2023-07-12 20:00 | 190 | 70 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 87807 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | Voice Communication
| CM-2023-12253656 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -FFL1 DINING |  | FM008 |  | 2023-10-04 14:14 | 2023-10-04 15:14 | 2023-10-05 15:14 | 24 | 2023-10-04 14:20 | 2023-10-04 15:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17333 | 87807 |  |  | 82773 | Nefzi, Mr. Ahmed | N - - - |  | Voice Communication
| CM-2024-12532732 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - MAIN RECPETION FFL1 |  | FM008 |  | 2024-01-03 09:47 | 2024-01-03 10:47 | 2024-01-04 10:47 | 24 | 2024-01-03 09:55 | 2024-01-03 17:00 | 425 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 77496 | Falul, Mrs. Fathima Shazra | N - - - |  | Voice Communication
| CM-2024-12593996 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C VENTS DIRTY A1-FFL1-27 |  | FM008 |  | 2024-01-27 09:51 | 2024-01-27 10:51 | 2024-01-28 10:51 | 24 | 2024-01-27 10:05 | 2024-01-27 12:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12593997 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C VENTS DIRTY A1-FFL1-28 |  | FM008 |  | 2024-01-27 09:53 | 2024-01-27 10:53 | 2024-01-28 10:53 | 24 | 2024-01-27 10:05 | 2024-01-27 12:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12796676 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 OPEN AREA SITTING AREA |  | FM008 |  | 2024-04-06 20:47 | 2024-04-06 21:47 | 2024-04-07 21:47 | 24 | 2024-04-06 20:55 | 2024-04-06 23:30 | 155 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 133396 | 17053 |  |  | 87522 | Ouacif, Mr. Isslam | N - - - |  | Voice Communication
| CM-2023-12258106 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC NOT WORKING -FFL1 ALL AREA |  | FM008 |  | 2023-10-06 19:08 | 2023-10-06 20:08 | 2023-10-07 20:08 | 24 | 2023-10-06 19:15 | 2023-10-06 23:58 | 283 | 31 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-12278418 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 OPEN AREA |  | FM008 |  | 2023-10-12 03:51 | 2023-10-12 04:51 | 2023-10-13 04:51 | 24 | 2023-10-12 03:55 | 2023-10-12 05:35 | 100 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 61871 | Kaluarachchige Don, Ms. Nuradha | N - - - |  | Voice Communication
| CM-2023-12322562 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD WHOLE LOUNGE FFL1 AND FLL2 |  | FM008 |  | 2023-10-28 02:59 | 2023-10-28 03:59 | 2023-10-29 03:59 | 24 | 2023-10-28 03:05 | 2023-10-28 06:40 | 215 | 40 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | 124129 | Elhassi, Ms. Houda | N - - - |  | Voice Communication
| CM-2023-12382325 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD – FFL2 LOUNGE OPEN AREA |  | FM008 |  | 2023-11-13 14:21 | 2023-11-13 15:21 | 2023-11-14 15:21 | 24 | 2023-11-13 14:25 | 2023-11-13 16:00 | 95 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 87807 |  |  | 63260 | Kasibante, Mr. Macknon | N - - - |  | Voice Communication
| CM-2023-12413973 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 BAR COUNTER AREA AC VENT PAINT TOUCH REQUIRED |  | FM008 |  | 2023-11-26 11:57 | 2023-11-26 12:57 | 2023-11-27 12:57 | 24 | 2023-11-26 12:05 | 2023-11-26 16:00 | 235 | 175 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM12941 | Kadam, Mr. Shailesh Eknath | N - - - |  | Voice Communication
| CM-2023-12508073 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - SEATING AREA |  | FM008 |  | 2023-12-28 02:25 | 2023-12-28 03:25 | 2023-12-29 03:25 | 24 | 2023-12-28 02:30 | 2023-12-28 06:40 | 250 | 40 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 63260 | Kasibante, Mr. Macknon | N - - - |  | Voice Communication
| CM-2023-12513383 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL1 FAMILY AREA AC TOO COLD |  | FM008 |  | 2023-12-29 11:41 | 2023-12-29 12:41 | 2023-12-30 12:41 | 24 | 2023-12-29 11:50 | 2023-12-29 18:30 | 400 | 68 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 112744 | Bhawarlal, Mr. Jithendar | N - - - |  | Voice Communication
| CM-2024-12609265 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD FFL2 SITTING AREA |  | FM008 |  | 2024-01-29 16:27 | 2024-01-29 17:27 | 2024-01-30 17:27 | 24 | 2024-01-29 16:35 | 2024-01-29 18:00 | 85 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 82773 | Nefzi, Mr. Ahmed | N - - - |  | Voice Communication
| CM-2024-12609233 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD FFL2 OPEN AREA NEAR BUFFET COUNTER AREA |  | FM008 |  | 2024-02-01 03:05 | 2024-02-01 04:05 | 2024-02-02 04:05 | 24 | 2024-02-01 03:10 | 2024-02-01 06:00 | 170 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 30842 | Anwari, Mr. Tanveer Iqbal | N - - - |  | Voice Communication
| CM-2024-12819402 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD – ENTIRE LOUNGE A2 FFL2 14 |  | FM008 |  | 2024-04-08 08:20 | 2024-04-08 09:20 | 2024-04-09 09:20 | 24 | 2024-04-08 08:25 | 2024-04-08 14:00 | 335 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 77496 | Falul, Mrs. Fathima Shazra | N - - - |  | Voice Communication
| CM-2024-12536642 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2-OPEN AREA AC TEMP TOO COLD -A2-FFL2-05 |  | FM008 |  | 2024-01-05 20:04 | 2024-01-05 21:04 | 2024-01-06 21:04 | 24 | 2024-01-05 20:10 | 2024-01-05 23:58 | 228 | 38 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 77406 | 17053 |  |  | FM7722 | PATRICK | N - - - |  | Voice Communication
| CM-2022-10223767 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM AC DUCT NEAR T1-0A-47- INSIDE AND OUTSIDE |  | FM008 |  | 2022-03-08 05:50 | 2022-03-08 06:50 | 2022-03-09 06:50 | 24 | 2022-03-08 06:00 | 2022-03-08 09:00 | 180 | 370 | 4 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 17053 |  |  | GSS639 | MANOJ | N - - - |  | Voice Communication
| CM-2022-10989542 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 DINING AREA |  | FM008 |  | 2022-09-03 02:41 | 2022-09-03 03:41 | 2022-09-04 03:41 | 24 | 2022-09-03 02:50 | 2022-09-03 05:00 | 130 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 55709 |  |  | FM6922 | Murerwa, Ms. Silvia Gatwiri | N - - - |  | Voice Communication
| CM-2022-11097826 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -FFL2 SEATING AREA |  | FM008 |  | 2022-10-12 22:49 | 2022-10-12 23:49 | 2022-10-13 23:49 | 24 | 2022-10-12 22:50 | 2022-10-12 23:30 | 40 | 40 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 122228 | Tsiri, Ms. Lerato Martinah | N - - - |  | Voice Communication
| CM-2022-11135433 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | PASSENGER SITTING AREA,AC TEMPERATURE TOO COLD.-CONCOURSE A-FREQUENT FLYER LOUNGE 2. |  | FM008 |  | 2022-10-26 00:02 | 2022-10-26 01:02 | 2022-10-27 01:02 | 24 | 2022-10-26 00:05 | 2022-10-26 01:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 71476 | Kaur Hargit Singh, Ms. Mangeet | N - - - |  | Voice Communication
| CM-2022-11321837 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 OPEN LOUNGE AREA AC TOO COLD |  | FM008 |  | 2022-12-27 21:13 | 2022-12-27 22:13 | 2022-12-28 22:13 | 24 | 2022-12-27 21:15 | 2022-12-27 22:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-11348411 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO HOT - FFL2 ENTIRE QUEIT AREA |  | FM008 |  | 2023-01-06 11:48 | 2023-01-06 12:48 | 2023-01-07 12:48 | 24 | 2023-01-06 11:55 | 2023-01-06 15:35 | 220 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | 109304 | Mahajani, Mr. Amit Ravindra | N - - - |  | Voice Communication
| CM-2023-11422160 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD -OPEN AREA |  | FM008 |  | 2023-02-01 21:09 | 2023-02-01 22:09 | 2023-02-02 22:09 | 24 | 2023-02-01 21:15 | 2023-02-01 22:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 87807 |  |  | 28329 | Gutierrez, Mr. Ronnie Natac | N - - - |  | Voice Communication
| CM-2023-11622288 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C IS TOO HOT FFL2 RECEPTION |  | FM008 |  | 2023-04-06 22:19 | 2023-04-06 23:19 | 2023-04-07 23:19 | 24 | 2023-04-06 22:25 | 2023-04-06 23:40 | 75 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | 127466 | Koduvayur Subramanian, Mr. Vaidyanathan | N - - - |  | Voice Communication
| CM-2023-11655129 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD , DINING AREA FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-04-14 00:24 | 2023-04-14 01:24 | 2023-04-15 01:24 | 24 | 2023-04-14 00:30 | 2023-04-14 02:30 | 120 | 60 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | 100398 | Chatterjee, Mr. Sanjib | N - - - |  | Voice Communication
| CM-2022-10825838 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN FFL1 & FFL2 |  | FM008 |  | 2022-07-08 21:39 | 2022-07-08 22:39 | 2022-07-09 22:39 | 24 | 2022-07-08 21:45 | 2022-07-08 22:50 | 65 | 40 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 95217 |  |  | 83027 | A K R Kurup, Mr. Sambhu | N - - - |  | Voice Communication
| CM-2023-11502755 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | FFL2 BACK OF HOUSE CORRIDOR (TOILET/KITCHEN) AC VENT DIRTY |  | FM008 |  | 2023-02-28 19:31 | 2023-02-28 20:31 | 2023-03-01 20:31 | 24 | 2023-02-28 19:35 | 2023-02-28 22:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 94954 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12239034 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - DINING AREA, A2-FFL2-01 |  | FM008 |  | 2023-10-01 11:54 | 2023-10-01 12:54 | 2023-10-02 12:54 | 24 | 2023-10-01 12:00 | 2023-10-01 15:15 | 195 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | FM7722 | PATRICK | N - - - |  | Voice Communication
| CM-2023-12252436 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD FFL1 RECEPTION |  | FM008 |  | 2023-10-03 18:07 | 2023-10-03 19:07 | 2023-10-04 19:07 | 24 | 2023-10-03 18:15 | 2023-10-03 20:00 | 105 | 65 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 112744 | Bhawarlal, Mr. Jithendar | N - - - |  | Voice Communication
| CM-2024-12749078 | ASD-COA-SFL005-AHU076 | AIR HANDLING UNIT-05 | AC TOO COLD - ENTIRE FFL2 LOUNGE |  | FM008 |  | 2024-03-19 08:42 | 2024-03-19 09:42 | 2024-03-20 09:42 | 24 | 2024-03-19 08:50 | 2024-03-19 12:05 | 195 | 65 | 1 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 95217 |  |  | 103922 | Istiak, Mr. Shamim | N - - - |  | Voice Communication
| CM-2022-10272500 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO COLD RCT B |  | FM008 |  | 2022-03-21 19:40 | 2022-03-21 20:40 | 2022-03-22 20:40 | 24 | 2022-03-21 19:50 | 2022-03-21 22:00 | 130 | 70 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10912286 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | REQUIRED TO MAINTAIN THE TEMPERATURE DUE TO HUMIDITY ON THE GLASS NOT VISIBLE - B6-20-01 (RAMP CONTROL TOWER) |  | FM008 |  | 2022-08-06 22:16 | 2022-08-06 23:16 | 2022-08-07 23:16 | 24 | 2022-08-06 22:25 | 2022-08-06 23:40 | 75 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 55709 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2023-11976044 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO COLD MIST FORMING ON GLASS RCTB |  | FM008 |  | 2023-07-14 21:03 | 2023-07-14 22:03 | 2023-07-15 22:03 | 24 | 2023-07-14 21:10 | 2023-07-14 23:58 | 168 | 63 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2023-12207544 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | B5-20-02 - AC HOT & SMELLY /CHOKING |  | FM008 |  | 2023-09-24 11:50 | 2023-09-24 12:50 | 2023-09-25 12:50 | 24 | 2023-09-24 11:55 | 2023-09-24 17:55 | 360 | 65 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 95217 |  |  | 55137 | Lazaro, Mr. Mark Anthony Jocson | N - - - |  | Voice Communication
| CM-2022-11079376 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO COLD (HUMIDITY FORMMING ON THE GLASS) |  | FM008 |  | 2022-10-06 22:06 | 2022-10-06 23:06 | 2022-10-07 23:06 | 24 | 2022-10-06 22:10 | 2022-10-07 01:00 | 170 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-11170973 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC IS TOO COLD- B6-20-01 (RAMP CONTROL TOWER))-AIRSIDE-CONCOURSE B-SIXTH FLOOR AREA 020 |  | FM008 |  | 2022-11-08 02:20 | 2022-11-08 03:20 | 2022-11-09 03:20 | 24 | 2022-11-08 02:25 | 2022-11-08 03:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 17053 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2023-11929876 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AHU-A1122-701 FILTER DIRTY |  | FM008 |  | 2023-06-26 07:08 | 2023-06-26 08:08 | 2023-06-27 08:08 | 24 | 2023-06-26 07:15 | 2023-06-26 08:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12369741 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | (AHU-A1122-701)TEMP GAUGE FAULTY-CONCOURSE B-APRON CONTROL TOWER |  | FM008 |  | 2023-11-12 09:18 | 2023-11-12 10:18 | 2023-11-13 10:18 | 24 | 2023-11-12 09:25 | 2023-11-12 10:30 | 65 | 182 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | DAMAGED | TEMPERATURE GAUGE DAMAGED | REPAIRED/REPLACED | 77406 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2024-12554397 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO COLD – RCT B B6-20-01 NEAR B5-20-02 |  | FM008 |  | 2024-01-10 09:17 | 2024-01-10 10:17 | 2024-01-11 10:17 | 24 | 2024-01-10 09:25 | 2024-01-10 11:00 | 95 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 106973 | 17053 |  |  | 117945 | Pratihar, Mr. Pritam | N - - - |  | Voice Communication
| CM-2022-10873228 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | RCT B AC TOO COLD B6-20-01 |  | FM008 |  | 2022-07-27 19:29 | 2022-07-27 20:29 | 2022-07-28 20:29 | 24 | 2022-07-27 19:35 | 2022-07-27 20:20 | 45 | 45 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10996913 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO COLD |  | FM008 |  | 2022-09-03 23:00 | 2022-09-04 | 2022-09-05 | 24 | 2022-09-03 23:05 | 2022-09-03 23:30 | 25 | 25 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | Voice Communication
| CM-2024-12713896 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AHU-A1122-701 B6-20-01 MOTOR NOISY |  | FM008 |  | 2024-03-09 08:59 | 2024-03-09 09:59 | 2024-03-10 09:59 | 24 | 2024-03-09 09:05 | 2024-03-09 11:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 138627 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-10223713 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO HOT RCT B |  | FM008 |  | 2022-03-07 19:28 | 2022-03-07 20:28 | 2022-03-08 20:28 | 24 | 2022-03-07 19:35 | 2022-03-07 20:35 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 17053 |  |  | 63880 | Maacha, Mr. Hamdi | N - - - |  | Voice Communication
| CM-2022-10262477 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC IS TOO COLD IN RCT-B |  | FM008 |  | 2022-03-19 14:59 | 2022-03-19 15:59 | 2022-03-20 15:59 | 24 | 2022-03-19 15:05 | 2022-03-19 15:35 | 30 | 30 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94953 | 87807 |  |  | 60309 | Tuwei, Ms. Vivian Cheptoo | N - - - |  | Voice Communication
| CM-2023-11362432 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC IS TOO COLD -: B6-20-01 (RAMP CONTROL TOWER))-AIRSIDE-CONCOURSE B-SIXTH FLOOR AREA 020 |  | FM008 |  | 2023-01-11 02:48 | 2023-01-11 03:48 | 2023-01-12 03:48 | 24 | 2023-01-11 02:55 | 2023-01-11 06:15 | 200 | 65 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 61072 | Odhiambo, Ms. Annette Auko | N - - - |  | E-mail
| CM-2022-10914148 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | AC TOO HOT - B5-20-01,RCT B |  | FM008 |  | 2022-08-07 05:05 | 2022-08-07 06:05 | 2022-08-08 06:05 | 24 | 2022-08-07 05:10 | 2022-08-07 06:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 55709 |  |  | 55804 | Ochava, Mr. Carlito Jr Friginal | N - - - |  | Voice Communication
| CM-2023-11487990 | ASD-COB-APR-AHU094 | AIR HANDLING UNIT-05 | HEATER NOT WORKING - (AHU-A1122-701) AIRSIDE-CONCOURSE B-APRON CONTROL TOWER |  | FM008 |  | 2023-02-26 11:50 | 2023-02-26 12:50 | 2023-02-27 12:50 | 24 | 2023-02-26 12:00 | 2023-02-26 14:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10128983 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD - RAMP CONTROL TOWER-B TOP FLOOR |  | FM008 |  | 2022-02-12 09:19 | 2022-02-12 10:19 | 2022-02-13 10:19 | 24 | 2022-02-12 09:25 | 2022-02-12 10:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 55709 |  |  | 57956 | Zash, Mr. Raad Hussam Fuad | N - - - |  | Voice Communication
| CM-2022-11176408 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD RCTB SIXTH FLOOR |  | FM008 |  | 2022-11-10 | 2022-11-10 01:00 | 2022-11-11 01:00 | 24 | 2022-11-10 00:10 | 2022-11-10 03:00 | 170 | 40 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-11022899 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | TO INCREASE THE TEMPERATURE -RCTB B6-20-01 |  | FM008 |  | 2022-09-13 00:37 | 2022-09-13 01:37 | 2022-09-14 01:37 | 24 | 2022-09-13 00:45 | 2022-09-13 01:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 87807 | 17053 |  |  | 117945 | Pratihar, Mr. Pritam | N - - - |  | Voice Communication
| CM-2023-11929877 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AHU-A1122-702 FILTER DIRTY |  | FM008 |  | 2023-06-26 07:09 | 2023-06-26 08:09 | 2023-06-27 08:09 | 24 | 2023-06-26 07:15 | 2023-06-26 10:30 | 195 | 205 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12222606 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-09-25 11:32 | 2023-09-25 12:32 | 2023-09-26 12:32 | 24 | 2023-09-25 11:40 | 2023-09-25 14:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68485 | 87807 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2022-11024066 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | RCT B AC TOO COLD |  | FM008 |  | 2022-09-14 21:42 | 2022-09-14 22:42 | 2022-09-15 22:42 | 24 | 2022-09-14 21:50 | 2022-09-14 23:15 | 85 | 70 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2024-12713897 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AHU-A1122-702 B6-20-01 MOTOR NOISY |  | FM008 |  | 2024-03-09 09:02 | 2024-03-09 10:02 | 2024-03-10 10:02 | 24 | 2024-03-09 09:10 | 2024-03-09 16:15 | 425 | 365 | 3 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 138627 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-10273842 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD RCTB |  | FM008 |  | 2022-03-22 21:44 | 2022-03-22 22:44 | 2022-03-23 22:44 | 24 | 2022-03-22 21:50 | 2022-03-22 23:55 | 125 | 40 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-9950845 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD RCT B |  | FM008 |  | 2022-01-01 20:07 | 2022-01-01 21:07 | 2022-01-02 21:07 | 24 | 2022-01-01 20:10 | 2022-01-01 23:55 | 225 | 65 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | 60309 | Tuwei, Ms. Vivian Cheptoo | N - - - |  | Voice Communication
| CM-2022-10366646 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD RCT B - B6-20-01 |  | FM008 |  | 2022-04-17 08:50 | 2022-04-17 09:50 | 2022-04-18 09:50 | 24 | 2022-04-17 08:55 | 2022-04-17 09:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 85125 | 17053 |  |  | 57956 | Zash, Mr. Raad Hussam Fuad | N - - - |  | Voice Communication
| CM-2022-10328651 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD FOG FORMING ON GLASS RCTB |  | FM008 |  | 2022-04-08 01:10 | 2022-04-08 02:10 | 2022-04-09 02:10 | 24 | 2022-04-08 01:15 | 2022-04-08 02:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-10578729 | ASD-COB-APR-AHU095 | AIR HANDLING UNIT-05 | AC TOO COLD - RCTB - B6-20-01 |  | FM008 |  | 2022-04-22 18:20 | 2022-04-22 19:20 | 2022-04-23 19:20 | 24 | 2022-04-22 18:30 | 2022-04-22 20:00 | 90 | 65 | 2 | HVAC |  | Closed | Normal | APRON CONTROL TOWER | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 17053 |  |  | 99323 | Vaddalapu, Mr. Ravitheja | N - - - |  | Voice Communication
| CM-2022-11063525 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | AHU-A1157-B01 – BELT DAMAGED-- |  | FM008 |  | 2022-09-27 19:02 | 2022-09-27 20:02 | 2022-09-28 20:02 | 24 | 2022-09-27 19:10 | 2022-09-27 23:40 | 270 | 125 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12041204 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING – MEC ROOM BB-17-09 |  | FM008 |  | 2023-08-01 19:11 | 2023-08-01 20:11 | 2023-08-02 20:11 | 24 | 2023-08-01 19:20 | 2023-08-02 00:49 | 329 | 303 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-12323733 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | SUPPLY AIR LOW ALARM//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.BSMTP1.IBFWB01.AHUB01.SYSALM.SUFLOALM / /MECHANICAL ROOM BB-17-09 |  | FM008 |  | 2023-10-25 08:13 | 2023-10-25 09:13 | 2023-10-26 09:13 | 24 | 2023-10-25 08:20 | 2023-10-25 16:00 | 460 | 245 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-11152416 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 190 ,-SUPPLY LOW AIR FLOW,-CONCOURSE B-BASEMENT AREA 17A. |  | FM008 |  | 2022-10-31 07:21 | 2022-10-31 08:21 | 2022-11-01 08:21 | 24 | 2022-10-31 07:30 | 2022-10-31 10:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12366056 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | CABIN LIGHT NOT WORKING -BB-17-09 |  | FM008 |  | 2023-11-09 22:29 | 2023-11-09 23:29 | 2023-11-10 23:29 | 24 | 2023-11-09 22:35 | 2023-11-10 01:05 | 150 | 300 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106914 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-11933175 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | AHU-A1157-B01 FILTER DIRTY |  | FM008 |  | 2023-06-27 07:57 | 2023-06-27 08:57 | 2023-06-28 08:57 | 24 | 2023-06-27 08:05 | 2023-06-27 12:45 | 280 | 365 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12322337 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | UNUSUAL NOISY FROM MOTOR - AHU-A1157-B01 - MECHANICAL ROOM BB-17-09 |  | FM008 |  | 2023-10-27 07:17 | 2023-10-27 08:17 | 2023-10-28 08:17 | 24 | 2023-10-27 07:25 | 2023-10-27 11:25 | 240 | 720 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12296883 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | BB 17 11 MALE WASH ROOM - AC NOT WORKING |  | FM008 |  | 2023-10-18 10:05 | 2023-10-18 11:05 | 2023-10-19 11:05 | 24 | 2023-10-18 10:10 | 2023-10-18 13:30 | 200 | 70 | 1 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | FM12877 | Naik, Mr. Rohith Sheshappa | N - - - |  | Voice Communication
| CM-2022-10106040 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-02-05 12:19 | 2022-02-05 13:19 | 2022-02-06 13:19 | 24 | 2022-02-05 12:25 | 2022-02-05 15:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11149905 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | CHILLED WATER PIPE LINE LEAKING BB-17-10 |  | FM008 |  | 2022-10-31 12:27 | 2022-10-31 13:27 | 2022-11-01 13:27 | 24 | 2022-10-31 12:32 | 2022-10-31 16:45 | 253 | 185 | 4 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106972 | 17053 |  |  | CT11169 | ROHAN | N - - - |  | Voice Communication
| CM-2023-12138655 | ASD-COB-BAS17A-AHU190 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-B01) |  | FM008 |  | 2023-09-01 19:24 | 2023-09-01 20:24 | 2023-09-02 20:24 | 24 | 2023-09-01 19:30 | 2023-09-01 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BASEMENT AREA 17A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 133396 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-10262535 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY-BG-17-03 |  | FM008 |  | 2022-03-19 19:28 | 2022-03-19 20:28 | 2022-03-20 20:28 | 24 | 2022-03-19 19:35 | 2022-03-19 22:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10365602 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU FLITER DIRTY - BG-17-03 |  | FM008 |  | 2022-04-15 21:39 | 2022-04-15 22:39 | 2022-04-16 22:39 | 24 | 2022-04-15 21:45 | 2022-04-15 23:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17053 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-10365691 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - BG-17-03 |  | FM008 |  | 2022-04-16 13:20 | 2022-04-16 14:20 | 2022-04-17 14:20 | 24 | 2022-04-16 13:25 | 2022-04-16 15:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11029819 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU-A1122-008 – AHU LAMP NOT WORKING |  | FM008 |  | 2022-09-17 19:31 | 2022-09-17 20:31 | 2022-09-18 20:31 | 24 | 2022-09-17 19:40 | 2022-09-18 01:30 | 350 | 179 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95217 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11095591 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1122-008 – BG-17-03 |  | FM008 |  | 2022-10-10 07:44 | 2022-10-10 08:44 | 2022-10-11 08:44 | 24 | 2022-10-10 07:50 | 2022-10-10 09:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11329998 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1122-008 – BG-17-03 |  | FM008 |  | 2022-12-30 19:40 | 2022-12-30 20:40 | 2022-12-31 20:40 | 24 | 2022-12-30 19:45 | 2022-12-30 22:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12035733 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU-A1122-008-DUCT INSULATION DAMAGE - |  | FM008 |  | 2023-08-03 00:56 | 2023-08-03 01:56 | 2023-08-04 01:56 | 24 | 2023-08-03 01:05 | 2023-08-03 03:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10995521 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1122-008 BG-17-03 |  | FM008 |  | 2022-09-07 01:34 | 2022-09-07 02:34 | 2022-09-08 02:34 | 24 | 2022-09-07 01:40 | 2022-09-07 03:10 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11122859 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU-A1122-008 FILTER DIRTY |  | FM008 |  | 2022-10-24 00:40 | 2022-10-24 01:40 | 2022-10-25 01:40 | 24 | 2022-10-24 00:45 | 2022-10-24 03:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 95217 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2023-11860348 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-008 - BG-17-08 |  | FM008 |  | 2023-06-06 20:00 | 2023-06-06 21:00 | 2023-06-07 21:00 | 24 | 2023-06-06 20:05 | 2023-06-07 01:35 | 330 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 94954 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12345542 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | BG-17-03 AHU-A1122-008 COOLING COIL DIRTY |  | FM008 |  | 2023-11-03 20:31 | 2023-11-03 21:31 | 2023-11-04 21:31 | 24 | 2023-11-03 20:40 | 2023-11-03 23:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11163812 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU-A1122-008- ISOLATION SPRING DAMAGED-- |  | FM008 |  | 2022-11-06 13:41 | 2022-11-06 14:41 | 2022-11-07 14:41 | 24 | 2022-11-06 13:45 | 2022-11-06 15:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 94953 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11259969 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU-A1122-008 – DUCT INSULATION DAMAGED – BG-17-03 |  | FM008 |  | 2022-12-11 14:33 | 2022-12-11 15:33 | 2022-12-12 15:33 | 24 | 2022-12-11 14:40 | 2022-12-11 18:40 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11439518 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU-A1122-008- FILTER DIRTY -BG-17-03 |  | FM008 |  | 2023-02-07 01:07 | 2023-02-07 02:07 | 2023-02-08 02:07 | 24 | 2023-02-07 01:15 | 2023-02-07 04:00 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11484216 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY -BG-17-03 |  | FM008 |  | 2023-02-24 19:22 | 2023-02-24 20:22 | 2023-02-25 20:22 | 24 | 2023-02-24 19:30 | 2023-02-24 23:00 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM5553 | MOHAMAD HANEEF ABDUL HAMEED MAJGAONKAR, | N - - - |  | Voice Communication
| CM-2024-12565200 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | LEVEL 1 COMMON AREA SECTION 1 FRONT OF B1 17 02 DEPLOYMENT ROOM AC VENTS GRILL CLEANING REQUIRED |  | FM008 |  | 2024-01-16 02:12 | 2024-01-16 03:12 | 2024-01-17 03:12 | 24 | 2024-01-16 02:20 | 2024-01-16 04:00 | 100 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM12286 | Camelet, Ms. Milagros Revilla | N - - - |  | E-mail
| CM-2022-10788763 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-06-28 10:30 | 2022-06-28 11:30 | 2022-06-29 11:30 | 24 | 2022-06-28 10:35 | 2022-06-28 12:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11975530 | ASD-COB-GFL017-AHU086 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1122-008– B1-17-03 – |  | FM008 |  | 2023-07-15 13:42 | 2023-07-15 14:42 | 2023-07-16 14:42 | 24 | 2023-07-15 13:45 | 2023-07-15 17:15 | 210 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11030927 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AHU LAMP IS NOT WORKING |  | FM008 |  | 2022-09-18 00:43 | 2022-09-18 01:43 | 2022-09-19 01:43 | 24 | 2022-09-18 00:53 | 2022-09-18 03:10 | 137 | 186 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11786395 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AC TOO WARM - NEAR B2-17-04 CORRIDOR AREA |  | FM008 |  | 2023-05-14 04:28 | 2023-05-14 05:28 | 2023-05-15 05:28 | 24 | 2023-05-14 04:32 | 2023-05-14 06:30 | 118 | 64 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 117605 | Abbasi, Mr. Sher Afgan | N - - - |  | Voice Communication
| CM-2023-12035734 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | A1122-011-DUCT INSULATION DAMAGE |  | FM008 |  | 2023-08-03 00:59 | 2023-08-03 01:59 | 2023-08-04 01:59 | 24 | 2023-08-03 01:05 | 2023-08-03 03:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12224041 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-25 20:36 | 2023-09-25 21:36 | 2023-09-26 21:36 | 24 | 2023-09-25 20:40 | 2023-09-25 23:30 | 170 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2022-11131292 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AHU-A1122-011 FILTER DIRTY |  | FM008 |  | 2022-10-23 20:25 | 2022-10-23 21:25 | 2022-10-24 21:25 | 24 | 2022-10-23 20:30 | 2022-10-23 22:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11211075 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1122-011)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 017 |  | FM008 |  | 2022-11-22 19:37 | 2022-11-22 20:37 | 2022-11-23 20:37 | 24 | 2022-11-22 19:45 | 2022-11-22 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11669657 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - (TAG NO:AHU-A1122-011)-CONCOURSE B-GROUND FLOOR AREA 017 |  | FM008 |  | 2023-04-16 21:31 | 2023-04-16 22:31 | 2023-04-17 22:31 | 24 | 2023-04-16 21:35 | 2023-04-16 23:45 | 130 | 485 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12041024 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1122-011 |  | FM008 |  | 2023-08-01 02:14 | 2023-08-01 03:14 | 2023-08-02 03:14 | 24 | 2023-08-01 02:20 | 2023-08-01 06:00 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12251625 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1122-011) – BG 17 03 |  | FM008 |  | 2023-10-01 21:08 | 2023-10-01 22:08 | 2023-10-02 22:08 | 24 | 2023-10-01 21:15 | 2023-10-01 23:30 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12387193 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1122-011 -BG-17-03 |  | FM008 |  | 2023-11-18 20:54 | 2023-11-18 21:54 | 2023-11-19 21:54 | 24 | 2023-11-18 21:00 | 2023-11-18 23:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12509572 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -BG-17-03 |  | FM008 |  | 2023-12-25 13:36 | 2023-12-25 14:36 | 2023-12-26 14:36 | 24 | 2023-12-25 13:45 | 2023-12-25 15:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11175870 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AHU-A1122-011 – LIGHTING FLEXIBLA CONNECTOR DAMAGED - BG-17-03 |  | FM008 |  | 2022-11-08 13:16 | 2022-11-08 14:16 | 2022-11-09 14:16 | 24 | 2022-11-08 13:20 | 2022-11-08 14:48 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17154 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11247858 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED -AHU-A1122-011 BG-17-03 |  | FM008 |  | 2022-12-05 12:57 | 2022-12-05 13:57 | 2022-12-06 13:57 | 24 | 2022-12-05 13:05 | 2022-12-05 17:15 | 250 | 970 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11531510 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1122-011 BG-17-03 |  | FM008 |  | 2023-03-08 13:51 | 2023-03-08 14:51 | 2023-03-09 14:51 | 24 | 2023-03-08 14:00 | 2023-03-08 17:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11779460 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AC GRILL DUSTY -NEAR B-MW-5 |  | FM008 |  | 2023-05-09 21:53 | 2023-05-09 22:53 | 2023-05-10 22:53 | 24 | 2023-05-09 22:00 | 2023-05-10 01:05 | 185 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 106972 |  |  | 88986 | Singh, Ms. Anamika | N - - - |  | Voice Communication
| CM-2023-11994434 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-011 – BG-17-03 |  | FM008 |  | 2023-07-19 20:13 | 2023-07-19 21:13 | 2023-07-20 21:13 | 24 | 2023-07-19 20:22 | 2023-07-19 22:20 | 118 | 354 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12157300 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1122-011)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 017 |  | FM008 |  | 2023-09-07 19:55 | 2023-09-07 20:55 | 2023-09-08 20:55 | 24 | 2023-09-07 20:00 | 2023-09-07 23:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2024-12713630 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AHU-A1122-011 FILTER DIRTY |  | FM008 |  | 2024-03-08 00:04 | 2024-03-08 01:04 | 2024-03-09 01:04 | 24 | 2024-03-08 00:10 | 2024-03-08 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10252459 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-03-14 18:59 | 2022-03-14 20:00 | 2022-03-15 20:00 | 24 | 2022-03-14 19:05 | 2022-03-14 21:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11044291 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | AHU-A1122-011 - AHU CABIN LAMP IS NOT WORKING |  | FM008 |  | 2022-09-24 19:08 | 2022-09-24 20:08 | 2022-09-25 20:08 | 24 | 2022-09-24 19:17 | 2022-09-24 22:20 | 183 | 98 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 94954 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11643682 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-011 – BG-17-03 |  | FM008 |  | 2023-04-10 09:37 | 2023-04-10 10:37 | 2023-04-11 10:37 | 24 | 2023-04-10 09:45 | 2023-04-10 12:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 94954 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11667927 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED – (AHU-A1122-011) - BG 17 03 |  | FM008 |  | 2023-04-15 09:07 | 2023-04-15 10:07 | 2023-04-16 10:07 | 24 | 2023-04-15 09:16 | 2023-04-15 13:20 | 244 | 248 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10352026 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-04-12 21:07 | 2022-04-12 22:07 | 2022-04-13 22:07 | 24 | 2022-04-12 21:15 | 2022-04-12 23:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12184279 | ASD-COB-GFL017-AHU089 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1122-011 |  | FM008 |  | 2023-09-12 20:41 | 2023-09-12 21:41 | 2023-09-13 21:41 | 24 | 2023-09-12 20:45 | 2023-09-12 23:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2022-11029815 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AHU-A1122-001- AHU LAMP NOT WORKING |  | FM008 |  | 2022-09-17 19:28 | 2022-09-17 20:28 | 2022-09-18 20:28 | 24 | 2022-09-17 19:35 | 2022-09-17 23:59 | 264 | 177 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | FAULTY CONTROL THERMOSTAT | REPLACED THE THERMOSTAT | 95217 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11078264 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1122-001 |  | FM008 |  | 2022-10-04 01:43 | 2022-10-04 02:43 | 2022-10-05 02:43 | 24 | 2022-10-04 01:45 | 2022-10-04 03:45 | 120 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 55709 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11835542 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AHU-A1122-001-(COOLING COIL DIRTY -BG-17-03 |  | FM008 |  | 2023-05-29 20:09 | 2023-05-29 21:09 | 2023-05-30 21:09 | 24 | 2023-05-29 20:15 | 2023-05-29 22:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11913676 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AHU-A1122-001-AHU CABIN LIGHTING SWITCH DAMAGED- |  | FM008 |  | 2023-06-24 10:01 | 2023-06-24 11:01 | 2023-06-25 11:01 | 24 | 2023-06-24 10:10 | 2023-06-24 12:35 | 145 | 243 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11931399 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A112-001 – MECHANICAL ROOM BG-17-03 |  | FM008 |  | 2023-06-26 19:37 | 2023-06-26 20:37 | 2023-06-27 20:37 | 24 | 2023-06-26 19:45 | 2023-06-26 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12018137 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AC TOO HOT BG-18-18 |  | FM008 |  | 2023-07-29 11:28 | 2023-07-29 12:28 | 2023-07-30 12:28 | 24 | 2023-07-29 11:35 | 2023-07-29 12:35 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | CUSTOMS | MAHANA | N - - - |  | Voice Communication
| CM-2023-12018155 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | B0-18-19 MOI AC TOO HOT |  | FM008 |  | 2023-07-29 11:48 | 2023-07-29 12:48 | 2023-07-30 12:48 | 24 | 2023-07-29 11:55 | 2023-07-29 12:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 89127 | 17053 |  |  |  | MOI ABDULLA | N - - - |  | Voice Communication
| CM-2023-12198733 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | DP1 FILTER STATUS MECHANICAL ROOM BG-17-03 - MECHANICAL ROOM BG-17-03 - CM-2023-02-0730 |  | FM008 |  | 2023-09-17 22:36 | 2023-09-17 23:36 | 2023-09-18 23:36 | 24 | 2023-09-17 22:45 | 2023-09-17 23:45 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM11814 | AYYAPPAN | - - -
| CM-2023-12358236 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING – AHU-A1122-001 - MECHANICAL ROOM BG-17-03 |  | FM008 |  | 2023-11-06 00:08 | 2023-11-06 01:08 | 2023-11-07 01:08 | 24 | 2023-11-06 00:15 | 2023-11-06 03:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12796021 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM AHU - AHU-A1122-001 - BG-17-03 |  | FM008 |  | 2024-04-04 13:27 | 2024-04-04 14:27 | 2024-04-05 14:27 | 24 | 2024-04-04 13:35 | 2024-04-04 16:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 17053 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2022-11301711 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | UNUSUAL NOISY FROM CEILING - B0-18-02 (CUSTOMS CARREL) |  | FM008 |  | 2022-12-25 08:44 | 2022-12-25 09:44 | 2022-12-26 09:44 | 24 | 2022-12-25 08:50 | 2022-12-25 17:00 | 490 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 17573 | 17053 |  |  |  | HAMAD | N - - - |  | Voice Communication
| CM-2022-10103773 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AIR LEAKING FROM ACCESS DOOR -BG-17-03 |  | FM008 |  | 2022-02-03 07:25 | 2022-02-03 08:25 | 2022-02-04 08:25 | 24 | 2022-02-03 07:30 | 2022-02-03 10:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10885732 | ASD-COB-GFL017-AHU079 | AIR HANDLING UNIT-05 | AHU-A1122-001 FILTER ALARM |  | FM008 |  | 2022-07-29 00:24 | 2022-07-29 01:24 | 2022-07-30 01:24 | 24 | 2022-07-29 00:30 | 2022-07-29 02:30 | 120 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-11029817 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 – AHU LAMP NOT WORKING |  | FM008 |  | 2022-09-17 19:30 | 2022-09-17 20:30 | 2022-09-18 20:30 | 24 | 2022-09-17 19:35 | 2022-09-17 22:30 | 175 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | HEATER NOT WORKING | REPLACED HEATING ELEMENT | 95217 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11824760 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 FILTER DIRTY - AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 017 |  | FM008 |  | 2023-05-26 23:13 | 2023-05-27 00:13 | 2023-05-28 00:13 | 24 | 2023-05-26 23:20 | 2023-05-27 01:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12184277 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1122-007 |  | FM008 |  | 2023-09-12 20:40 | 2023-09-12 21:40 | 2023-09-13 21:40 | 24 | 2023-09-12 20:45 | 2023-09-12 23:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2022-11122860 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 FILTER DIRTY |  | FM008 |  | 2022-10-24 00:42 | 2022-10-24 01:41 | 2022-10-25 01:41 | 24 | 2022-10-24 00:50 | 2022-10-24 05:45 | 295 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 95217 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2022-11134426 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 COOLING COIL DIRTY |  | FM008 |  | 2022-10-24 19:36 | 2022-10-24 20:36 | 2022-10-25 20:36 | 24 | 2022-10-24 19:42 | 2022-10-24 23:10 | 208 | 416 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 95217 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11480320 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -BG-17-03 |  | FM008 |  | 2023-02-25 19:41 | 2023-02-25 20:41 | 2023-02-26 20:41 | 24 | 2023-02-25 19:50 | 2023-02-26 00:15 | 265 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11984156 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1122-007 – BG-17-03 |  | FM008 |  | 2023-07-16 20:39 | 2023-07-16 21:39 | 2023-07-17 21:39 | 24 | 2023-07-16 20:45 | 2023-07-16 23:40 | 175 | 359 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11331448 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 COOLING COIL IS DIRTY |  | FM008 |  | 2022-12-31 20:01 | 2022-12-31 21:01 | 2023-01-01 21:01 | 24 | 2022-12-31 20:10 | 2022-12-31 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11932657 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH DAMAGED – BG-17-03 |  | FM008 |  | 2023-06-28 09:20 | 2023-06-28 10:20 | 2023-06-29 10:20 | 24 | 2023-06-28 09:30 | 2023-06-28 18:40 | 550 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 105233 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12361598 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AIR HANDLING UNIT 085 (TAG NO:AHU-A1122-007)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 017 |  | FM008 |  | 2023-11-06 16:26 | 2023-11-06 17:26 | 2023-11-07 17:26 | 24 | 2023-11-06 16:35 | 2023-11-06 18:45 | 130 | 195 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2024-12667409 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 FILTER DIRTY BG-17-03 |  | FM008 |  | 2024-02-21 13:44 | 2024-02-21 14:44 | 2024-02-22 14:44 | 24 | 2024-02-21 13:50 | 2024-02-21 16:00 | 130 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM5553 | Mohamad Haneef Abdul Hameed, Mr. Majgaonkar | N - - - |  | Voice Communication
| CM-2024-12709115 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 DUCT INSULATION DAMAGED BG-17-03 |  | FM008 |  | 2024-03-08 10:28 | 2024-03-08 11:28 | 2024-03-09 11:28 | 24 | 2024-03-08 10:35 | 2024-03-08 15:45 | 310 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12609395 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-FILTER DIRTY -BG-17-03 |  | FM008 |  | 2024-01-30 13:12 | 2024-01-30 14:12 | 2024-01-31 14:12 | 24 | 2024-01-30 13:20 | 2024-01-30 15:00 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11004822 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 – FILTER ALARM – BG-17-03 |  | FM008 |  | 2022-09-08 00:44 | 2022-09-08 01:44 | 2022-09-09 01:44 | 24 | 2022-09-08 00:50 | 2022-09-08 02:20 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOISY | VIBRATION DUE TO LOOSE PARTS OR BROKEN COMPONENTS | RECTIFIED | 94954 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11113508 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING – BG-17-03 |  | FM008 |  | 2022-10-18 22:35 | 2022-10-18 23:35 | 2022-10-19 23:35 | 24 | 2022-10-18 22:40 | 2022-10-18 23:55 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | Y - - - |  | Voice Communication
| CM-2022-10791129 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 FILTER DIRTY BG-17-03 |  | FM008 |  | 2022-07-01 18:57 | 2022-07-01 19:57 | 2022-07-02 19:57 | 24 | 2022-07-01 19:05 | 2022-07-01 21:35 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 87807 | 95217 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11382923 | ASD-COB-GFL017-AHU085 | AIR HANDLING UNIT-05 | AHU-A1122-007 FILTER DIRTY |  | FM008 |  | 2023-01-18 16:03 | 2023-01-18 17:02 | 2023-01-19 17:02 | 24 | 2023-01-18 16:10 | 2023-01-18 18:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 017 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-10655955 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AC TOO HOT - BG-16-16 |  | FM008 |  | 2022-05-15 05:38 | 2022-05-15 06:38 | 2022-05-16 06:38 | 24 | 2022-05-15 05:45 | 2022-05-15 06:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 55709 |  |  |  | MOI-ABDALA | N - - - |  | Voice Communication
| CM-2022-10855154 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AC NOT WORKING – B0-16-16 |  | FM008 |  | 2022-07-19 07:35 | 2022-07-19 08:35 | 2022-07-20 08:35 | 24 | 2022-07-19 07:40 | 2022-07-19 08:00 | 20 | 20 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17573 | 95217 |  |  |  | WAILED SAMEER | N - - - |  | Voice Communication
| CM-2022-10877455 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | NEAR BG-16-14 – LEAKAGE FROM THE AC DUCT |  | FM008 |  | 2022-07-27 17:28 | 2022-07-27 18:28 | 2022-07-28 18:28 | 24 | 2022-07-27 17:35 | 2022-07-27 18:15 | 40 | 80 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 87807 |  |  | C5289 | Faiyaz, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-11177465 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU-A1122-013-AHU CABIN LIGHT NOT WORKING |  | FM008 |  | 2022-11-10 08:34 | 2022-11-10 09:34 | 2022-11-11 09:34 | 24 | 2022-11-10 08:43 | 2022-11-10 10:11 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95217 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11935218 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AC VENT PAINT FADED - DOG ROOM B0-16-16 |  | FM008 |  | 2023-06-30 06:29 | 2023-06-30 07:29 | 2023-07-01 07:29 | 24 | 2023-06-30 06:35 | 2023-06-30 08:15 | 100 | 230 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | 90949 | Mahapa, Mr. Somnath | N - - - |  | Voice Communication
| CM-2022-11179653 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS DAMAGED - AHU-A1122-013 – BG-16-18 |  | FM008 |  | 2022-11-11 23:05 | 2022-11-12 00:05 | 2022-11-13 00:05 | 24 | 2022-11-11 23:10 | 2022-11-12 02:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11843334 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - AHU-A1122-013 - BG-16-18 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1122.GNDP6.CONB13.AHU013.SYSALM.DP3 / |  | FM008 |  | 2023-06-01 20:14 | 2023-06-01 21:14 | 2023-06-02 21:14 | 24 | 2023-06-01 20:20 | 2023-06-01 23:35 | 195 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11916772 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH DAMAGED (AHU-A1122-013) – BG 16 18 |  | FM008 |  | 2023-06-24 08:18 | 2023-06-24 09:18 | 2023-06-25 09:18 | 24 | 2023-06-24 08:27 | 2023-06-24 10:25 | 118 | 236 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12015346 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - BG-16-18 |  | FM008 |  | 2023-07-28 18:42 | 2023-07-28 19:42 | 2023-07-29 19:42 | 24 | 2023-07-28 18:50 | 2023-07-28 20:30 | 100 | 280 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12198731 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS MECHANICAL ROOM BG-16-18 - MECHANICAL ROOM BG-16-18 - CM-2023-02-0728 |  | FM008 |  | 2023-09-17 22:36 | 2023-09-17 23:36 | 2023-09-18 23:36 | 24 | 2023-09-17 22:45 | 2023-09-17 23:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM11814 | AYYAPPAN | - - -
| CM-2023-12250171 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1122-013) - BG 16 18 |  | FM008 |  | 2023-10-01 18:47 | 2023-10-01 19:47 | 2023-10-02 19:47 | 24 | 2023-10-01 18:55 | 2023-10-01 21:00 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12513622 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU-A1122-013 - DUCT INSULATION IS DAMAGED – BG-16-17 |  | FM008 |  | 2023-12-30 13:42 | 2023-12-30 14:42 | 2023-12-31 14:42 | 24 | 2023-12-30 13:50 | 2023-12-30 18:00 | 250 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-11913557 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - AHU-A1122-013 ( |  | FM008 |  | 2023-06-23 20:10 | 2023-06-23 21:10 | 2023-06-24 21:10 | 24 | 2023-06-23 20:20 | 2023-06-23 23:58 | 218 | 111 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12165577 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU-A1122-013 COOLING COIL DIRTY BG-16-18 |  | FM008 |  | 2023-09-09 00:17 | 2023-09-09 01:17 | 2023-09-10 01:17 | 24 | 2023-09-09 00:25 | 2023-09-09 04:30 | 245 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12379553 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AC VENTS GRILL PAINTING REQUIRED / FADED-BO 16 16 |  | FM008 |  | 2023-11-16 14:25 | 2023-11-16 15:25 | 2023-11-17 15:25 | 24 | 2023-11-16 14:35 | 2023-11-17 01:45 | 670 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 87807 | 87807 |  |  | FM12286 | Camelet, Ms. Milagros Revilla | N - - - |  | E-mail
| CM-2024-12845757 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1122-013 – B0-16-16 – |  | FM008 |  | 2024-04-22 00:06 | 2024-04-22 01:06 | 2024-04-23 01:06 | 24 | 2024-04-22 00:10 | 2024-04-22 02:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10100520 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | B0-16-16 - AC VENTS PAINT FADED |  | FM008 |  | 2022-02-05 14:47 | 2022-02-05 15:47 | 2022-02-06 15:47 | 24 | 2022-02-05 14:50 | 2022-02-05 16:30 | 100 | 132 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106976 | 55709 |  |  | 90949 | Mahapa, Mr. Somnath | N - - - |  | E-mail
| CM-2022-10257218 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AC VENTS PAINT FADED IN CUBICLES DOG ROOM B0 16 16 |  | FM008 |  | 2022-03-19 14:23 | 2022-03-19 15:23 | 2022-03-20 15:23 | 24 | 2022-03-19 14:30 | 2022-03-19 16:35 | 125 | 130 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | 90949 | Mahapa, Mr. Somnath | N - - - |  | E-mail
| CM-2022-10224383 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1122-013 - BG-16-18 |  | FM008 |  | 2022-03-08 01:46 | 2022-03-08 02:46 | 2022-03-09 02:46 | 24 | 2022-03-08 01:50 | 2022-03-08 02:50 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10328840 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1122-013 – BG-16-18 |  | FM008 |  | 2022-04-08 11:08 | 2022-04-08 12:08 | 2022-04-09 12:08 | 24 | 2022-04-08 11:15 | 2022-04-08 14:00 | 165 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2022-10932810 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - BG-16-18, CONCOURSE B-GROUND FLOOR AREA 016 |  | FM008 |  | 2022-08-12 19:51 | 2022-08-12 20:51 | 2022-08-13 20:51 | 24 | 2022-08-12 20:00 | 2022-08-12 23:00 | 180 | 230 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 55709 |  |  | FM0459 | MANHANDAVIDA SHAHEEL | N - - - |  | BMS
| CM-2022-11078378 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AC NOT WORKING -B0-16-16 |  | FM008 |  | 2022-10-04 15:43 | 2022-10-04 16:43 | 2022-10-05 16:43 | 24 | 2022-10-04 15:50 | 2022-10-04 16:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 87807 |  |  | MOI | MOHAMAD | N - - - |  | Voice Communication
| CM-2022-11267214 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-12 14:25 | 2022-12-12 15:25 | 2022-12-13 15:25 | 24 | 2022-12-12 14:35 | 2022-12-12 17:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 17053 |  |  | FM0473 | Balan Nair, Mr. Sreejesh | N - - - |  | Voice Communication
| CM-2022-10237428 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1122-013 |  | FM008 |  | 2022-03-11 20:39 | 2022-03-11 21:39 | 2022-03-12 21:39 | 24 | 2022-03-11 20:45 | 2022-03-11 23:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10595913 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | A/C IS TOO HOT B0-16-16 |  | FM008 |  | 2022-04-26 15:17 | 2022-04-26 16:17 | 2022-04-27 16:17 | 24 | 2022-04-26 15:25 | 2022-04-26 16:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | MOI | AAHIYA | N - - - |  | Voice Communication
| CM-2022-10611610 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU-A1122-013 DP3 FILTER ALARM BG-16-18 |  | FM008 |  | 2022-05-01 09:18 | 2022-05-01 10:18 | 2022-05-02 10:18 | 24 | 2022-05-01 09:25 | 2022-05-01 12:30 | 185 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10796304 | ASD-COB-GFL016-AHU091 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-06-30 18:57 | 2022-06-30 19:57 | 2022-07-01 19:57 | 24 | 2022-06-30 19:05 | 2022-06-30 21:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 95217 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | BMS
| CM-2022-10071261 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AC TOO COLD-QDF-EXPRESS SHOP-NEAR GATE B3 |  | FM008 |  | 2022-01-21 22:21 | 2022-01-21 23:21 | 2022-01-22 23:21 | 24 | 2022-01-21 22:30 | 2022-01-21 23:55 | 85 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95217 | 55709 |  |  | 114218 | Chebbay, Ms. Zineb | N - - - |  | Voice Communication
| CM-2022-10147211 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1122-005)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 019 |  | FM008 |  | 2022-02-17 08:27 | 2022-02-17 09:27 | 2022-02-18 09:27 | 24 | 2022-02-17 08:35 | 2022-02-17 11:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10171177 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1122-005 BG-19-04 |  | FM008 |  | 2022-02-23 21:51 | 2022-02-23 22:51 | 2022-02-24 22:51 | 24 | 2022-02-23 21:55 | 2022-02-23 23:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10613213 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | A/C IS TOO HOT AT B8 GATE |  | FM008 |  | 2022-05-03 06:56 | 2022-05-03 07:56 | 2022-05-04 07:56 | 24 | 2022-05-03 07:02 | 2022-05-03 08:00 | 58 | 58 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 98654 | Sheikh, Mr. Sohel Kalam | N - - - |  | Voice Communication
| CM-2022-11190326 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-11-13 20:31 | 2022-11-13 21:31 | 2022-11-14 21:31 | 24 | 2022-11-13 20:35 | 2022-11-13 23:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11360943 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005) – COOLING COIL DIRTY-- |  | FM008 |  | 2023-01-10 02:48 | 2023-01-10 03:48 | 2023-01-11 03:48 | 24 | 2023-01-10 02:55 | 2023-01-10 06:00 | 185 | 370 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11498209 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AIR HANDLING UNIT 083 (TAG NO:AHU-A1122-005) |  | FM008 |  | 2023-02-26 21:31 | 2023-02-26 22:31 | 2023-02-27 22:31 | 24 | 2023-02-26 21:40 | 2023-02-27 00:40 | 180 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11784211 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005 – COOLING COIL DIRTY- - |  | FM008 |  | 2023-05-10 20:18 | 2023-05-10 21:18 | 2023-05-11 21:18 | 24 | 2023-05-10 20:25 | 2023-05-10 22:45 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | COOING COIL DAMAGE | REPLACED/REPAIRED THE COOLING COIL | 94953 | 106972 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12042392 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-005 – BG-19-04 |  | FM008 |  | 2023-08-03 19:42 | 2023-08-03 20:42 | 2023-08-04 20:42 | 24 | 2023-08-03 19:50 | 2023-08-03 23:15 | 205 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106973 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12066963 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-005 – BG 19 04 |  | FM008 |  | 2023-08-12 08:56 | 2023-08-12 09:56 | 2023-08-13 09:56 | 24 | 2023-08-12 09:00 | 2023-08-12 14:00 | 300 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 132112 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12130067 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-29 14:04 | 2023-08-29 15:04 | 2023-08-30 15:04 | 24 | 2023-08-29 14:10 | 2023-08-29 17:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-12408720 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1122-005 – BG-19-04 |  | FM008 |  | 2023-11-23 20:35 | 2023-11-23 21:35 | 2023-11-24 21:35 | 24 | 2023-11-23 20:40 | 2023-11-23 23:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2022-11131291 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005 FILTER DIRTY |  | FM008 |  | 2022-10-23 20:24 | 2022-10-23 21:24 | 2022-10-24 21:24 | 24 | 2022-10-23 20:30 | 2022-10-23 22:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11134425 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005 COOLING COIL DIRTY |  | FM008 |  | 2022-10-24 19:35 | 2022-10-24 20:35 | 2022-10-25 20:35 | 24 | 2022-10-24 19:40 | 2022-10-24 22:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 95217 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11226389 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | LOOSE STRIP METAL ON THE AC VENT - NEAR B1-19-12 |  | FM008 |  | 2022-11-28 09:47 | 2022-11-28 10:47 | 2022-11-29 10:47 | 24 | 2022-11-28 09:55 | 2022-11-28 13:00 | 185 | 555 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | VIBRATION OF EQUIPMENT DUE TO LOOSE PARTS | RECTIFIED | 95216 | 17053 |  |  | R11051 | Gitau, Ms. Anne Wamucii | N - - - |  | Voice Communication
| CM-2023-11851387 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-005 - MECHANICAL ROOM BG-19-04 |  | FM008 |  | 2023-06-05 12:41 | 2023-06-05 13:41 | 2023-06-06 13:41 | 24 | 2023-06-05 12:50 | 2023-06-05 17:00 | 250 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 17573 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12033147 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005 COOLING COIL DIRTY |  | FM008 |  | 2023-07-31 02:21 | 2023-07-31 03:21 | 2023-08-01 03:21 | 24 | 2023-07-31 02:30 | 2023-07-31 05:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12363577 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY BG-19-04 |  | FM008 |  | 2023-11-07 19:34 | 2023-11-07 20:34 | 2023-11-08 20:34 | 24 | 2023-11-07 19:40 | 2023-11-07 23:10 | 210 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 17053 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2023-12428579 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005 SUPPLY MOTOR WITH ABNORMAL SOUND – BG-19-04 |  | FM008 |  | 2023-12-01 13:30 | 2023-12-01 14:30 | 2023-12-02 14:30 | 24 | 2023-12-01 13:35 | 2023-12-01 16:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 106914 | 87807 |  |  | FM0473 | Balan Nair, Mr. Sreejesh | N - - - |  | Voice Communication
| CM-2023-11823531 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-05-23 13:13 | 2023-05-23 14:13 | 2023-05-24 14:13 | 24 | 2023-05-23 13:20 | 2023-05-23 17:20 | 240 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11918293 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -:AHU-A1122-005)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 019 |  | FM008 |  | 2023-06-25 07:12 | 2023-06-25 08:12 | 2023-06-26 08:12 | 24 | 2023-06-25 07:20 | 2023-06-25 10:30 | 190 | 380 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12096969 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005-AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-08-18 12:55 | 2023-08-18 13:55 | 2023-08-19 13:55 | 24 | 2023-08-18 13:04 | 2023-08-18 15:30 | 146 | 292 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95217 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12671476 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | BROKEN AIR VENT IN BETWEEN B9 AND B10 |  | FM008 |  | 2024-02-21 17:45 | 2024-02-21 18:45 | 2024-02-22 18:45 | 24 | 2024-02-21 17:50 | 2024-02-21 18:55 | 65 | 85 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106972 | 17053 |  |  | 119195 | Adari, Ms. Demica | N - - - |  | E-mail
| CM-2023-12254561 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-005 – BG-19-03 |  | FM008 |  | 2023-10-05 14:11 | 2023-10-05 15:11 | 2023-10-06 15:11 | 24 | 2023-10-05 14:20 | 2023-10-05 17:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12339171 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AC TOO HOT - FROM GATES B2 TO B12 |  | FM008 |  | 2023-11-01 00:05 | 2023-11-01 01:05 | 2023-11-02 01:05 | 24 | 2023-11-01 00:10 | 2023-11-01 02:00 | 110 | 60 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | R13612 | Mass, Mr. Asfekhan | N - - - |  | Voice Communication
| CM-2023-12423743 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-005 – BG-19-04 |  | FM008 |  | 2023-11-30 21:12 | 2023-11-30 22:12 | 2023-12-01 22:12 | 24 | 2023-11-30 21:20 | 2023-12-01 00:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 133396 | 87807 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2023-12287827 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU COOLING COIL IS DIRTY |  | FM008 |  | 2023-10-16 13:51 | 2023-10-16 14:51 | 2023-10-17 14:51 | 24 | 2023-10-16 14:00 | 2023-10-16 17:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12428332 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | SUPPLY BLOWER BEARING ABNORMAL SOUND - BG-19-04 - AIR HANDLING UNIT 083 (TAG NO:AHU-A1122-005)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 019 |  | FM008 |  | 2023-11-30 13:57 | 2023-11-30 14:57 | 2023-12-01 14:57 | 24 | 2023-11-30 14:05 | 2023-11-30 17:30 | 205 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 119320 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2024-12692745 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | BG-19-04-COOLING COIL DIRTY-AIR HANDLING UNIT 083 (TAG NO:AHU-A1122-005) |  | FM008 |  | 2024-03-01 20:09 | 2024-03-01 21:09 | 2024-03-02 21:09 | 24 | 2024-03-01 20:15 | 2024-03-01 22:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 17053 |  |  | FM11766 | Tajeem, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10050852 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AC TOO HOT B8 GATE |  | FM008 |  | 2022-01-16 | 2022-01-16 00:30 | 2022-01-16 04:30 | 4 | 2022-01-16 00:05 | 2022-01-16 02:15 | 130 | 50 | 1 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 019 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | 68377 | Rodrigues, Mr. Calvin | N - - - |  | Voice Communication
| CM-2022-11192183 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING – BG-09-04 |  | FM008 |  | 2022-11-15 02:25 | 2022-11-15 03:25 | 2022-11-16 03:25 | 24 | 2022-11-15 02:30 | 2022-11-15 04:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11971751 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU LIGHT FLEXIBLE CONNECTOR DAMAGED - AHU-A1122-005 – BG-19-04 |  | FM008 |  | 2023-07-11 19:30 | 2023-07-11 20:30 | 2023-07-12 20:30 | 24 | 2023-07-11 19:40 | 2023-07-12 00:40 | 300 | 303 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106973 | 87807 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-10100236 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | ENTIRE AREA VERY HOT - BOARDING GATE B8, B9, B10 AREA |  | FM008 |  | 2022-02-03 17:49 | 2022-02-03 18:49 | 2022-02-04 18:49 | 24 | 2022-02-03 17:55 | 2022-02-03 18:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 17053 |  |  | 69525 | Logde, Mr. Fahd Mazhar | N - - - |  | Voice Communication
| CM-2022-10611565 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | GATE B10 AC TOO HOT |  | FM008 |  | 2022-04-30 17:18 | 2022-04-30 18:18 | 2022-05-01 18:18 | 24 | 2022-04-30 17:25 | 2022-04-30 18:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 84448 | Marata, Ms. Michelle De Los Angeles | N - - - |  | Voice Communication
| CM-2022-10654422 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | AHU-A1122-005- FILTER DIRTY BG-19-04- |  | FM008 |  | 2022-05-11 21:40 | 2022-05-11 22:40 | 2022-05-12 22:40 | 24 | 2022-05-11 21:50 | 2022-05-12 00:20 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10888759 | ASD-COB-GFL019-AHU083 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-07-31 06:58 | 2022-07-31 07:58 | 2022-08-01 07:58 | 24 | 2022-07-31 07:08 | 2022-07-31 10:50 | 222 | 272 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 019 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10775113 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | SUPPLY AIR LOW ALARM |  | FM008 |  | 2022-06-20 09:45 | 2022-06-20 10:45 | 2022-06-21 10:45 | 24 | 2022-06-20 09:50 | 2022-06-20 11:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11179161 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT ILLUMINATING |  | FM008 |  | 2022-11-09 21:42 | 2022-11-09 22:42 | 2022-11-10 22:42 | 24 | 2022-11-09 21:45 | 2022-11-09 23:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12202437 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1122-002 – BG-19-04 |  | FM008 |  | 2023-09-20 00:10 | 2023-09-20 01:10 | 2023-09-21 01:10 | 24 | 2023-09-20 00:15 | 2023-09-20 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12364085 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1122-002 – BG-19-04 |  | FM008 |  | 2023-11-08 20:10 | 2023-11-08 21:10 | 2023-11-09 21:10 | 24 | 2023-11-08 20:15 | 2023-11-08 22:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12382946 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-002 – BG-19-04 |  | FM008 |  | 2023-11-15 08:31 | 2023-11-15 09:31 | 2023-11-16 09:31 | 24 | 2023-11-15 08:40 | 2023-11-15 09:40 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10930358 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED - AHU-A1122-002 – BG-19-04 |  | FM008 |  | 2022-08-14 10:02 | 2022-08-14 11:02 | 2022-08-15 11:02 | 24 | 2022-08-14 10:10 | 2022-08-14 15:10 | 300 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106973 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-11348250 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | UNUSUAL SOUND COMING FROM RETURN BLOWER - AHU-A1122-002 – BG-19-04 |  | FM008 |  | 2023-01-05 13:31 | 2023-01-05 14:31 | 2023-01-06 14:31 | 24 | 2023-01-05 13:40 | 2023-01-05 16:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12059318 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | FILTER DIRTY BG-19-04 |  | FM008 |  | 2023-08-10 09:55 | 2023-08-10 10:55 | 2023-08-11 10:55 | 24 | 2023-08-10 10:05 | 2023-08-10 12:10 | 125 | 375 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12097427 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU-A1122-002-AHU-CABIN LAMP FAULTY |  | FM008 |  | 2023-08-16 15:53 | 2023-08-16 16:53 | 2023-08-17 16:53 | 24 | 2023-08-16 16:00 | 2023-08-16 18:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 77406 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12128180 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | RETURN FAN BELT DAMAGED - AHU-A1122-002 – BG 19 04 |  | FM008 |  | 2023-08-30 00:43 | 2023-08-30 01:43 | 2023-08-31 01:43 | 24 | 2023-08-30 00:48 | 2023-08-30 02:40 | 112 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2024-12591764 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | FILTER DIRTY - BG-19-04 |  | FM008 |  | 2024-01-23 19:16 | 2024-01-23 20:16 | 2024-01-24 20:16 | 24 | 2024-01-23 19:25 | 2024-01-23 23:50 | 265 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 95217 |  |  | FM12908 | Kumar, Mr. Abhishek | N - - - |  | Voice Communication
| CM-2024-12609627 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU-A1122-002-SUPPLY DUST INSULATION DAMAGE-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2024-01-31 13:26 | 2024-01-31 14:26 | 2024-02-01 14:26 | 24 | 2024-01-31 13:35 | 2024-01-31 15:15 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10154562 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | BELT DAMAGED - AHU-A1122-202 – BG-19-03 |  | FM008 |  | 2022-02-21 19:28 | 2022-02-21 20:28 | 2022-02-22 20:28 | 24 | 2022-02-21 19:35 | 2022-02-21 21:15 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 55709 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11194316 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2022-11-16 19:04 | 2022-11-16 20:04 | 2022-11-17 20:04 | 24 | 2022-11-16 19:14 | 2022-11-16 22:00 | 166 | 246 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11194312 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU-A1122-002 RETURN SIDE BLOWER NOISY BG-19-04 |  | FM008 |  | 2022-11-16 18:57 | 2022-11-16 19:57 | 2022-11-17 19:57 | 24 | 2022-11-16 19:05 | 2022-11-16 20:30 | 85 | 255 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10273960 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1122-002 - BG-19-04 |  | FM008 |  | 2022-03-23 19:02 | 2022-03-23 20:02 | 2022-03-24 20:02 | 24 | 2022-03-23 19:10 | 2022-03-23 21:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10573938 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -TG-19-04 |  | FM008 |  | 2022-04-19 19:09 | 2022-04-19 20:09 | 2022-04-20 20:09 | 24 | 2022-04-19 19:15 | 2022-04-19 20:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10597171 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | EXHAUST FAN NOT WORKING-BG-19-11 |  | FM008 |  | 2022-04-25 12:59 | 2022-04-25 13:59 | 2022-04-26 13:59 | 24 | 2022-04-25 13:05 | 2022-04-25 16:30 | 205 | 70 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOT WORKING | SUPPLY FAN FAULTY | REPAIRED THE FAN | 17336 | 17053 |  |  | 31762 | Briones, Mr. Chris Bulanhagui | N - - - |  | Voice Communication
| CM-2022-10885733 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | AHU-A1122-002 FILTER ALARM |  | FM008 |  | 2022-07-29 00:26 | 2022-07-29 01:26 | 2022-07-30 01:26 | 24 | 2022-07-29 00:30 | 2022-07-29 05:10 | 280 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11526788 | ASD-COB-GFL018-AHU080 | AIR HANDLING UNIT-05 | FILTER DIRTY - ( AHU-A1122-002 ) - BG 19 04 |  | FM008 |  | 2023-03-08 00:34 | 2023-03-08 01:34 | 2023-03-09 01:34 | 24 | 2023-03-08 00:40 | 2023-03-08 02:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 132112 | 95217 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10045436 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM ACCESS DOOR |  | FM008 |  | 2022-01-13 21:27 | 2022-01-13 22:27 | 2022-01-14 22:27 | 24 | 2022-01-13 21:30 | 2022-01-13 23:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | BMS
| CM-2022-10095793 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006 – COOLING COIL DIRTY-- |  | FM008 |  | 2022-01-30 14:50 | 2022-01-30 15:50 | 2022-01-31 15:50 | 24 | 2022-01-30 15:00 | 2022-01-30 17:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10627300 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AIR DUCTS DAMAGED -TERMIC TAPE TO BE PROPERLY REPLACED--BG-18-07)- |  | FM008 |  | 2022-05-08 15:04 | 2022-05-08 16:04 | 2022-05-09 16:04 | 24 | 2022-05-08 15:15 | 2022-05-08 21:00 | 345 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-11159074 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AHU-A1122-006)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2022-11-05 08:50 | 2022-11-05 09:50 | 2022-11-06 09:50 | 24 | 2022-11-05 09:00 | 2022-11-05 12:30 | 210 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11430416 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED – NEAR BG-17-03 |  | FM008 |  | 2023-02-08 12:33 | 2023-02-08 13:33 | 2023-02-09 13:33 | 24 | 2023-02-08 12:40 | 2023-02-08 14:40 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11649653 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1122-006 - BG-19-04 |  | FM008 |  | 2023-04-11 11:56 | 2023-04-11 12:56 | 2023-04-12 12:56 | 24 | 2023-04-11 12:05 | 2023-04-11 15:30 | 205 | 545 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 94954 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11879501 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | NEAR BG-18-07 – AHU-A1122-006 – RETUNE DUCT INSULATION DAMAGED |  | FM008 |  | 2023-06-13 07:26 | 2023-06-13 08:26 | 2023-06-14 08:26 | 24 | 2023-06-13 07:30 | 2023-06-13 09:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12151978 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY, AHUA-A1126-006, BG-19-04 |  | FM008 |  | 2023-09-04 20:05 | 2023-09-04 21:05 | 2023-09-05 21:05 | 24 | 2023-09-04 20:10 | 2023-09-04 22:30 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 87807 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12364084 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1122-006 – BG-19-04 |  | FM008 |  | 2023-11-08 20:09 | 2023-11-08 21:09 | 2023-11-09 21:09 | 24 | 2023-11-08 20:15 | 2023-11-08 22:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12493151 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE - AIR HANDLING UNIT 084 (TAG NO:AHU-A1122-006)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2023-12-23 11:33 | 2023-12-23 12:33 | 2023-12-24 12:33 | 24 | 2023-12-23 11:40 | 2023-12-23 13:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12689437 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006 FILTER DIRTY – BG-19-04 |  | FM008 |  | 2024-02-27 07:23 | 2024-02-27 08:23 | 2024-02-28 08:23 | 24 | 2024-02-27 07:30 | 2024-02-27 09:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM4703 | Joseph, Mr. Mathew | N - - - |  | Voice Communication
| CM-2022-11165859 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | RETUNE MOTOR COOLING FAN DAMAGED - AHU-A1122-006 – BG-19-03 |  | FM008 |  | 2022-11-08 13:29 | 2022-11-08 14:29 | 2022-11-09 14:29 | 24 | 2022-11-08 13:38 | 2022-11-08 18:50 | 312 | 167 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17573 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11785251 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | CLOSE TO WOMEN WASHROOM BO 19 07 HVAC AIR DUCT - EXTERNAL ISOLATION - ALUMINUM DAMAGED (PERMANENT SOLUTION TO BE PROVIDED PROBLEM ALREADY RAISED LAST MONTH APR/23) |  | FM008 |  | 2023-05-11 14:42 | 2023-05-11 15:42 | 2023-05-12 15:42 | 24 | 2023-05-11 14:50 | 2023-05-11 18:15 | 205 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2023-12232708 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT DUCT INSTALLATION DAMAGE - AIR HANDLING UNIT 084 (TAG NO:AHU-A1122-006)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2023-09-29 20:30 | 2023-09-29 21:30 | 2023-09-30 21:30 | 24 | 2023-09-29 20:35 | 2023-09-29 23:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10924487 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS -AIRSIDE-CONCOURSE B-FIRST FLOOR AREA 019 |  | FM008 |  | 2022-08-08 16:36 | 2022-08-08 17:36 | 2022-08-09 17:36 | 24 | 2022-08-08 16:45 | 2022-08-08 17:40 | 55 | 40 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11128280 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006 FILTER DIRTY BG-19-04 |  | FM008 |  | 2022-10-24 08:08 | 2022-10-24 09:08 | 2022-10-25 09:08 | 24 | 2022-10-24 08:12 | 2022-10-24 10:20 | 128 | 226 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 89127 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11822888 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006 FILTER DIRTY BG-19-04 |  | FM008 |  | 2023-05-24 12:47 | 2023-05-24 13:47 | 2023-05-25 13:47 | 24 | 2023-05-24 12:55 | 2023-05-24 17:50 | 295 | 485 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 87807 | 17053 |  |  | FM5553 | Mohamad Haneef Abdul Hameed, Mr. Majgaonkar | N - - - |  | Voice Communication
| CM-2023-11879283 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1122-006 -NEAR BG-18-07 - |  | FM008 |  | 2023-06-12 09:05 | 2023-06-12 10:05 | 2023-06-13 10:05 | 24 | 2023-06-12 09:10 | 2023-06-12 12:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12095882 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006 FILTER DIRTY BG-19-03 |  | FM008 |  | 2023-08-16 20:26 | 2023-08-16 21:26 | 2023-08-17 21:26 | 24 | 2023-08-16 20:35 | 2023-08-16 23:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2024-12553289 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006 – DUCT INSULATION IS DAMAGED – BG-19-04 |  | FM008 |  | 2024-01-08 22:03 | 2024-01-08 23:03 | 2024-01-09 23:03 | 24 | 2024-01-08 22:10 | 2024-01-08 23:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | E-mail
| CM-2022-10328352 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AIR DUCTS DAMAGED 03 - BG-18-07 |  | FM008 |  | 2022-04-06 15:19 | 2022-04-06 16:19 | 2022-04-07 16:19 | 24 | 2022-04-06 15:29 | 2022-04-06 22:15 | 406 | 246 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-10730715 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AIR DUCTS DAMAGED -TERMIC TAPE TO BE PROPERLY REPLACED--BG-18-07)- |  | FM008 |  | 2022-06-07 22:02 | 2022-06-07 23:02 | 2022-06-08 23:02 | 24 | 2022-06-07 22:10 | 2022-06-08 05:15 | 425 | 90 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2023-11346105 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | RETUNE DUCT ACCESS DOOR LEAKAGE -AHU-A1122-006 – BG-17-03 |  | FM008 |  | 2023-01-03 16:03 | 2023-01-03 17:03 | 2023-01-04 17:03 | 24 | 2023-01-03 16:10 | 2023-01-03 18:30 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | E-mail
| CM-2022-10154593 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU-A1122-006-BG-19-04-AHU FILTER DIRTY |  | FM008 |  | 2022-02-21 21:45 | 2022-02-21 22:45 | 2022-02-22 22:45 | 24 | 2022-02-21 21:50 | 2022-02-22 00:20 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10231355 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-03-10 23:53 | 2022-03-11 00:53 | 2022-03-12 00:53 | 24 | 2022-03-11 | 2022-03-11 01:45 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | BMS
| CM-2022-10670447 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – BG-19-04 |  | FM008 |  | 2022-05-16 10:40 | 2022-05-16 11:40 | 2022-05-17 11:40 | 24 | 2022-05-16 10:45 | 2022-05-16 13:00 | 135 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2022-10888760 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | AHU FILTER ALARM |  | FM008 |  | 2022-07-31 06:59 | 2022-07-31 07:59 | 2022-08-01 07:59 | 24 | 2022-07-31 07:09 | 2022-07-31 12:24 | 315 | 272 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11637678 | ASD-COB-GFL018-AHU084 | AIR HANDLING UNIT-05 | HVAC AIR DUCT EXTERNAL ISOLATION ALUMINUM DAMAGED - CLOSE TO WOMEN WASHROOM B0-19-07 |  | FM008 |  | 2023-04-09 11:36 | 2023-04-09 12:36 | 2023-04-10 12:36 | 24 | 2023-04-09 11:45 | 2023-04-09 15:45 | 240 | 840 | 5 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17573 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-11135404 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY,-CONCOURSE B-GROUND FLOOR AREA 018. |  | FM008 |  | 2022-10-25 19:50 | 2022-10-25 20:50 | 2022-10-26 20:50 | 24 | 2022-10-25 19:55 | 2022-10-25 22:50 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11825690 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU-A1122-010- AC-BELT DAMAGE -CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2023-05-27 08:00 | 2023-05-27 09:00 | 2023-05-28 09:00 | 24 | 2023-05-27 08:05 | 2023-05-27 11:00 | 175 | 700 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11908489 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1122-010 – NEAR BG-18-07 |  | FM008 |  | 2023-06-20 07:55 | 2023-06-20 08:55 | 2023-06-21 08:55 | 24 | 2023-06-20 08:05 | 2023-06-20 10:30 | 145 | 725 | 5 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 17573 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | BMS
| CM-2023-12224040 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-25 20:35 | 2023-09-25 21:35 | 2023-09-26 21:35 | 24 | 2023-09-25 20:40 | 2023-09-25 23:30 | 170 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2023-11888411 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-06-18 07:40 | 2023-06-18 08:40 | 2023-06-19 08:40 | 24 | 2023-06-18 07:45 | 2023-06-18 10:00 | 135 | 810 | 6 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12067838 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-12 16:10 | 2023-08-12 17:10 | 2023-08-13 17:10 | 24 | 2023-08-12 16:15 | 2023-08-12 18:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12231052 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT ILLUMINATING - AHU-A1122-010 - BG-19-04 – MECHANICAL ROOM |  | FM008 |  | 2023-09-27 01:16 | 2023-09-27 02:16 | 2023-09-28 02:16 | 24 | 2023-09-27 01:25 | 2023-09-27 05:30 | 245 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-11128281 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU-A1122-010 FILTER DIRTY BG-19-04 |  | FM008 |  | 2022-10-24 08:09 | 2022-10-24 09:09 | 2022-10-25 09:09 | 24 | 2022-10-24 08:13 | 2022-10-24 10:30 | 137 | 243 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11351110 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1122-010- BG-19-04 |  | FM008 |  | 2023-01-06 00:45 | 2023-01-06 01:45 | 2023-01-07 01:45 | 24 | 2023-01-06 00:55 | 2023-01-06 03:55 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11822889 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU-A1122-010 FILTER DIRTY BG-19-04 |  | FM008 |  | 2023-05-24 12:49 | 2023-05-24 13:49 | 2023-05-25 13:49 | 24 | 2023-05-24 12:55 | 2023-05-24 15:45 | 170 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM5553 | MOHAMAD HANEEF ABDUL HAMEED MAJGAONKAR, | N - - - |  | Voice Communication
| CM-2023-12165943 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU-A1122-010 COOLING COIL DIRTY |  | FM008 |  | 2023-09-09 20:24 | 2023-09-09 21:24 | 2023-09-10 21:24 | 24 | 2023-09-09 20:30 | 2023-09-09 23:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12685702 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU-FILETR DIRTY (CONCOURSE B-GROUND FLOOR AREA 018) |  | FM008 |  | 2024-02-26 23:04 | 2024-02-27 00:04 | 2024-02-28 00:04 | 24 | 2024-02-26 23:10 | 2024-02-27 00:30 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10106072 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU088 DUCT INSULATION DAMAGED – BG-19-04 |  | FM008 |  | 2022-02-05 16:55 | 2022-02-05 17:55 | 2022-02-06 17:55 | 24 | 2022-02-05 17:05 | 2022-02-05 18:30 | 85 | 255 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106976 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10325119 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | AHU-A1122-010- RELEASE FAN BLOWER BELT DAMAGED |  | FM008 |  | 2022-04-04 22:56 | 2022-04-04 23:56 | 2022-04-05 23:56 | 24 | 2022-04-04 23:05 | 2022-04-05 00:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 87807 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10791926 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | FILTER IS DIRTY AHU-A1122-010 |  | FM008 |  | 2022-06-29 19:04 | 2022-06-29 20:04 | 2022-06-30 20:04 | 24 | 2022-06-29 19:10 | 2022-06-29 21:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 95217 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | BMS
| CM-2023-11342094 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR LEAKAGE-BG-17-03 |  | FM008 |  | 2023-01-03 15:53 | 2023-01-03 16:53 | 2023-01-04 16:53 | 24 | 2023-01-03 16:00 | 2023-01-03 18:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 77406 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-11445776 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | SUPPLY INSULATION DUCT DAMAGED |  | FM008 |  | 2023-02-11 13:24 | 2023-02-11 14:24 | 2023-02-12 14:24 | 24 | 2023-02-11 13:30 | 2023-02-11 17:00 | 210 | 840 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11661081 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-04-14 21:08 | 2023-04-14 22:08 | 2023-04-15 22:08 | 24 | 2023-04-14 21:15 | 2023-04-14 23:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10120801 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1122-010 BG-19-04 |  | FM008 |  | 2022-02-08 13:58 | 2022-02-08 14:58 | 2022-02-09 14:58 | 24 | 2022-02-08 14:05 | 2022-02-08 16:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 85125 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10231356 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-03-10 23:55 | 2022-03-11 00:55 | 2022-03-12 00:55 | 24 | 2022-03-11 | 2022-03-11 01:45 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11430215 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED -BG-17-03 |  | FM008 |  | 2023-02-07 12:27 | 2023-02-07 13:27 | 2023-02-08 13:27 | 24 | 2023-02-07 12:35 | 2023-02-07 15:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11615910 | ASD-COB-GFL018-AHU088 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-010 - BG-19-04 |  | FM008 |  | 2023-04-04 00:05 | 2023-04-04 01:05 | 2023-04-05 01:05 | 24 | 2023-04-04 00:10 | 2023-04-04 02:10 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10147212 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM ACCESS DOOR -AHU-A1122-012)-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2022-02-17 08:29 | 2022-02-17 09:29 | 2022-02-18 09:29 | 24 | 2022-02-17 08:35 | 2022-02-17 11:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10325874 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 – FILTER DIRTY- |  | FM008 |  | 2022-04-05 07:15 | 2022-04-05 08:15 | 2022-04-06 08:15 | 24 | 2022-04-05 07:20 | 2022-04-05 10:00 | 160 | 320 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94953 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11041068 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU BELT DAMAGED -TG-19-04 |  | FM008 |  | 2022-09-23 16:53 | 2022-09-23 17:53 | 2022-09-24 17:53 | 24 | 2022-09-23 17:00 | 2022-09-23 18:00 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12043521 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-012 – BG-19-04 |  | FM008 |  | 2023-08-05 00:20 | 2023-08-05 01:20 | 2023-08-06 01:20 | 24 | 2023-08-05 00:30 | 2023-08-05 03:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12134002 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-012 -BG-19-04 |  | FM008 |  | 2023-08-30 14:06 | 2023-08-30 15:06 | 2023-08-31 15:06 | 24 | 2023-08-30 14:10 | 2023-08-30 17:00 | 170 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 133396 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12345204 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - BG-18A-02 |  | FM008 |  | 2023-11-01 23:57 | 2023-11-02 00:57 | 2023-11-03 00:57 | 24 | 2023-11-02 00:05 | 2023-11-02 03:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 87807 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2023-12366281 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-012 – BG-19-04 |  | FM008 |  | 2023-11-10 19:43 | 2023-11-10 20:43 | 2023-11-11 20:43 | 24 | 2023-11-10 19:50 | 2023-11-10 23:00 | 190 | 380 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12488889 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 COOLING COIL DIRTY |  | FM008 |  | 2023-12-21 12:00 | 2023-12-21 13:00 | 2023-12-22 13:00 | 24 | 2023-12-21 12:10 | 2023-12-21 15:00 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11254967 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AHU-A1122-012 – BG-19-04 |  | FM008 |  | 2022-12-10 12:17 | 2022-12-10 13:17 | 2022-12-11 13:17 | 24 | 2022-12-10 12:25 | 2022-12-10 16:25 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12067839 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-12 16:11 | 2023-08-12 17:11 | 2023-08-13 17:11 | 24 | 2023-08-12 16:20 | 2023-08-12 18:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12111697 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | FILTER DIRTY – AHU-A1122-012 – BG-19-04 |  | FM008 |  | 2023-08-22 13:50 | 2023-08-22 14:50 | 2023-08-23 14:50 | 24 | 2023-08-22 13:55 | 2023-08-22 16:00 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM0081 | Rayachur, Mr. Srinivas | N - - - |  | Voice Communication
| CM-2023-12229069 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT IS FAULTY |  | FM008 |  | 2023-09-27 08:39 | 2023-09-27 09:39 | 2023-09-28 09:39 | 24 | 2023-09-27 08:42 | 2023-09-27 18:06 | 564 | 357 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12382626 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY - AHU-A1122-012 - MECHANICAL ROOM BG-19-04 |  | FM008 |  | 2023-11-14 22:31 | 2023-11-14 23:31 | 2023-11-15 23:31 | 24 | 2023-11-14 22:40 | 2023-11-15 00:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11128282 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 FILTER DIRTY BG-19-04 |  | FM008 |  | 2022-10-24 08:09 | 2022-10-24 09:09 | 2022-10-25 09:09 | 24 | 2022-10-24 08:15 | 2022-10-24 12:20 | 245 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11163813 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 – RETURN DUCT CANVAS DAMAGED- |  | FM008 |  | 2022-11-06 13:42 | 2022-11-06 14:42 | 2022-11-07 14:42 | 24 | 2022-11-06 13:50 | 2022-11-06 15:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11189088 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-11-14 21:03 | 2022-11-14 22:03 | 2022-11-15 22:03 | 24 | 2022-11-14 21:10 | 2022-11-14 23:30 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11823532 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-05-23 13:14 | 2023-05-23 14:14 | 2023-05-24 14:14 | 24 | 2023-05-23 13:20 | 2023-05-23 17:20 | 240 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11818980 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM SUPPLY SIDE -AHU-A1122-012)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2023-05-24 15:39 | 2023-05-24 16:39 | 2023-05-25 16:39 | 24 | 2023-05-24 15:45 | 2023-05-24 17:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12406264 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-012 – BG-19-04 |  | FM008 |  | 2023-11-21 20:40 | 2023-11-21 21:40 | 2023-11-22 21:40 | 24 | 2023-11-21 20:45 | 2023-11-21 23:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 87807 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2024-12745610 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 BG-19-04 FILTER DIRTY |  | FM008 |  | 2024-03-20 03:52 | 2024-03-20 04:52 | 2024-03-21 04:52 | 24 | 2024-03-20 04:00 | 2024-03-20 06:50 | 170 | 225 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-10791927 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-06-29 19:06 | 2022-06-29 20:06 | 2022-06-30 20:06 | 24 | 2022-06-29 19:15 | 2022-06-29 23:15 | 240 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 95217 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-10958618 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | FAD FEEDBACK MISMATCHED |  | FM008 |  | 2022-08-23 08:31 | 2022-08-23 09:31 | 2022-08-24 09:31 | 24 | 2022-08-23 08:40 | 2022-08-23 10:08 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 68060 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11340965 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 COOLING COIL DIRTY BG-19-07 |  | FM008 |  | 2023-01-04 20:27 | 2023-01-04 21:27 | 2023-01-05 21:27 | 24 | 2023-01-04 20:35 | 2023-01-04 23:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11406262 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 COOLING COIL DIRTY BG-19-04 |  | FM008 |  | 2023-01-27 20:34 | 2023-01-27 21:34 | 2023-01-28 21:34 | 24 | 2023-01-27 20:40 | 2023-01-27 22:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10048699 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-01-14 19:04 | 2022-01-14 20:04 | 2022-01-15 20:04 | 24 | 2022-01-14 19:10 | 2022-01-14 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | BMS
| CM-2023-11648426 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012-COOLING COIL DIRTY-CONCOURSE B-GROUND FLOOR AREA 018 |  | FM008 |  | 2023-04-10 13:31 | 2023-04-10 14:31 | 2023-04-11 14:31 | 24 | 2023-04-10 13:35 | 2023-04-10 18:45 | 310 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 94954 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11918014 | ASD-COB-GFL018-AHU090 | AIR HANDLING UNIT-05 | AHU-A1122-012 – COOLING COIL DIRTY-- |  | FM008 |  | 2023-06-25 12:56 | 2023-06-25 13:56 | 2023-06-26 13:56 | 24 | 2023-06-25 13:00 | 2023-06-25 17:30 | 270 | 425 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 018 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10116652 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AIR DUCTS DAMAGED - TO BE RECTIFIED - CONCOURSE B- GROUND FLOOR (NEAR B11 - BUS ENTRANCE - GROUND FLOOR) |  | FM008 |  | 2022-02-06 15:25 | 2022-02-06 16:25 | 2022-02-07 16:25 | 24 | 2022-02-06 15:30 | 2022-02-06 18:50 | 200 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 85125 | 55709 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-10157812 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU081 LIGHTING FLEXIBLE CONNECTOR DAMAGED – BG-20-09 |  | FM008 |  | 2022-02-22 10:46 | 2022-02-22 11:46 | 2022-02-23 11:46 | 24 | 2022-02-22 10:55 | 2022-02-22 12:24 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106976 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10669497 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003- DP3FILTER ALARM BG-20-09 |  | FM008 |  | 2022-05-16 14:22 | 2022-05-16 15:22 | 2022-05-17 15:22 | 24 | 2022-05-16 14:30 | 2022-05-16 16:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10694851 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY – BG-20-09 – AHU-A1122-003 |  | FM008 |  | 2022-05-27 20:52 | 2022-05-27 21:52 | 2022-05-28 21:52 | 24 | 2022-05-27 21:00 | 2022-05-27 23:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM0422 | Thekkekara Jose, Mr. Shoby | N - - - |  | Voice Communication
| CM-2022-10734781 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 DP1-B FILTER ALARM BG-20-09 |  | FM008 |  | 2022-06-10 21:26 | 2022-06-10 22:26 | 2022-06-11 22:26 | 24 | 2022-06-10 21:30 | 2022-06-10 23:10 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11237365 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY - BG-20-09 |  | FM008 |  | 2022-12-02 20:16 | 2022-12-02 21:16 | 2022-12-03 21:16 | 24 | 2022-12-02 20:25 | 2022-12-02 23:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-11257006 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY |  | FM008 |  | 2022-12-10 21:10 | 2022-12-10 22:10 | 2022-12-11 22:10 | 24 | 2022-12-10 21:20 | 2022-12-10 23:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11763628 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-05 00:11 | 2023-05-05 01:11 | 2023-05-06 01:11 | 24 | 2023-05-05 00:15 | 2023-05-05 01:15 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-11781852 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOILING COIL DIRTY , AHU-A1122-003, BG-20-09 |  | FM008 |  | 2023-05-08 20:29 | 2023-05-08 21:29 | 2023-05-09 21:29 | 24 | 2023-05-08 20:35 | 2023-05-08 22:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-11850210 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-06-04 19:04 | 2023-06-04 20:04 | 2023-06-05 20:04 | 24 | 2023-06-04 19:10 | 2023-06-04 22:10 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 89127 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11913739 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | DARINE LINE DAMAGED –CRAC-A1122-003 – BG 19 01 |  | FM008 |  | 2023-06-24 16:11 | 2023-06-24 17:11 | 2023-06-25 17:11 | 24 | 2023-06-24 16:20 | 2023-06-24 18:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 132112 | 17053 |  |  | FM0487 | Faqruddin, Mr. Abdul | N - - - |  | Voice Communication
| CM-2023-12059382 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | DRAIN LINE INSULATION DAMAGED - AHU-A1122-003 – BG-20-09 |  | FM008 |  | 2023-08-10 13:26 | 2023-08-10 14:26 | 2023-08-11 14:26 | 24 | 2023-08-10 13:35 | 2023-08-10 15:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2022-11310914 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - (AHU-1122003) - AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 020 |  | FM008 |  | 2022-12-25 20:28 | 2022-12-25 21:28 | 2022-12-26 21:28 | 24 | 2022-12-25 20:35 | 2022-12-25 23:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 132112 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11629832 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOL COIL DIRTY – BG-19-09 |  | FM008 |  | 2023-04-07 19:05 | 2023-04-07 20:05 | 2023-04-08 20:05 | 24 | 2023-04-07 19:15 | 2023-04-07 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11929972 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 COOLING COIL DIRTY BG-20-09 |  | FM008 |  | 2023-06-26 13:08 | 2023-06-26 14:08 | 2023-06-27 14:08 | 24 | 2023-06-26 13:15 | 2023-06-26 17:10 | 235 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12083521 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-(A1122-003) CABIN LAMP FAULTY -BG-20-09 |  | FM008 |  | 2023-08-14 08:53 | 2023-08-14 09:53 | 2023-08-15 09:53 | 24 | 2023-08-14 09:00 | 2023-08-14 11:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 77406 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-11656515 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 – COOLING COIL DIRTY – BG-20-09 |  | FM008 |  | 2023-04-12 19:27 | 2023-04-12 20:27 | 2023-04-13 20:27 | 24 | 2023-04-12 19:30 | 2023-04-12 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17154 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11932203 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-06-26 13:15 | 2023-06-26 14:15 | 2023-06-27 14:15 | 24 | 2023-06-26 13:20 | 2023-06-26 17:10 | 230 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12128239 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1122-003 |  | FM008 |  | 2023-08-30 07:36 | 2023-08-30 08:36 | 2023-08-31 08:36 | 24 | 2023-08-30 07:45 | 2023-08-30 11:00 | 195 | 390 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2024-12592591 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM THE AHU - AHU-A1122-003 – BG-20-03 |  | FM008 |  | 2024-01-26 13:14 | 2024-01-26 14:14 | 2024-01-27 14:14 | 24 | 2024-01-26 13:20 | 2024-01-26 16:15 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 106914 | 17053 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2023-12382595 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - BG-20-09A |  | FM008 |  | 2023-11-14 20:04 | 2023-11-14 21:04 | 2023-11-15 21:04 | 24 | 2023-11-14 20:15 | 2023-11-14 22:10 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM12539 | SOWMESH JAYARAJ, | N - - - |  | Voice Communication
| CM-2022-10044456 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY TAG NO:AHU-A1122-003) |  | FM008 |  | 2022-01-12 20:32 | 2022-01-12 21:32 | 2022-01-13 21:32 | 24 | 2022-01-12 20:40 | 2022-01-12 23:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10044457 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-01-12 20:33 | 2022-01-12 21:33 | 2022-01-13 21:33 | 24 | 2022-01-12 20:40 | 2022-01-12 23:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11114063 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 FILTER DIRTY BG-19-09 |  | FM008 |  | 2022-10-22 07:08 | 2022-10-22 08:08 | 2022-10-23 08:08 | 24 | 2022-10-22 07:15 | 2022-10-22 12:00 | 285 | 195 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11177608 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 -AIR LEAKAGE FROM SUPPLY SIDE |  | FM008 |  | 2022-11-11 00:50 | 2022-11-11 01:50 | 2022-11-12 01:50 | 24 | 2022-11-11 01:00 | 2022-11-11 03:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11179901 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-11-12 19:33 | 2022-11-12 20:33 | 2022-11-13 20:33 | 24 | 2022-11-12 19:40 | 2022-11-12 21:30 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11270804 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-12-14 11:36 | 2022-12-14 12:36 | 2022-12-15 12:36 | 24 | 2022-12-14 11:45 | 2022-12-14 16:00 | 255 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11296049 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 081 -COOL COIL DIRTY -TG-20-09 |  | FM008 |  | 2022-12-21 20:09 | 2022-12-21 21:09 | 2022-12-22 21:09 | 24 | 2022-12-21 20:15 | 2022-12-21 22:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10209529 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | FILTER DIRTY- AHU-A1122-003- BG-20-09 |  | FM008 |  | 2022-03-03 21:23 | 2022-03-03 22:23 | 2022-03-04 22:23 | 24 | 2022-03-03 21:30 | 2022-03-03 23:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-10364460 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM -BG-20-09 |  | FM008 |  | 2022-04-16 07:13 | 2022-04-16 08:13 | 2022-04-17 08:13 | 24 | 2022-04-16 07:20 | 2022-04-16 09:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10886663 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 FILTER ALARM GROUND FLOOR AREA 020 |  | FM008 |  | 2022-07-29 00:29 | 2022-07-29 01:29 | 2022-07-30 01:29 | 24 | 2022-07-29 00:35 | 2022-07-29 03:35 | 180 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11479942 | ASD-COB-GFL020-AHU081 | AIR HANDLING UNIT-05 | AHU-A1122-003 - COOLING COIL DIRTY - TG-20-09 |  | FM008 |  | 2023-02-23 19:19 | 2023-02-23 20:18 | 2023-02-24 20:18 | 24 | 2023-02-23 19:25 | 2023-02-23 23:00 | 215 | 645 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10109551 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-004 – BG-20-09 |  | FM008 |  | 2022-02-04 14:01 | 2022-02-04 15:01 | 2022-02-05 15:01 | 24 | 2022-02-04 14:05 | 2022-02-04 17:00 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10217569 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY BG-20-09 |  | FM008 |  | 2022-03-06 10:08 | 2022-03-06 11:08 | 2022-03-07 11:08 | 24 | 2022-03-06 10:15 | 2022-03-06 14:00 | 225 | 550 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5553 | MOHAMAD HANEEF ABDUL HAMEED MAJGAONKAR, | N - - - |  | Voice Communication
| CM-2022-10368501 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-04-16 09:29 | 2022-04-16 10:29 | 2022-04-17 10:29 | 24 | 2022-04-16 09:35 | 2022-04-16 13:10 | 215 | 370 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2022-10730304 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP1-B FINAL FILTER STATUS BG-20-09 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1122.GNDP3.CONB04.AHU004.SYSALM.DP1B / |  | FM008 |  | 2022-06-09 12:00 | 2022-06-09 13:00 | 2022-06-10 13:00 | 24 | 2022-06-09 12:05 | 2022-06-09 14:00 | 115 | 345 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - |  | E-mail
| CM-2022-11095592 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1122-004 – BG-20-09 |  | FM008 |  | 2022-10-10 07:45 | 2022-10-10 08:45 | 2022-10-11 08:45 | 24 | 2022-10-10 07:50 | 2022-10-10 09:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106973 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11947667 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP1-B FINAL FILTER STATUS BG-20-09 |  | FM008 |  | 2023-07-05 13:23 | 2023-07-05 14:23 | 2023-07-06 14:23 | 24 | 2023-07-05 13:30 | 2023-07-05 14:40 | 70 | 140 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12041458 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-004 – BG-20-09 |  | FM008 |  | 2023-08-02 20:03 | 2023-08-02 21:03 | 2023-08-03 21:03 | 24 | 2023-08-02 20:10 | 2023-08-02 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 133396 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | BMS
| CM-2023-12116867 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – (AHU-A1122-004) – BG 20 09 |  | FM008 |  | 2023-08-27 07:32 | 2023-08-27 08:32 | 2023-08-28 08:32 | 24 | 2023-08-27 07:40 | 2023-08-27 11:00 | 200 | 400 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 132112 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2024-12666798 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | SUPPLY MOTOR NOISY -BG-20-09 |  | FM008 |  | 2024-02-19 08:11 | 2024-02-19 09:11 | 2024-02-20 09:11 | 24 | 2024-02-19 08:15 | 2024-02-19 11:30 | 195 | 780 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11176879 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 082,-COOLING COIL DIRTY-CONCOURSE B-GROUND FLOOR AREA 020.BG-20-09. |  | FM008 |  | 2022-11-11 20:04 | 2022-11-11 21:04 | 2022-11-12 21:04 | 24 | 2022-11-11 20:10 | 2022-11-11 22:40 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11482673 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP1-B FINAL FILTER STATUS - AHU-A1122-004 - BG-20-09 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1122.GNDP3.CONB04.AHU004.SYSALM.DP1B / |  | FM008 |  | 2023-02-23 10:18 | 2023-02-23 11:18 | 2023-02-24 11:18 | 24 | 2023-02-23 10:25 | 2023-02-23 15:10 | 285 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12015084 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-07-27 20:11 | 2023-07-27 21:11 | 2023-07-28 21:11 | 24 | 2023-07-27 20:20 | 2023-07-27 22:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12041451 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH DAMAGED – BG-20-09,MEC ROOM |  | FM008 |  | 2023-08-02 19:20 | 2023-08-02 20:20 | 2023-08-03 20:20 | 24 | 2023-08-02 19:30 | 2023-08-03 00:30 | 300 | 338 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 105233 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-12130015 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DRAIN LINE INSULATION DAMAGED |  | FM008 |  | 2023-08-29 07:32 | 2023-08-29 08:32 | 2023-08-30 08:32 | 24 | 2023-08-29 07:40 | 2023-08-29 10:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM11766 | Tajeem, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12366821 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | RELEASE SIDE ABNORMAL SOUND AHU-A1122-004 |  | FM008 |  | 2023-11-10 07:56 | 2023-11-10 08:56 | 2023-11-11 08:56 | 24 | 2023-11-10 08:05 | 2023-11-10 11:35 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106972 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2024-12833657 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | FRESH AIR DUCT INSULATION DAMAGED |  | FM008 |  | 2024-04-21 13:32 | 2024-04-21 14:32 | 2024-04-22 14:32 | 24 | 2024-04-21 13:40 | 2024-04-21 15:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2022-11160522 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DRAIN LINE INSULATION DAMAGED |  | FM008 |  | 2022-11-05 13:35 | 2022-11-05 14:35 | 2022-11-06 14:35 | 24 | 2022-11-05 13:40 | 2022-11-05 15:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-11217358 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | RELIEF VFD LOAN CARD LOG DAMAGED - MEC ROOM BG-20-09 |  | FM008 |  | 2022-11-24 10:01 | 2022-11-24 11:01 | 2022-11-25 11:01 | 24 | 2022-11-24 10:06 | 2022-11-24 11:30 | 84 | 168 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 105233 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11231296 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU-A1122-004-COOLING COIL DIRTY-BG-20-09 |  | FM008 |  | 2022-11-28 20:24 | 2022-11-28 21:24 | 2022-11-29 21:24 | 24 | 2022-11-28 20:30 | 2022-11-29 00:30 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11253485 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | FILTER DIRTY -BG-20-09 |  | FM008 |  | 2022-12-07 19:46 | 2022-12-07 20:46 | 2022-12-08 20:46 | 24 | 2022-12-07 19:55 | 2022-12-07 23:30 | 215 | 765 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-11256605 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1122-004)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 020 |  | FM008 |  | 2022-12-09 02:07 | 2022-12-09 03:07 | 2022-12-10 03:07 | 24 | 2022-12-09 02:15 | 2022-12-09 05:30 | 195 | 710 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11355436 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | FILTER DIRTY – BG-20-09 |  | FM008 |  | 2023-01-08 11:18 | 2023-01-08 12:18 | 2023-01-09 12:18 | 24 | 2023-01-08 11:25 | 2023-01-08 13:25 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11568681 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – BG-19-04 |  | FM008 |  | 2023-03-17 14:16 | 2023-03-17 15:16 | 2023-03-18 15:16 | 24 | 2023-03-17 14:20 | 2023-03-17 17:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 95217 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11764925 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-05 01:17 | 2023-05-05 02:17 | 2023-05-06 02:17 | 24 | 2023-05-05 01:25 | 2023-05-05 03:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-11800053 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP1-B FINAL FILTER STATUS AHU-A1122-004 BG-20-09 |  | FM008 |  | 2023-05-17 09:41 | 2023-05-17 10:41 | 2023-05-18 10:41 | 24 | 2023-05-17 09:45 | 2023-05-17 18:45 | 540 | 230 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12217889 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-09-25 03:23 | 2023-09-25 04:23 | 2023-09-26 04:23 | 24 | 2023-09-25 03:30 | 2023-09-25 06:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12684454 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | FILTER DIRTY -BG-20-09 |  | FM008 |  | 2024-02-26 07:57 | 2024-02-26 08:58 | 2024-02-27 08:58 | 24 | 2024-02-26 08:05 | 2024-02-26 10:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM0473 | Balan Nair, Mr. Sreejesh | N - - - |  | Voice Communication
| CM-2023-12322124 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1122-004 – BG-20-09 |  | FM008 |  | 2023-10-26 13:48 | 2023-10-26 14:48 | 2023-10-27 14:48 | 24 | 2023-10-26 13:55 | 2023-10-26 16:30 | 155 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12382594 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - BG-20-09A |  | FM008 |  | 2023-11-14 20:03 | 2023-11-14 21:03 | 2023-11-15 21:03 | 24 | 2023-11-14 20:10 | 2023-11-14 22:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 87807 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2023-12367773 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | SUPPLY SIDE HAVING ABNORMAL SOUND |  | FM008 |  | 2023-11-10 13:28 | 2023-11-10 14:28 | 2023-11-11 14:28 | 24 | 2023-11-10 13:35 | 2023-11-10 16:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-10045120 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU-A1122-004 – COOLING COIL IS DIRTY – BG-20-09 |  | FM008 |  | 2022-01-12 00:57 | 2022-01-12 01:57 | 2022-01-13 01:57 | 24 | 2022-01-12 01:05 | 2022-01-12 04:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94954 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11044290 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU-A1122-004 – AHU CABIN LAMP IS NOT WORKING |  | FM008 |  | 2022-09-24 19:06 | 2022-09-24 20:06 | 2022-09-25 20:06 | 24 | 2022-09-24 19:16 | 2022-09-24 20:45 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94954 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11114064 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU-A1122-004 FILTER DIRTY BG-19-09 |  | FM008 |  | 2022-10-22 07:09 | 2022-10-22 08:09 | 2022-10-23 08:09 | 24 | 2022-10-22 07:15 | 2022-10-22 08:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10570592 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-04-19 07:19 | 2022-04-19 08:19 | 2022-04-20 08:19 | 24 | 2022-04-19 07:25 | 2022-04-19 09:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10693612 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -BG-20-09 |  | FM008 |  | 2022-05-26 08:14 | 2022-05-26 09:14 | 2022-05-27 09:14 | 24 | 2022-05-26 08:20 | 2022-05-26 15:00 | 400 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10886664 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU-A1122-004 FILTER ALARM GROUND FLOOR AREA 020 |  | FM008 |  | 2022-07-29 00:30 | 2022-07-29 01:30 | 2022-07-30 01:30 | 24 | 2022-07-29 00:35 | 2022-07-29 06:45 | 370 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11949001 | ASD-COB-GFL020-AHU082 | AIR HANDLING UNIT-05 | AHU-A1122-004 COOLING COIL DIRTY |  | FM008 |  | 2023-07-07 20:08 | 2023-07-07 21:08 | 2023-07-08 21:08 | 24 | 2023-07-07 20:18 | 2023-07-07 23:18 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10044129 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – BG-20-09 |  | FM008 |  | 2022-01-11 00:57 | 2022-01-11 01:57 | 2022-01-12 01:57 | 24 | 2022-01-11 01:00 | 2022-01-11 03:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10116648 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AIR DUCTS DAMAGED - TO BE RECTIFIED - CONCOURSE B- GROUND FLOOR (NEAR B11 - BUS ENTRANCE - GROUND FLOOR) |  | FM008 |  | 2022-02-06 15:12 | 2022-02-06 16:12 | 2022-02-07 16:12 | 24 | 2022-02-06 15:25 | 2022-02-06 18:50 | 205 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 85125 | 55709 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-10202469 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | LIGHTENING FLEXIBLE CONNECTOR DAMAGED AHU-A1122-009 - BG-20-09 |  | FM008 |  | 2022-03-01 08:54 | 2022-03-01 09:54 | 2022-03-02 09:54 | 24 | 2022-03-01 09:04 | 2022-03-01 11:39 | 155 | 183 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 106914 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10217611 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | Air ducts damaged - this needs to be replaced - last month it was observed only emergency repair (metallic tape) - 03 different ducts in the same location. Concourse B- Ground Floor (near B11 - bus entrance - ground floor) |  | FM008 |  | 2022-03-06 12:10 | 2022-03-06 13:10 | 2022-03-07 13:10 | 24 | 2022-03-06 12:15 | 2022-03-06 18:00 | 345 | 635 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-11176367 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 – BG-20-09A- SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-09 16:16 | 2022-11-09 17:16 | 2022-11-10 17:16 | 24 | 2022-11-09 16:25 | 2022-11-09 18:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11481619 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DDIRTY ; -BG-20-09 |  | FM008 |  | 2023-02-23 01:55 | 2023-02-23 02:55 | 2023-02-24 02:55 | 24 | 2023-02-23 02:00 | 2023-02-23 05:30 | 210 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11482467 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -BG-20-09 |  | FM008 |  | 2023-02-22 12:31 | 2023-02-22 13:31 | 2023-02-23 13:31 | 24 | 2023-02-22 12:40 | 2023-02-22 15:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-11785864 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-05-12 21:30 | 2023-05-12 22:30 | 2023-05-13 22:30 | 24 | 2023-05-12 21:35 | 2023-05-13 00:30 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2023-12036332 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 DUCT INSULATION DAMAGED BG-20-09DA |  | FM008 |  | 2023-07-31 19:40 | 2023-07-31 20:40 | 2023-08-01 20:40 | 24 | 2023-07-31 19:45 | 2023-07-31 21:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12059381 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DRAIN LINE INSULATION DAMAGED - AHU-A1122-009 – BG-20-09 |  | FM008 |  | 2023-08-10 13:25 | 2023-08-10 14:25 | 2023-08-11 14:25 | 24 | 2023-08-10 13:35 | 2023-08-10 15:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12252527 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-04 00:35 | 2023-10-04 01:35 | 2023-10-05 01:35 | 24 | 2023-10-04 00:45 | 2023-10-04 03:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12692396 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AIR HANDLING UNIT 087 (TAG NO:AHU-A1122-009-CONCOURSE B-GROUND FLOOR AREA 020 |  | FM008 |  | 2024-02-29 20:05 | 2024-02-29 21:05 | 2024-03-01 21:05 | 24 | 2024-02-29 20:10 | 2024-02-29 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17336 | 17053 |  |  | FM12539 | SOWMESH JAYARAJ, | N - - - |  | Voice Communication
| CM-2022-11181503 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-009 – BG-20-09 |  | FM008 |  | 2022-11-12 22:03 | 2022-11-12 23:03 | 2022-11-13 23:03 | 24 | 2022-11-12 22:10 | 2022-11-13 01:00 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11310913 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY (BG-20-09A) - AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 020 |  | FM008 |  | 2022-12-25 20:03 | 2022-12-25 21:03 | 2022-12-26 21:03 | 24 | 2022-12-25 20:10 | 2022-12-25 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 132112 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11345010 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 – COOLING COIL DIRTY-- |  | FM008 |  | 2023-01-02 20:22 | 2023-01-02 21:22 | 2023-01-03 21:22 | 24 | 2023-01-02 20:30 | 2023-01-02 23:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11844528 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 COOLING COIL DIRTY BG-19-04 |  | FM008 |  | 2023-06-03 19:12 | 2023-06-03 20:12 | 2023-06-04 20:12 | 24 | 2023-06-03 19:20 | 2023-06-03 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 89127 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12155179 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -BG-20-09A-AIR HANDLING UNIT 087 (TAG NO:AHU-A1122-009)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 020 |  | FM008 |  | 2023-09-06 19:42 | 2023-09-06 20:42 | 2023-09-07 20:42 | 24 | 2023-09-06 19:50 | 2023-09-06 22:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 17053 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2023-12192177 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU FILER DIRTY - AHU-A1122-009 - BG-20-09 |  | FM008 |  | 2023-09-17 16:21 | 2023-09-17 17:21 | 2023-09-18 17:21 | 24 | 2023-09-17 16:30 | 2023-09-17 18:45 | 135 | 145 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12349545 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – BG-20-09 |  | FM008 |  | 2023-11-05 22:05 | 2023-11-05 23:05 | 2023-11-06 23:05 | 24 | 2023-11-05 22:10 | 2023-11-06 00:15 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12683943 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 AHU FILTER DIRTY |  | FM008 |  | 2024-02-28 19:57 | 2024-02-28 20:57 | 2024-02-29 20:57 | 24 | 2024-02-28 20:05 | 2024-02-28 22:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-11355838 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-09 21:35 | 2023-01-09 22:35 | 2023-01-10 22:35 | 24 | 2023-01-09 21:40 | 2023-01-09 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11972513 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1122-009 – BG-20-09 |  | FM008 |  | 2023-07-11 21:20 | 2023-07-11 22:20 | 2023-07-12 22:20 | 24 | 2023-07-11 21:30 | 2023-07-12 00:30 | 180 | 335 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12085271 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | FILTER DIRTY - BG-20-09 |  | FM008 |  | 2023-08-15 08:32 | 2023-08-15 09:32 | 2023-08-16 09:32 | 24 | 2023-08-15 08:40 | 2023-08-15 18:35 | 595 | 190 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12114431 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 AHU CABIN LAMP FAULTY BG-20-09 |  | FM008 |  | 2023-08-23 19:13 | 2023-08-23 20:13 | 2023-08-24 20:13 | 24 | 2023-08-23 19:20 | 2023-08-23 23:55 | 275 | 145 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68485 | 17053 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-12133783 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | CONDENSATION DRAIN LINE INSULATION DAMAGED BG-20-09 |  | FM008 |  | 2023-08-29 13:48 | 2023-08-29 14:48 | 2023-08-30 14:48 | 24 | 2023-08-29 13:55 | 2023-08-29 16:55 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 106972 | 17053 |  |  | FM1119 | Farok, Mr. Omur | N - - - |  | Voice Communication
| CM-2023-12141642 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DRAIN LINE INSULATION DAMAGED -BG-20-09 |  | FM008 |  | 2023-09-02 07:48 | 2023-09-02 08:48 | 2023-09-03 08:48 | 24 | 2023-09-02 07:55 | 2023-09-02 10:25 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2024-12825200 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 COOLING COIL DIRTY BG-20-09 |  | FM008 |  | 2024-04-13 01:16 | 2024-04-13 02:16 | 2024-04-14 02:16 | 24 | 2024-04-13 01:20 | 2024-04-13 05:00 | 220 | 455 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12342158 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -BG-20-09 |  | FM008 |  | 2023-10-31 15:09 | 2023-10-31 16:09 | 2023-11-01 16:09 | 24 | 2023-10-31 15:15 | 2023-10-31 18:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12483946 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU NOISY -BG-20-09 |  | FM008 |  | 2023-12-17 08:16 | 2023-12-17 09:16 | 2023-12-18 09:16 | 24 | 2023-12-17 08:25 | 2023-12-17 12:30 | 245 | 980 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | BLOWER DAMAGE | REPLACED THE BLOWER | 17333 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10208198 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1122-009 BG-20-09 |  | FM008 |  | 2022-03-02 08:36 | 2022-03-02 09:36 | 2022-03-03 09:36 | 24 | 2022-03-02 08:45 | 2022-03-02 11:00 | 135 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10223940 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009- COOLING COIL DIRTY – BG-20-09 |  | FM008 |  | 2022-03-09 00:16 | 2022-03-09 01:16 | 2022-03-10 01:16 | 24 | 2022-03-09 00:25 | 2022-03-09 02:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10326306 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1122-009 – BG-20-09 |  | FM008 |  | 2022-04-08 13:37 | 2022-04-08 14:37 | 2022-04-09 14:37 | 24 | 2022-04-08 13:45 | 2022-04-08 16:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2022-10696466 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY – AHU-A1122-009 – BG-20-09 |  | FM008 |  | 2022-05-26 19:30 | 2022-05-26 20:30 | 2022-05-27 20:30 | 24 | 2022-05-26 19:35 | 2022-05-26 22:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11044292 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 - AHU CABIN LAMP IS NOT WORKING |  | FM008 |  | 2022-09-24 19:09 | 2022-09-24 20:09 | 2022-09-25 20:09 | 24 | 2022-09-24 19:19 | 2022-09-24 23:55 | 276 | 188 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOT WORKING | THE EQUIPMENT HAS BEEN SWITCH OFF | THE POWER HAS BEEN RESTORED | 94954 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11114062 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU-A1122-009 FILTER DIRTY BG-19-09 |  | FM008 |  | 2022-10-22 07:07 | 2022-10-22 08:07 | 2022-10-23 08:07 | 24 | 2022-10-22 07:15 | 2022-10-22 09:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10142436 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | AHU087 DUCT INSULATION DAMAGED – BG-20-09 |  | FM008 |  | 2022-02-15 14:10 | 2022-02-15 15:10 | 2022-02-16 15:10 | 24 | 2022-02-15 14:15 | 2022-02-15 15:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106976 | 55709 |  |  | FM10089 | Singh, Mr. Dhananjay Kumar | N - - - |  | Voice Communication
| CM-2022-10958719 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – BG-20-09 |  | FM008 |  | 2022-08-23 21:59 | 2022-08-23 22:59 | 2022-08-24 22:59 | 24 | 2022-08-23 22:05 | 2022-08-23 23:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11948301 | ASD-COB-GFL020-AHU087 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS CONCOURSE B-GROUND FLOOR AREA 020 |  | FM008 |  | 2023-07-05 11:43 | 2023-07-05 12:43 | 2023-07-06 12:43 | 24 | 2023-07-05 11:50 | 2023-07-05 15:42 | 232 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 020 | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2022-10726808 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU-A1157-001 FILTER DIRTY – BG-18A-02 |  | FM008 |  | 2022-06-05 21:58 | 2022-06-05 22:58 | 2022-06-06 22:58 | 24 | 2022-06-05 22:05 | 2022-06-05 23:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-11117700 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-001 |  | FM008 |  | 2022-10-22 07:14 | 2022-10-22 08:13 | 2022-10-23 08:13 | 24 | 2022-10-22 07:20 | 2022-10-22 10:20 | 180 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106972 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11226363 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | SUPLY FAN BELT DAMAGED – AHU-A1157-001 |  | FM008 |  | 2022-11-28 08:20 | 2022-11-28 09:20 | 2022-11-29 09:20 | 24 | 2022-11-28 08:25 | 2022-11-28 10:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-11226364 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1157-001 |  | FM008 |  | 2022-11-28 08:22 | 2022-11-28 09:22 | 2022-11-29 09:22 | 24 | 2022-11-28 08:26 | 2022-11-28 12:30 | 244 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11250704 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 191 -FILTER DIRTY-CONCOURSE B-GROUND FLOOR AREA 18A |  | FM008 |  | 2022-12-04 20:30 | 2022-12-04 21:30 | 2022-12-05 21:30 | 24 | 2022-12-04 20:35 | 2022-12-04 23:55 | 200 | 600 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 77406 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12114553 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1157-001 - CONCOURSE B-GROUND FLOOR AREA 18A - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.GNDP4.IBFW02.AHU001.SYSALM.DP1 / |  | FM008 |  | 2023-08-24 11:18 | 2023-08-24 12:18 | 2023-08-25 12:18 | 24 | 2023-08-24 11:25 | 2023-08-24 14:00 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12233275 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1157-001 – BG 18A 02 |  | FM008 |  | 2023-09-30 21:34 | 2023-09-30 22:34 | 2023-10-01 22:34 | 24 | 2023-09-30 21:40 | 2023-09-30 23:58 | 138 | 276 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12324977 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-10-26 00:03 | 2023-10-26 01:03 | 2023-10-27 01:03 | 24 | 2023-10-26 00:10 | 2023-10-26 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12422489 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU-A1157-001 COOLING COIL DIRTY BG-18-02 |  | FM008 |  | 2023-11-28 19:44 | 2023-11-28 20:44 | 2023-11-29 20:44 | 24 | 2023-11-28 19:50 | 2023-11-28 23:00 | 190 | 570 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 87807 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2022-11159381 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU-A1157-001 – AHU INSIDE LIGHT NOT WORKING – BG-18A-02 |  | FM008 |  | 2022-11-02 21:15 | 2022-11-02 22:15 | 2022-11-03 22:15 | 24 | 2022-11-02 21:20 | 2022-11-02 23:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11230511 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU-A1157-001 RETURN DUCT WIRE MESH BLOCKED |  | FM008 |  | 2022-11-29 10:07 | 2022-11-29 11:07 | 2022-11-30 11:07 | 24 | 2022-11-29 10:15 | 2022-11-29 15:15 | 300 | 900 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2023-11609792 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | FILTER DIRTY-AHU-A1157-001-CONCOURSE B-GROUND FLOOR AREA 18A |  | FM008 |  | 2023-03-30 20:43 | 2023-03-30 21:43 | 2023-03-31 21:43 | 24 | 2023-03-30 20:50 | 2023-03-30 23:55 | 185 | 370 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | E-mail
| CM-2023-11762258 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | CABIN LAMP NOT WORKING -BG-18A-02 |  | FM008 |  | 2023-05-02 19:00 | 2023-05-02 20:00 | 2023-05-03 20:00 | 24 | 2023-05-02 19:10 | 2023-05-02 23:00 | 230 | 355 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 17053 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2023-11835120 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU SUPPLY DUCT INSULATION DAMAGED – BG-18A-08 |  | FM008 |  | 2023-05-30 08:19 | 2023-05-30 09:19 | 2023-05-31 09:19 | 24 | 2023-05-30 08:25 | 2023-05-30 12:25 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 87807 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2023-11842358 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-AIR HANDLING UNIT 191 (TAG NO:AHU-A1157-001)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 18A |  | FM008 |  | 2023-06-01 16:41 | 2023-06-01 17:41 | 2023-06-02 17:41 | 24 | 2023-06-01 16:50 | 2023-06-01 18:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | FILTER DRIER OBSTRUCTED | CLEARED THE OBSTRUCTION | 106914 | 87807 |  |  | 10302 | Thomas J K | N - - - |  | Voice Communication
| CM-2023-11901128 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU-A1157-001 DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-06-19 11:13 | 2023-06-19 12:13 | 2023-06-20 12:13 | 24 | 2023-06-19 11:20 | 2023-06-19 13:30 | 130 | 250 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 121959 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11994587 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARM – (AHU-A1157-001) – BG 18A 02 |  | FM008 |  | 2023-07-20 13:54 | 2023-07-20 14:54 | 2023-07-21 14:54 | 24 | 2023-07-20 14:05 | 2023-07-20 17:50 | 225 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 94954 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12192178 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1157-001 - BG-18A-02 |  | FM008 |  | 2023-09-17 16:23 | 2023-09-17 17:23 | 2023-09-18 17:23 | 24 | 2023-09-17 16:30 | 2023-09-17 17:30 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12493815 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - A1157-001 -BG 18A 02 |  | FM008 |  | 2023-12-23 13:43 | 2023-12-23 14:43 | 2023-12-24 14:43 | 24 | 2023-12-23 13:55 | 2023-12-23 16:00 | 125 | 375 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2022-11230115 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - BG-18A-02 |  | FM008 |  | 2022-11-27 19:29 | 2022-11-27 20:29 | 2022-11-28 20:29 | 24 | 2022-11-27 19:40 | 2022-11-27 23:40 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11231708 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU-A1157-001- COOLING COIL DIRTY |  | FM008 |  | 2022-12-01 00:15 | 2022-12-01 01:15 | 2022-12-02 01:15 | 24 | 2022-12-01 00:20 | 2022-12-01 03:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12527119 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1157-001 – BG-18A-02 |  | FM008 |  | 2024-01-03 20:03 | 2024-01-03 21:03 | 2024-01-04 21:03 | 24 | 2024-01-03 20:10 | 2024-01-03 22:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2023-12423311 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1157-001 – BG-18A-02 |  | FM008 |  | 2023-11-28 16:13 | 2023-11-28 17:13 | 2023-11-29 17:13 | 24 | 2023-11-28 16:20 | 2023-11-28 18:45 | 145 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12514924 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1157-001 – BG-18A-02 |  | FM008 |  | 2023-12-29 12:31 | 2023-12-29 13:31 | 2023-12-30 13:31 | 24 | 2023-12-29 12:40 | 2023-12-29 15:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11333474 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - TG-18A-02 |  | FM008 |  | 2023-01-01 14:06 | 2023-01-01 15:06 | 2023-01-02 15:06 | 24 | 2023-01-01 14:15 | 2023-01-01 15:48 | 93 | 372 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-10226455 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-03-09 19:10 | 2022-03-09 20:10 | 2022-03-10 20:10 | 24 | 2022-03-09 19:15 | 2022-03-09 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | BMS
| CM-2022-10615514 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1157-001 – TG-18-02 |  | FM008 |  | 2022-05-04 21:00 | 2022-05-04 22:00 | 2022-05-05 22:00 | 24 | 2022-05-04 21:05 | 2022-05-04 23:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-10694495 | ASD-COB-GFL18A-AHU191 | AIR HANDLING UNIT-05 | AHU- A1157-001- AIR LEAKAGE FROM SUPPLY AIR DUCT – - |  | FM008 |  | 2022-05-25 21:53 | 2022-05-25 22:53 | 2022-05-26 22:53 | 24 | 2022-05-25 21:55 | 2022-05-25 23:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 94953 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10048822 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002 COOLING COIL DIRTY |  | FM008 |  | 2022-01-15 19:27 | 2022-01-15 20:27 | 2022-01-16 20:27 | 24 | 2022-01-15 19:30 | 2022-01-15 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10121214 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | COOILING COIL DIRTY-AHU-A1157-002)-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 18A |  | FM008 |  | 2022-02-09 13:06 | 2022-02-09 14:06 | 2022-02-10 14:06 | 24 | 2022-02-09 13:10 | 2022-02-09 16:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10627289 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AIR DUTS DAMAGED -TERMIC TAPE TO BE PROPERLY REPLACED NEAR BG-18A-08 (SCR))-AIRSIDE-CONCOURSE B-GROUND FLOOR AREA 018A |  | FM008 |  | 2022-05-08 14:43 | 2022-05-08 15:43 | 2022-05-09 15:43 | 24 | 2022-05-08 14:50 | 2022-05-08 18:58 | 248 | 269 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17336 | 17053 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | Voice Communication
| CM-2022-11222737 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -BG-18-02 |  | FM008 |  | 2022-11-27 14:21 | 2022-11-27 15:21 | 2022-11-28 15:21 | 24 | 2022-11-27 14:25 | 2022-11-27 16:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11805267 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002-FILTER DIRTY-CONCOURSE B-GROUND FLOOR AREA 18A |  | FM008 |  | 2023-05-21 21:53 | 2023-05-21 22:53 | 2023-05-22 22:53 | 24 | 2023-05-21 22:00 | 2023-05-22 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM12183 | Ray, Mr. Sree Khatis Chandra | N - - - |  | Voice Communication
| CM-2023-11936177 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1157-002 – BG-18-02 |  | FM008 |  | 2023-06-30 09:21 | 2023-06-30 10:21 | 2023-07-01 10:21 | 24 | 2023-06-30 09:25 | 2023-06-30 13:40 | 255 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12018231 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002- AHU CABIN LAMP NOT WORKING |  | FM008 |  | 2023-07-29 19:19 | 2023-07-29 20:19 | 2023-07-30 20:19 | 24 | 2023-07-29 19:30 | 2023-07-29 22:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 87807 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12017456 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AC VENT DIRTY - AHU-A1157-002 - MECHANICAL ROOM BG-18A-02 |  | FM008 |  | 2023-07-30 09:43 | 2023-07-30 10:43 | 2023-07-31 10:43 | 24 | 2023-07-30 09:50 | 2023-07-30 14:55 | 305 | 485 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12034003 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002 FILTER DIRTY BG-18A-02 |  | FM008 |  | 2023-07-30 22:03 | 2023-07-30 23:03 | 2023-07-31 23:03 | 24 | 2023-07-30 22:05 | 2023-07-31 00:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 89127 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12116864 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | FLOOR AC VENT DIRTY-GATE B02 |  | FM008 |  | 2023-08-27 07:25 | 2023-08-27 08:25 | 2023-08-28 08:25 | 24 | 2023-08-27 07:35 | 2023-08-27 10:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2024-12537795 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002 DUCT INSULATION DAMAGED BG-18A-02 |  | FM008 |  | 2024-01-06 19:51 | 2024-01-06 20:51 | 2024-01-07 20:51 | 24 | 2024-01-06 20:00 | 2024-01-06 23:30 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11197937 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | FLOOR AC VENTS IS DIRTY – AHU-A1157-002 – MECHANICAL ROOM BG-18A-02 |  | FM008 |  | 2022-11-19 21:02 | 2022-11-19 22:02 | 2022-11-20 22:02 | 24 | 2022-11-19 21:10 | 2022-11-19 23:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11842133 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002 COOLING COIL DIRTY BG-18A-02 |  | FM008 |  | 2023-06-03 19:06 | 2023-06-03 20:06 | 2023-06-04 20:06 | 24 | 2023-06-03 19:15 | 2023-06-03 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 89127 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11937178 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | FLOOR AC VENT DIRTY - GATE B2 NEAR B1-18A-27 |  | FM008 |  | 2023-06-30 16:48 | 2023-06-30 17:48 | 2023-07-01 17:48 | 24 | 2023-06-30 16:55 | 2023-06-30 18:50 | 115 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM5770 | Khan, Mr. Md Ratan | N - - - |  | Voice Communication
| CM-2023-12016548 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AC VENT DIRTY - AHU-A1157-002 – BOARDING GATE B2 |  | FM008 |  | 2023-07-29 07:56 | 2023-07-29 08:56 | 2023-07-30 08:56 | 24 | 2023-07-29 08:00 | 2023-07-29 09:40 | 100 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12250207 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM SUPPLY SIDE MOTOR -AHU-A1157-002 BG18A-02 |  | FM008 |  | 2023-10-01 23:38 | 2023-10-02 00:38 | 2023-10-03 00:38 | 24 | 2023-10-01 23:45 | 2023-10-02 03:00 | 195 | 780 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12410136 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-002) |  | FM008 |  | 2023-11-25 13:12 | 2023-11-25 14:12 | 2023-11-26 14:12 | 24 | 2023-11-25 13:20 | 2023-11-25 16:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2023-12493816 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - A1157-002 – BG 18A 02 |  | FM008 |  | 2023-12-23 13:46 | 2023-12-23 14:46 | 2023-12-24 14:46 | 24 | 2023-12-23 13:55 | 2023-12-23 16:00 | 125 | 375 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-11620589 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002 DP1 FILTER ALARM |  | FM008 |  | 2023-04-02 22:17 | 2023-04-02 23:17 | 2023-04-03 23:17 | 24 | 2023-04-02 22:20 | 2023-04-03 03:00 | 280 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12124632 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | FLOOR AC VENT DIRTY |  | FM008 |  | 2023-08-28 07:46 | 2023-08-28 08:46 | 2023-08-29 08:46 | 24 | 2023-08-28 07:55 | 2023-08-28 10:30 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-10031459 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AIR DUCTS DAMAGED - TO BE RECTIFIED CONCOURSE B- GROUND FLOOR (NEAR SECONDARY COMMUNICATIONS ROOM BG 18A 09 ) |  | FM008 |  | 2022-01-06 15:17 | 2022-01-06 16:17 | 2022-01-07 16:17 | 24 | 2022-01-06 15:25 | 2022-01-06 18:15 | 170 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 55709 |  |  | 106590 | Claudio, Mr. Henry Augusto | N - - - |  | E-mail
| CM-2022-10351979 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | GATE B2 – NOISE FROM AC PANEL BOX- |  | FM008 |  | 2022-04-12 16:38 | 2022-04-12 17:38 | 2022-04-13 17:38 | 24 | 2022-04-12 16:45 | 2022-04-12 23:55 | 430 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 17053 |  |  | 66244 | Subramaniyam, Mr. Sivaraj | N - - - |  | Voice Communication
| CM-2022-11114069 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | AHU-A1157-002 FILTER DIRTY BG-18A-02 |  | FM008 |  | 2022-10-22 08:03 | 2022-10-22 09:03 | 2022-10-23 09:03 | 24 | 2022-10-22 08:10 | 2022-10-22 11:05 | 175 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11179131 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WOKRING |  | FM008 |  | 2022-11-09 19:08 | 2022-11-09 20:08 | 2022-11-10 20:08 | 24 | 2022-11-09 19:15 | 2022-11-09 21:25 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10226456 | ASD-COB-GFL18A-AHU192 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-03-09 19:11 | 2022-03-09 20:11 | 2022-03-10 20:11 | 24 | 2022-03-09 19:20 | 2022-03-09 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 18A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | BMS
| CM-2022-11209065 | ASD-COB-SFL016-AHU092 | AIR HANDLING UNIT-05 | CABIN LIGHT NOT WORKING -AHU-A1122-201)-AIRSIDE-CONCOURSE B-SECOND FLOOR AREA 016 |  | FM008 |  | 2022-11-22 21:48 | 2022-11-22 22:48 | 2022-11-23 22:48 | 24 | 2022-11-22 21:55 | 2022-11-22 23:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17336 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11440722 | ASD-COB-SFL016-AHU092 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS- AIR HANDLING UNIT 092 (TAG NO:AHU-A1122-201)-AIRSIDE-CONCOURSE B-SECOND FLOOR AREA 016 |  | FM008 |  | 2023-02-09 13:25 | 2023-02-09 14:25 | 2023-02-10 14:25 | 24 | 2023-02-09 13:30 | 2023-02-09 15:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12114321 | ASD-COB-SFL016-AHU092 | AIR HANDLING UNIT-05 | AHU CABIN LAMP SWITCH FAULTY - AHU-A1122-201 – BG-17-21 |  | FM008 |  | 2023-08-26 12:40 | 2023-08-26 13:40 | 2023-08-27 13:40 | 24 | 2023-08-26 12:50 | 2023-08-26 14:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-10736635 | ASD-COB-SFL016-AHU092 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - AHU-A1122-201 - MECHANICAL ROOM B2-17-21 |  | FM008 |  | 2022-06-11 14:05 | 2022-06-11 15:05 | 2022-06-12 15:05 | 24 | 2022-06-11 14:10 | 2022-06-11 16:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11615885 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1122-202 - B2-16-20 |  | FM008 |  | 2023-04-03 20:00 | 2023-04-03 21:00 | 2023-04-04 21:00 | 24 | 2023-04-03 20:05 | 2023-04-03 22:35 | 150 | 300 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11933422 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING –( AHU-A1122-202) - B2 16 38 |  | FM008 |  | 2023-06-28 02:32 | 2023-06-28 03:32 | 2023-06-29 03:32 | 24 | 2023-06-28 02:40 | 2023-06-28 04:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 132112 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12202438 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1122-202 - SECOND FLOOR AREA 016 |  | FM008 |  | 2023-09-20 00:11 | 2023-09-20 01:11 | 2023-09-21 01:11 | 24 | 2023-09-20 00:15 | 2023-09-20 03:30 | 195 | 125 | 3 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11843521 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED |  | FM008 |  | 2023-06-02 20:33 | 2023-06-02 21:33 | 2023-06-03 21:33 | 24 | 2023-06-02 20:40 | 2023-06-02 23:00 | 140 | 125 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11226998 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AHU-A1122-202 |  | FM008 |  | 2022-11-30 00:17 | 2022-11-30 01:17 | 2022-12-01 01:17 | 24 | 2022-11-30 00:25 | 2022-11-30 03:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10736634 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - AHU-A1122-202 - MECHANICAL ROOM B2-16-38 |  | FM008 |  | 2022-06-11 14:03 | 2022-06-11 15:03 | 2022-06-12 15:03 | 24 | 2022-06-11 14:10 | 2022-06-11 16:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10796305 | ASD-COB-SFL016-AHU093 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-06-30 18:58 | 2022-06-30 19:58 | 2022-07-01 19:58 | 24 | 2022-06-30 19:05 | 2022-06-30 21:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | SECOND FLOOR AREA 016 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68060 | 95217 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10256888 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU-A1126-002-RETURN DUCT ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-03-17 22:46 | 2022-03-17 23:46 | 2022-03-18 23:46 | 24 | 2022-03-17 22:55 | 2022-03-18 00:45 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95217 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10885989 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1126-002 – C0-01-20 |  | FM008 |  | 2022-07-29 15:16 | 2022-07-29 16:16 | 2022-07-30 16:16 | 24 | 2022-07-29 15:20 | 2022-07-29 17:00 | 100 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11570163 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-03-19 14:23 | 2023-03-19 15:23 | 2023-03-20 15:23 | 24 | 2023-03-19 14:30 | 2023-03-19 16:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11853695 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-002 /C0-01-20 |  | FM008 |  | 2023-06-05 14:25 | 2023-06-05 15:25 | 2023-06-06 15:25 | 24 | 2023-06-05 14:30 | 2023-06-05 16:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 94954 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12064394 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU CABIN HEATER FLEXIBLE CONNECTOR DAMAGED - C0-01-20,MEC ROOM |  | FM008 |  | 2023-08-10 02:02 | 2023-08-10 03:02 | 2023-08-11 03:02 | 24 | 2023-08-10 02:10 | 2023-08-10 06:40 | 270 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 105233 | 87807 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-12516535 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-30 19:04 | 2023-12-30 20:04 | 2023-12-31 20:04 | 24 | 2023-12-30 19:10 | 2023-12-30 21:40 | 150 | 600 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12554394 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | FLOOR AC VENT DETACHED NEAR C2-01-36 |  | FM008 |  | 2024-01-10 09:04 | 2024-01-10 10:04 | 2024-01-11 10:04 | 24 | 2024-01-10 09:08 | 2024-01-10 12:00 | 172 | 354 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | VIBRATION OF EQUIPMENT DUE TO LOOSE PARTS | RECTIFIED | 106914 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2024-12635620 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-002 - MECHANICAL ROOM C0-01-20 |  | FM008 |  | 2024-02-10 19:33 | 2024-02-10 20:33 | 2024-02-11 20:33 | 24 | 2024-02-10 19:40 | 2024-02-10 22:10 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17573 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11226427 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU-A1126-002 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-11-28 12:28 | 2022-11-28 13:28 | 2022-11-29 13:28 | 24 | 2022-11-28 12:35 | 2022-11-28 15:05 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11300174 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED C0-01-02 |  | FM008 |  | 2022-12-22 20:37 | 2022-12-22 21:37 | 2022-12-23 21:37 | 24 | 2022-12-22 20:45 | 2022-12-22 22:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11779446 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C0-01-20 |  | FM008 |  | 2023-05-09 20:02 | 2023-05-09 21:02 | 2023-05-10 21:02 | 24 | 2023-05-09 20:10 | 2023-05-09 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 106972 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11908897 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU-A1126-002 C0-01-20 FILTER DIRTY |  | FM008 |  | 2023-06-21 15:53 | 2023-06-21 16:53 | 2023-06-22 16:53 | 24 | 2023-06-21 16:00 | 2023-06-21 18:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12117844 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-002, C0-01-20 |  | FM008 |  | 2023-08-27 12:34 | 2023-08-27 13:34 | 2023-08-28 13:34 | 24 | 2023-08-27 12:40 | 2023-08-27 14:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12279224 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-002;C0-01-20 |  | FM008 |  | 2023-10-12 19:02 | 2023-10-12 20:02 | 2023-10-13 20:02 | 24 | 2023-10-12 19:10 | 2023-10-12 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12725998 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU-A1126-002 C0-01-20 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-03-11 07:14 | 2024-03-11 08:14 | 2024-03-12 08:14 | 24 | 2024-03-11 07:30 | 2024-03-11 10:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11918237 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE-C0-01-20 |  | FM008 |  | 2023-06-24 20:21 | 2023-06-24 21:21 | 2023-06-25 21:21 | 24 | 2023-06-24 20:30 | 2023-06-24 22:50 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12096675 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY, AHU-A1126-002, C0-01-20 |  | FM008 |  | 2023-08-17 08:43 | 2023-08-17 09:43 | 2023-08-18 09:43 | 24 | 2023-08-17 08:50 | 2023-08-17 12:45 | 235 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12226192 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED â?? AHU-A1126-002 â?? C0 01 20 |  | FM008 |  | 2023-09-26 09:21 | 2023-09-26 10:21 | 2023-09-27 10:21 | 24 | 2023-09-26 09:25 | 2023-09-26 11:55 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 87807 |  |  | FM12472 | Arumuga Nainar Senthilkumar, | N - - - |  | Voice Communication
| CM-2024-12693221 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY |  | FM008 |  | 2024-03-03 19:23 | 2024-03-03 20:23 | 2024-03-04 20:23 | 24 | 2024-03-03 19:30 | 2024-03-03 21:55 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12810763 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-002, C0-01-20 |  | FM008 |  | 2024-04-10 14:07 | 2024-04-10 15:07 | 2024-04-11 15:07 | 24 | 2024-04-10 14:15 | 2024-04-10 17:10 | 175 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2023-12383183 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1126-002)-CONCOURSE C-GROUND FLOOR AREA 001- C0-01-20 |  | FM008 |  | 2023-11-16 07:40 | 2023-11-16 08:40 | 2023-11-17 08:40 | 24 | 2023-11-16 07:45 | 2023-11-16 10:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12456743 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-10 10:22 | 2023-12-10 11:22 | 2023-12-11 11:22 | 24 | 2023-12-10 10:30 | 2023-12-10 13:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12539137 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | FLOOR AC VENT DIRTY -C0-01-20 |  | FM008 |  | 2024-01-09 08:52 | 2024-01-09 09:52 | 2024-01-10 09:52 | 24 | 2024-01-09 09:00 | 2024-01-09 12:30 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12644842 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C0-01-20 |  | FM008 |  | 2024-02-12 19:43 | 2024-02-12 20:43 | 2024-02-13 20:43 | 24 | 2024-02-12 19:50 | 2024-02-12 21:55 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10084693 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1126-002 – C0-01-20 |  | FM008 |  | 2022-01-28 22:31 | 2022-01-28 23:31 | 2022-01-29 23:31 | 24 | 2022-01-28 22:35 | 2022-01-29 01:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106973 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-9958622 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1126-002)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-01-03 21:54 | 2022-01-03 22:54 | 2022-01-04 22:54 | 24 | 2022-01-03 22:00 | 2022-01-03 23:55 | 115 | 345 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 55709 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10694079 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-05-29 10:10 | 2022-05-29 11:10 | 2022-05-30 11:10 | 24 | 2022-05-29 10:15 | 2022-05-29 12:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95216 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11114319 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-10-18 07:16 | 2022-10-18 08:16 | 2022-10-19 08:16 | 24 | 2022-10-18 07:25 | 2022-10-18 12:05 | 280 | 370 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 95217 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11423438 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- C0-01-20 |  | FM008 |  | 2023-02-03 21:13 | 2023-02-03 22:13 | 2023-02-04 22:13 | 24 | 2023-02-03 21:20 | 2023-02-03 23:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11656453 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE C0-01-20 |  | FM008 |  | 2023-04-12 14:04 | 2023-04-12 15:04 | 2023-04-13 15:04 | 24 | 2023-04-12 14:13 | 2023-04-12 16:20 | 127 | 381 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10258880 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU-A1126-002-RETURN AIR DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-18 19:01 | 2022-03-18 20:01 | 2022-03-19 20:01 | 24 | 2022-03-18 19:05 | 2022-03-18 21:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11951044 | ASD-COC-GFL001-AHU096 | AIR HANDLING UNIT-05 | AHU-A1126-002 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-07-07 22:02 | 2023-07-07 23:02 | 2023-07-08 23:02 | 24 | 2023-07-07 22:10 | 2023-07-08 01:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10154523 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGE AHU-A1126-003 |  | FM008 |  | 2022-02-21 16:46 | 2022-02-21 17:46 | 2022-02-22 17:46 | 24 | 2022-02-21 16:50 | 2022-02-21 18:45 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2022-11030723 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003 – SUPPLY DUCT INSULATION IS DAMAGED – C0-01-08 |  | FM008 |  | 2022-09-16 20:46 | 2022-09-16 21:46 | 2022-09-17 21:46 | 24 | 2022-09-16 20:50 | 2022-09-16 23:00 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11190528 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-11-14 12:47 | 2022-11-14 13:47 | 2022-11-15 13:47 | 24 | 2022-11-14 12:57 | 2022-11-14 14:25 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | SUPPLY POWER FAILURE | RESET THE BREAKER | 121959 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12324691 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003 FILTER DIRY – C0-01-08 |  | FM008 |  | 2023-10-25 07:05 | 2023-10-25 08:05 | 2023-10-26 08:05 | 24 | 2023-10-25 07:10 | 2023-10-25 18:00 | 650 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12340685 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-003 - MECHANICAL ROOM C0-01-08 |  | FM008 |  | 2023-10-29 23:29 | 2023-10-30 00:29 | 2023-10-31 00:29 | 24 | 2023-10-29 23:35 | 2023-10-30 02:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12555898 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | FILER DIRTY -AHU-A1126-003 (C0-01-08) |  | FM008 |  | 2024-01-14 09:23 | 2024-01-14 10:23 | 2024-01-15 10:23 | 24 | 2024-01-14 09:30 | 2024-01-14 11:10 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 95217 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12797319 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | EXHUAST FAN NOISY - C2-01-01 |  | FM008 |  | 2024-04-06 02:56 | 2024-04-06 03:56 | 2024-04-07 03:56 | 24 | 2024-04-06 03:05 | 2024-04-06 08:02 | 297 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 17053 |  |  | 17537 | Agyapong, Mr. Abraham Sono Kwame | N - - - |  | Voice Communication
| CM-2022-11028076 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - FILTERS 850-AIR HANDLING UNIT 097 (TAG NO:AHU-A1126-003)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP1.CONC0108.AHU003.SYSALM.DP1 / |  | FM008 |  | 2022-09-17 01:39 | 2022-09-17 02:39 | 2022-09-18 02:39 | 24 | 2022-09-17 01:45 | 2022-09-17 06:45 | 300 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12014170 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-07-25 20:44 | 2023-07-25 21:44 | 2023-07-26 21:44 | 24 | 2023-07-25 20:50 | 2023-07-25 23:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12217936 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003 â?? DUCT INSULATION DAMAGED â?? C0-01-08 |  | FM008 |  | 2023-09-25 08:38 | 2023-09-25 09:38 | 2023-09-26 09:38 | 24 | 2023-09-25 08:45 | 2023-09-25 11:45 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 87807 |  |  | FM12472 | Arumuga Nainar Senthilkumar, | N - - - |  | Voice Communication
| CM-2023-12365245 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-08 07:20 | 2023-11-08 08:20 | 2023-11-09 08:20 | 24 | 2023-11-08 07:25 | 2023-11-08 10:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2024-12757929 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003 DUCT INSULATION DAMAGED C0-01-08 |  | FM008 |  | 2024-03-24 08:22 | 2024-03-24 09:22 | 2024-03-25 09:22 | 24 | 2024-03-24 08:30 | 2024-03-24 11:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-11356901 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003-CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-01-09 00:43 | 2023-01-09 01:43 | 2023-01-10 01:43 | 24 | 2023-01-09 00:50 | 2023-01-09 02:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 95217 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11786135 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-003 – C0-01-08 – |  | FM008 |  | 2023-05-13 21:11 | 2023-05-13 22:11 | 2023-05-14 22:11 | 24 | 2023-05-13 21:20 | 2023-05-13 23:20 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12641400 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-003 – C0-01-08 |  | FM008 |  | 2024-02-11 19:16 | 2024-02-11 20:16 | 2024-02-12 20:16 | 24 | 2024-02-11 19:20 | 2024-02-11 21:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12656199 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1126-003, C0-01-08 |  | FM008 |  | 2024-02-20 19:55 | 2024-02-20 20:55 | 2024-02-21 20:55 | 24 | 2024-02-20 20:00 | 2024-02-20 21:55 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 95217 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12408838 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH FAULTY -- C0-01-08 |  | FM008 |  | 2023-11-24 07:47 | 2023-11-24 08:47 | 2023-11-25 08:47 | 24 | 2023-11-24 07:55 | 2023-11-24 10:35 | 160 | 320 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 138627 | 17053 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-12429552 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-C0-01-08 |  | FM008 |  | 2023-12-01 07:10 | 2023-12-01 08:10 | 2023-12-02 08:10 | 24 | 2023-12-01 07:15 | 2023-12-01 17:00 | 585 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-10258589 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003 – RETURN DUCT INSULATION DAMAGED – C0-01-08 |  | FM008 |  | 2022-03-16 19:23 | 2022-03-16 20:23 | 2022-03-17 20:23 | 24 | 2022-03-16 19:30 | 2022-03-16 21:10 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10749697 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AC TOO HOT C1-01-15 |  | FM008 |  | 2022-06-15 17:19 | 2022-06-15 17:49 | 2022-06-15 21:49 | 4 | 2022-06-15 17:23 | 2022-06-15 18:00 | 37 | 37 | 1 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | 82565 | Karimova, Ms. Ramziya | N - - - |  | Voice Communication
| CM-2023-11693639 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | AHU-A1126-003 – FILTER DIRTY – C3-01-20 |  | FM008 |  | 2023-04-20 19:21 | 2023-04-20 20:21 | 2023-04-21 20:21 | 24 | 2023-04-20 19:25 | 2023-04-20 23:30 | 245 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10142207 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-003 C0-01-08 |  | FM008 |  | 2022-02-14 13:16 | 2022-02-14 14:16 | 2022-02-15 14:16 | 24 | 2022-02-14 13:20 | 2022-02-14 15:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 85125 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11513796 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-03-04 19:01 | 2023-03-04 20:01 | 2023-03-05 20:01 | 24 | 2023-03-04 19:10 | 2023-03-04 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11932393 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-06-27 07:06 | 2023-06-27 08:06 | 2023-06-28 08:06 | 24 | 2023-06-27 07:15 | 2023-06-27 09:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11933505 | ASD-COC-GFL001-AHU097 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - C0-01-08 |  | FM008 |  | 2023-06-28 08:31 | 2023-06-28 09:31 | 2023-06-29 09:31 | 24 | 2023-06-28 08:35 | 2023-06-28 17:05 | 510 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10223376 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-01-08 |  | FM008 |  | 2022-03-06 16:16 | 2022-03-06 17:16 | 2022-03-07 17:16 | 24 | 2022-03-06 16:25 | 2022-03-06 18:40 | 135 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11303230 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED AHU-A1126-005 |  | FM008 |  | 2022-12-24 08:52 | 2022-12-24 09:52 | 2022-12-25 09:52 | 24 | 2022-12-24 09:00 | 2022-12-24 10:30 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2023-11362122 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - (AHU-A1126-005) - AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-01-09 19:59 | 2023-01-09 20:59 | 2023-01-10 20:59 | 24 | 2023-01-09 20:05 | 2023-01-09 22:05 | 120 | 120 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11783666 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU-A1126-005 ACCESS DOOR AIR LEAKAGE C0-01-08 |  | FM008 |  | 2023-05-12 19:16 | 2023-05-12 20:16 | 2023-05-13 20:16 | 24 | 2023-05-12 19:20 | 2023-05-12 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11972736 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY |  | FM008 |  | 2023-07-12 19:56 | 2023-07-12 20:56 | 2023-07-13 20:56 | 24 | 2023-07-12 20:00 | 2023-07-12 22:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2024-12526661 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-005 – C0-01-08 |  | FM008 |  | 2024-01-01 21:15 | 2024-01-01 22:15 | 2024-01-02 22:15 | 24 | 2024-01-01 21:20 | 2024-01-01 23:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12728955 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-01-08 |  | FM008 |  | 2024-03-11 07:21 | 2024-03-11 08:21 | 2024-03-12 08:21 | 24 | 2024-03-11 07:30 | 2024-03-11 10:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2024-12799108 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -C0-01-08 |  | FM008 |  | 2024-04-06 08:33 | 2024-04-06 09:33 | 2024-04-07 09:33 | 24 | 2024-04-06 08:40 | 2024-04-06 17:00 | 500 | 185 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12847086 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C0-01-08 |  | FM008 |  | 2024-04-22 19:22 | 2024-04-22 20:22 | 2024-04-23 20:22 | 24 | 2024-04-22 19:30 | 2024-04-22 21:45 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2022-11190544 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING -AHU-A1126-005)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-11-14 13:50 | 2022-11-14 14:50 | 2022-11-15 14:50 | 24 | 2022-11-14 14:00 | 2022-11-14 16:04 | 124 | 183 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17336 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12322702 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU-A1126-005 FILTER DIRY – C0-01-08 |  | FM008 |  | 2023-10-25 07:08 | 2023-10-25 08:08 | 2023-10-26 08:08 | 24 | 2023-10-25 07:10 | 2023-10-25 16:30 | 560 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12384881 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - AIR HANDLING UNIT 098 (TAG NO:AHU-A1126-005)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-11-16 00:03 | 2023-11-16 01:03 | 2023-11-17 01:03 | 24 | 2023-11-16 00:10 | 2023-11-16 02:55 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 119320 | 87807 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-11806767 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU-A1126-005 AHU CABIN LAMP NOT WORKING |  | FM008 |  | 2023-05-20 01:15 | 2023-05-20 02:15 | 2023-05-21 02:15 | 24 | 2023-05-20 01:20 | 2023-05-20 03:00 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12229989 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – C0-01-08 |  | FM008 |  | 2023-09-26 22:33 | 2023-09-26 23:33 | 2023-09-27 23:33 | 24 | 2023-09-26 22:40 | 2023-09-27 01:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 87807 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12670528 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1126-005, C0-01-08 |  | FM008 |  | 2024-02-20 19:55 | 2024-02-20 20:55 | 2024-02-21 20:55 | 24 | 2024-02-20 20:00 | 2024-02-20 21:50 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12821585 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C0-01-08 |  | FM008 |  | 2024-04-10 20:05 | 2024-04-10 21:05 | 2024-04-11 21:05 | 24 | 2024-04-10 20:15 | 2024-04-10 23:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10142209 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-005 C0-01-08 |  | FM008 |  | 2022-02-14 13:21 | 2022-02-14 14:21 | 2022-02-15 14:21 | 24 | 2022-02-14 13:30 | 2022-02-14 15:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 85125 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11513797 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-03-04 19:04 | 2023-03-04 20:04 | 2023-03-05 20:04 | 24 | 2023-03-04 19:10 | 2023-03-04 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11933506 | ASD-COC-GFL001-AHU098 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - C0-01-08 |  | FM008 |  | 2023-06-28 08:32 | 2023-06-28 09:32 | 2023-06-29 09:32 | 24 | 2023-06-28 08:35 | 2023-06-28 17:05 | 510 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10655904 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 – DP1 FILTER ALARM-- |  | FM008 |  | 2022-05-14 15:56 | 2022-05-14 16:56 | 2022-05-15 16:56 | 24 | 2022-05-14 16:00 | 2022-05-14 17:45 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10707656 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 DUCT INSULATION DAMAGED C0-01-20 |  | FM008 |  | 2022-05-30 08:35 | 2022-05-30 09:35 | 2022-05-31 09:35 | 24 | 2022-05-30 08:40 | 2022-05-30 11:40 | 180 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10792821 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – AHU-A1126-006 – C0-01-20 |  | FM008 |  | 2022-06-30 07:05 | 2022-06-30 08:05 | 2022-07-01 08:05 | 24 | 2022-06-30 07:14 | 2022-06-30 11:45 | 271 | 269 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11112087 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 099 SUPPLY BUCT INSTALLATION DAMAGE,-TAG NO:AHU-A1126-006. |  | FM008 |  | 2022-10-16 15:09 | 2022-10-16 16:09 | 2022-10-17 16:09 | 24 | 2022-10-16 15:15 | 2022-10-16 17:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11250699 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C0-01-20 |  | FM008 |  | 2022-12-04 20:04 | 2022-12-04 21:04 | 2022-12-05 21:04 | 24 | 2022-12-04 20:10 | 2022-12-04 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11579107 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1126-006)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-03-21 13:38 | 2023-03-21 14:38 | 2023-03-22 14:38 | 24 | 2023-03-21 13:45 | 2023-03-21 16:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM1933 | Shukla, Mr. Ashok Kumar | N - - - |  | Voice Communication
| CM-2023-12345996 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | C0-01-20-DUCT INSULATION DAMAGED -AIR HANDLING UNIT 099 (TAG NO:AHU-A1126-006-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-11-02 19:49 | 2023-11-02 20:49 | 2023-11-03 20:49 | 24 | 2023-11-02 20:00 | 2023-11-02 22:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-11233658 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 – COOLING COIL DIRTY - C0-01-20 |  | FM008 |  | 2022-12-03 07:15 | 2022-12-03 08:15 | 2022-12-04 08:15 | 24 | 2022-12-03 07:20 | 2022-12-03 11:20 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11332913 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - (AHU-A1126-006)- AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-01-01 21:31 | 2023-01-01 22:31 | 2023-01-02 22:31 | 24 | 2023-01-01 21:40 | 2023-01-01 23:55 | 135 | 405 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 132112 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11698830 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AHU-A1126-006 – C0 01 20 |  | FM008 |  | 2023-04-25 00:38 | 2023-04-25 01:38 | 2023-04-26 01:38 | 24 | 2023-04-25 00:45 | 2023-04-25 02:00 | 75 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11908898 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 C0-01-20 FILTER DIRTY |  | FM008 |  | 2023-06-21 15:53 | 2023-06-21 16:53 | 2023-06-22 16:53 | 24 | 2023-06-21 16:00 | 2023-06-21 18:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11948926 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006-DUCT INSULATION DAMAGE -CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2023-07-07 15:05 | 2023-07-07 16:05 | 2023-07-08 16:05 | 24 | 2023-07-07 15:10 | 2023-07-07 18:40 | 210 | 200 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2024-12725999 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 C0-01-20 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-03-11 07:15 | 2024-03-11 08:15 | 2024-03-12 08:15 | 24 | 2024-03-11 07:20 | 2024-03-11 13:35 | 375 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11654758 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AHU-A1126-006 - C0-01-20 |  | FM008 |  | 2023-04-12 19:21 | 2023-04-12 20:21 | 2023-04-13 20:21 | 24 | 2023-04-12 19:30 | 2023-04-12 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11877614 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-006 - C0-01-20 |  | FM008 |  | 2023-06-13 12:44 | 2023-06-13 13:44 | 2023-06-14 13:44 | 24 | 2023-06-13 12:50 | 2023-06-13 15:00 | 130 | 520 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | BMS
| CM-2023-11930694 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED , AHU-A1126-006, C0-01-20 |  | FM008 |  | 2023-06-25 19:07 | 2023-06-25 20:07 | 2023-06-26 20:07 | 24 | 2023-06-25 19:15 | 2023-06-25 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12298957 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | ABNORMAL NOISY (AIR HANDLING UNIT)-C0-01-20 |  | FM008 |  | 2023-10-18 14:23 | 2023-10-18 15:23 | 2023-10-19 15:23 | 24 | 2023-10-18 14:30 | 2023-10-18 17:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 77406 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2024-12839294 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AC TOO HOT INSIDE RESTAURANT AREA SN-1053 |  | FM008 |  | 2024-04-21 11:06 | 2024-04-21 12:06 | 2024-04-22 12:06 | 24 | 2024-04-21 11:15 | 2024-04-21 12:00 | 45 | 45 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 603183 | ASHKAR | N - - - |  | Voice Communication
| CM-2023-12383184 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1126-006)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001- C0-01-20 |  | FM008 |  | 2023-11-16 07:42 | 2023-11-16 08:42 | 2023-11-17 08:42 | 24 | 2023-11-16 07:50 | 2023-11-16 14:00 | 370 | 545 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12513279 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-01-20 |  | FM008 |  | 2023-12-28 21:14 | 2023-12-28 22:14 | 2023-12-29 22:14 | 24 | 2023-12-28 21:20 | 2023-12-29 00:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2024-12629898 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-006 – C0-01-20 |  | FM008 |  | 2024-02-08 10:58 | 2024-02-08 11:58 | 2024-02-09 11:58 | 24 | 2024-02-08 11:05 | 2024-02-08 13:55 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12644843 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C0-01-20 |  | FM008 |  | 2024-02-12 19:44 | 2024-02-12 20:44 | 2024-02-13 20:44 | 24 | 2024-02-12 19:50 | 2024-02-12 21:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12820582 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-006, C0-01-20 |  | FM008 |  | 2024-04-10 14:08 | 2024-04-10 15:08 | 2024-04-11 15:08 | 24 | 2024-04-10 14:15 | 2024-04-10 17:30 | 195 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2022-10066231 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | CHILLED WATER LINE FADED-AIR HANDLING UNIT 099 (TAG NO:AHU-A1126-006)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 001 |  | FM008 |  | 2022-01-19 14:14 | 2022-01-19 15:14 | 2022-01-20 15:14 | 24 | 2022-01-19 14:20 | 2022-01-19 16:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 55709 |  |  | FM5678 | Muhamedkwaja Muhamed Yahya , Mr. Alumkoottathil | N - - - |  | Voice Communication
| CM-2022-10934638 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1126-006 |  | FM008 |  | 2022-08-12 19:50 | 2022-08-12 20:50 | 2022-08-13 20:50 | 24 | 2022-08-12 19:55 | 2022-08-12 20:30 | 35 | 35 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - |  | BMS
| CM-2022-9967014 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE AHU-A1126-006 |  | FM008 |  | 2022-01-02 20:33 | 2022-01-02 21:33 | 2022-01-03 21:33 | 24 | 2022-01-02 20:40 | 2022-01-02 22:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10194383 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 – DP1 FILTER ALARM – MEC ROOM C0-01-20 |  | FM008 |  | 2022-02-27 07:57 | 2022-02-27 08:57 | 2022-02-28 08:57 | 24 | 2022-02-27 08:05 | 2022-02-27 17:10 | 545 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 105233 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11427430 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 DUCT INSULATION DAMAGED C0-01-20 |  | FM008 |  | 2023-02-04 19:22 | 2023-02-04 20:22 | 2023-02-05 20:22 | 24 | 2023-02-04 19:30 | 2023-02-04 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11428901 | ASD-COC-GFL001-AHU099 | AIR HANDLING UNIT-05 | AHU-A1126-006 AHU CABLE LAMP NOT WORKING C0-01-20 |  | FM008 |  | 2023-02-05 00:14 | 2023-02-05 01:14 | 2023-02-06 01:14 | 24 | 2023-02-05 00:20 | 2023-02-05 02:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 001 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 89127 | 133396 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10045439 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | CHILLED WATER PAINT FADED |  | FM008 |  | 2022-01-13 21:55 | 2022-01-13 22:55 | 2022-01-14 22:55 | 24 | 2022-01-13 22:00 | 2022-01-13 23:55 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68060 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11822863 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-05-24 10:12 | 2023-05-24 11:12 | 2023-05-25 11:12 | 24 | 2023-05-24 10:15 | 2023-05-24 13:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12175520 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED - AHU-A1126-007 – C0-02-06 |  | FM008 |  | 2023-09-10 16:38 | 2023-09-10 17:38 | 2023-09-11 17:38 | 24 | 2023-09-10 16:45 | 2023-09-10 18:50 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 106973 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2024-12819646 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C0-02-06 |  | FM008 |  | 2024-04-09 07:40 | 2024-04-09 08:40 | 2024-04-10 08:40 | 24 | 2024-04-09 07:45 | 2024-04-09 10:05 | 140 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11179301 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AHU-A1126-007 – C0-02-06 |  | FM008 |  | 2022-11-10 11:39 | 2022-11-10 12:39 | 2022-11-11 12:39 | 24 | 2022-11-10 11:45 | 2022-11-10 15:00 | 195 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2022-11197924 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | INSIDE AHU LIGHT NOT ILLUMINATING - AHU-A1126-007 - MECHANICAL ROOM C0-02-06 |  | FM008 |  | 2022-11-19 19:06 | 2022-11-19 20:06 | 2022-11-20 20:06 | 24 | 2022-11-19 19:10 | 2022-11-19 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11877922 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-007 – C0-02-06 |  | FM008 |  | 2023-06-14 13:52 | 2023-06-14 14:52 | 2023-06-15 14:52 | 24 | 2023-06-14 14:00 | 2023-06-14 17:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10958454 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-007 – C0-02-06 |  | FM008 |  | 2022-08-22 07:45 | 2022-08-22 08:45 | 2022-08-23 08:45 | 24 | 2022-08-22 07:50 | 2022-08-22 11:20 | 210 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11437928 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | AHU-A1126-007 – DUCT ACCESS DOOR AIR LEAKAGE – C0-02-06 |  | FM008 |  | 2023-02-06 20:34 | 2023-02-06 21:34 | 2023-02-07 21:34 | 24 | 2023-02-06 20:40 | 2023-02-06 22:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11610294 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C0-02-06 |  | FM008 |  | 2023-04-02 07:06 | 2023-04-02 08:06 | 2023-04-03 08:06 | 24 | 2023-04-02 07:15 | 2023-04-02 10:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11752594 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | AHU-A1126-007- DUCT INSULATION DAMAGED-C0-02-06 |  | FM008 |  | 2023-04-30 07:09 | 2023-04-30 08:09 | 2023-05-01 08:09 | 24 | 2023-04-30 07:20 | 2023-04-30 09:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12614564 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | AHU-DUCT INSULATION DAMAGE -(C0-02-06) |  | FM008 |  | 2024-02-02 19:19 | 2024-02-02 20:19 | 2024-02-03 20:19 | 24 | 2024-02-02 19:25 | 2024-02-02 22:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12713380 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AIR HANDLING UNIT 100 (TAG NO:AHU-A1126-007)-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2024-03-07 07:36 | 2024-03-07 08:36 | 2024-03-08 08:36 | 24 | 2024-03-07 07:40 | 2024-03-07 16:10 | 510 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12461439 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE -- AIR HANDLING UNIT 100 (TAG NO:AHU-A1126-007)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-12-11 14:39 | 2023-12-11 15:39 | 2023-12-12 15:39 | 24 | 2023-12-11 14:45 | 2023-12-11 17:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12510571 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | AHU-A1126-007 ACCESS DOOR AIR LEAKAGE - AIR HANDLING UNIT 100 (TAG NO:AHU-A1126-007)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-12-26 19:10 | 2023-12-26 20:10 | 2023-12-27 20:10 | 24 | 2023-12-26 19:15 | 2023-12-26 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 119320 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11297975 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | AHU-A1126-007 – DUCT INSULATION DAMAGED – C0-02-06 |  | FM008 |  | 2022-12-20 20:28 | 2022-12-20 21:28 | 2022-12-21 21:28 | 24 | 2022-12-20 20:38 | 2022-12-20 23:40 | 182 | 546 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11668712 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-04-16 07:11 | 2023-04-16 08:11 | 2023-04-17 08:11 | 24 | 2023-04-16 07:20 | 2023-04-16 13:30 | 370 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-10032864 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-01-08 21:54 | 2022-01-08 22:54 | 2022-01-09 22:54 | 24 | 2022-01-08 22:00 | 2022-01-08 23:55 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10154231 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-007 – C0-02-06 |  | FM008 |  | 2022-02-20 07:27 | 2022-02-20 08:27 | 2022-02-21 08:27 | 24 | 2022-02-20 07:35 | 2022-02-20 10:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11959628 | ASD-COC-GFL002-AHU100 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-007, C0-02-06 |  | FM008 |  | 2023-07-09 07:04 | 2023-07-09 08:04 | 2023-07-10 08:04 | 24 | 2023-07-09 07:05 | 2023-07-09 10:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10084646 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1126-008 – C0-02-16 |  | FM008 |  | 2022-01-28 19:58 | 2022-01-28 20:58 | 2022-01-29 20:58 | 24 | 2022-01-28 20:10 | 2022-01-28 22:30 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10154098 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED -C0-02-16 |  | FM008 |  | 2022-02-19 11:33 | 2022-02-19 12:33 | 2022-02-20 12:33 | 24 | 2022-02-19 11:40 | 2022-02-19 14:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10777589 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008 – DP1 FILTER ALARM – C0-02-16 |  | FM008 |  | 2022-06-26 08:13 | 2022-06-26 09:13 | 2022-06-27 09:13 | 24 | 2022-06-26 08:20 | 2022-06-26 12:40 | 260 | 205 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11219655 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED - AHU-A1126-008 – C0-02-16 |  | FM008 |  | 2022-11-26 21:39 | 2022-11-26 22:39 | 2022-11-27 22:39 | 24 | 2022-11-26 21:45 | 2022-11-26 23:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11879310 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | LIGHTENING SWITCH DAMAGED - AHU-A1126-008 - C0-02-16 |  | FM008 |  | 2023-06-12 10:25 | 2023-06-12 11:25 | 2023-06-13 11:25 | 24 | 2023-06-12 10:34 | 2023-06-12 12:31 | 117 | 234 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12600021 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – C0-02-16 |  | FM008 |  | 2024-01-31 10:44 | 2024-01-31 11:44 | 2024-02-01 11:44 | 24 | 2024-01-31 10:50 | 2024-01-31 12:30 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11593546 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-02-16 |  | FM008 |  | 2023-03-26 10:20 | 2023-03-26 11:20 | 2023-03-27 11:20 | 24 | 2023-03-26 10:30 | 2023-03-26 13:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12045243 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AHU-A1126-008 – C0-02-16 |  | FM008 |  | 2023-08-05 10:40 | 2023-08-05 11:40 | 2023-08-06 11:40 | 24 | 2023-08-05 10:50 | 2023-08-05 13:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12130392 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED-AIR HANDLING UNIT 101 (TAG NO:AHU-A1126-008)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-08-30 22:44 | 2023-08-30 23:44 | 2023-08-31 23:44 | 24 | 2023-08-30 22:50 | 2023-08-31 00:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-12169903 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT IS FAULTY |  | FM008 |  | 2023-09-10 12:33 | 2023-09-10 13:33 | 2023-09-11 13:33 | 24 | 2023-09-10 12:40 | 2023-09-10 15:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | TIMER FAULTY | TIMER NOT WORKING | SWITCH HAS BEEN REPLACED | 68060 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12647738 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1126-008, C0-02-16 |  | FM008 |  | 2024-02-12 19:59 | 2024-02-12 20:59 | 2024-02-13 20:59 | 24 | 2024-02-12 20:05 | 2024-02-12 23:55 | 230 | 235 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2024-12712515 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY,AHU-A1126-008, C0-02-16 |  | FM008 |  | 2024-03-06 22:39 | 2024-03-06 23:39 | 2024-03-07 23:39 | 24 | 2024-03-06 22:45 | 2024-03-07 01:25 | 160 | 320 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 124475 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12757930 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008 DUCT INSULATION DAMAGED C0-02-16 |  | FM008 |  | 2024-03-24 08:23 | 2024-03-24 09:23 | 2024-03-25 09:23 | 24 | 2024-03-24 08:30 | 2024-03-24 11:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11166419 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING AHU-A1126-008 |  | FM008 |  | 2022-11-06 10:30 | 2022-11-06 11:30 | 2022-11-07 11:30 | 24 | 2022-11-06 10:39 | 2022-11-06 12:08 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106972 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11364240 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008 COOLING COIL DIRTY |  | FM008 |  | 2023-01-11 19:12 | 2023-01-11 20:12 | 2023-01-12 20:12 | 24 | 2023-01-11 19:15 | 2023-01-11 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11752595 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008- DUCT INSULATION DAMAGED-C0-02-16- |  | FM008 |  | 2023-04-30 07:10 | 2023-04-30 08:10 | 2023-05-01 08:10 | 24 | 2023-04-30 07:20 | 2023-04-30 09:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12690899 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008 C0-02-16 FILTER DIRTY |  | FM008 |  | 2024-02-29 08:28 | 2024-02-29 09:28 | 2024-03-01 09:28 | 24 | 2024-02-29 08:35 | 2024-02-29 13:40 | 305 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12236001 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | FILTER DIRTY -C0-01-16 |  | FM008 |  | 2023-09-30 19:12 | 2023-09-30 20:12 | 2023-10-01 20:12 | 24 | 2023-09-30 19:20 | 2023-09-30 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 87807 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2023-12468827 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE -- C0-02-16 |  | FM008 |  | 2023-12-13 20:27 | 2023-12-13 21:27 | 2023-12-14 21:27 | 24 | 2023-12-13 20:35 | 2023-12-13 23:00 | 145 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 138627 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12592414 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2024-01-25 16:14 | 2024-01-25 17:14 | 2024-01-26 17:14 | 24 | 2024-01-25 16:20 | 2024-01-25 18:05 | 105 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-10281561 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | RETURN ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-03-26 10:25 | 2022-03-26 11:25 | 2022-03-27 11:25 | 24 | 2022-03-26 10:34 | 2022-03-26 12:34 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95216 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11170889 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED – C0-02-16 |  | FM008 |  | 2022-11-07 19:47 | 2022-11-07 20:47 | 2022-11-08 20:47 | 24 | 2022-11-07 19:50 | 2022-11-07 21:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10032159 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE AHU-A1126-008 C0-02-16 |  | FM008 |  | 2022-01-08 00:04 | 2022-01-08 01:04 | 2022-01-09 01:04 | 24 | 2022-01-08 00:10 | 2022-01-08 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 85125 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10772460 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-06-23 11:37 | 2022-06-23 12:37 | 2022-06-24 12:37 | 24 | 2022-06-23 11:40 | 2022-06-23 17:00 | 320 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11957166 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | AHU-A1126-008 ACCESS DOOR AIR LEAK C0-02-16 |  | FM008 |  | 2023-07-06 19:07 | 2023-07-06 20:07 | 2023-07-07 20:07 | 24 | 2023-07-06 19:15 | 2023-07-06 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12794247 | ASD-COC-GFL002-AHU101 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED AHU-A1126-008 -C0-02-16 |  | FM008 |  | 2024-04-02 20:27 | 2024-04-02 21:27 | 2024-04-03 21:27 | 24 | 2024-04-02 20:35 | 2024-04-02 23:20 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2022-10933013 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU SUPPLY DUCT INSULATION DAMAGED - CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2022-08-13 22:42 | 2022-08-13 23:42 | 2022-08-14 23:42 | 24 | 2022-08-13 22:50 | 2022-08-14 00:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 55709 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11179245 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | SUPPLY GRILL DIRTY - AHU-A1126-025 – C0-02-06 |  | FM008 |  | 2022-11-10 07:16 | 2022-11-10 08:16 | 2022-11-11 08:16 | 24 | 2022-11-10 07:20 | 2022-11-10 12:00 | 280 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM5803 | Tiwari, Mr. Sanjeed Kumar | N - - - |  | Voice Communication
| CM-2022-11219656 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AC SUPPLY GRILL DIRTY - AHU-A1126-025 – C0-02-06 |  | FM008 |  | 2022-11-26 21:40 | 2022-11-26 22:40 | 2022-11-27 22:40 | 24 | 2022-11-26 21:45 | 2022-11-26 23:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11853697 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-025-FM10657-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2023-06-05 14:34 | 2023-06-05 15:34 | 2023-06-06 15:34 | 24 | 2023-06-05 14:40 | 2023-06-05 17:10 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 94954 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-11905025 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 FILTER DIRTY C0-02-06 |  | FM008 |  | 2023-06-19 14:36 | 2023-06-19 15:36 | 2023-06-20 15:36 | 24 | 2023-06-19 14:40 | 2023-06-19 16:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 121959 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12322760 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025-FILTER DIRTY-C0-02-06) |  | FM008 |  | 2023-10-25 09:14 | 2023-10-25 10:14 | 2023-10-26 10:14 | 24 | 2023-10-25 09:20 | 2023-10-25 15:13 | 353 | 224 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12769280 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 C0-02-06 GRILL DIRTY |  | FM008 |  | 2024-03-26 20:35 | 2024-03-26 21:35 | 2024-03-27 21:35 | 24 | 2024-03-26 20:40 | 2024-03-26 23:15 | 155 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 138627 | 95217 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | E-mail
| CM-2022-10956719 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 SUPPLY GRILL DIRTY |  | FM008 |  | 2022-08-20 22:20 | 2022-08-20 23:20 | 2022-08-21 23:20 | 24 | 2022-08-20 22:25 | 2022-08-20 23:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11170682 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1126-025)--CONCOURSE C-GROUND FLOOR AREA 002-C0-02-06 |  | FM008 |  | 2022-11-07 00:10 | 2022-11-07 01:10 | 2022-11-08 01:10 | 24 | 2022-11-07 00:15 | 2022-11-07 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11230635 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | COOLING COL DIRTY - AHU-A1126-027 – C0-03-06 |  | FM008 |  | 2022-11-30 00:06 | 2022-11-30 01:06 | 2022-12-01 01:06 | 24 | 2022-11-30 00:10 | 2022-11-30 03:10 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11350336 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED – C0-02-06 - AHU-A1126-025 |  | FM008 |  | 2023-01-06 00:05 | 2023-01-06 01:05 | 2023-01-07 01:05 | 24 | 2023-01-06 00:15 | 2023-01-06 03:45 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11610043 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY – C0-02-06 |  | FM008 |  | 2023-04-01 07:05 | 2023-04-01 08:05 | 2023-04-02 08:05 | 24 | 2023-04-01 07:10 | 2023-04-01 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11876089 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 LIGHTNING FLEXIBLE CONNECTOR DAMAGED C0-02-06 |  | FM008 |  | 2023-06-11 16:19 | 2023-06-11 17:19 | 2023-06-12 17:19 | 24 | 2023-06-11 16:29 | 2023-06-11 18:55 | 146 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 77406 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12088583 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | FILTER DIRTY C0-02-06 AHU-A1126-025 |  | FM008 |  | 2023-08-14 08:36 | 2023-08-14 09:36 | 2023-08-15 09:36 | 24 | 2023-08-14 08:40 | 2023-08-14 14:05 | 325 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12469767 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-025 - MECHANICAL ROOM C0-02-06 |  | FM008 |  | 2023-12-14 08:49 | 2023-12-14 09:49 | 2023-12-15 09:49 | 24 | 2023-12-14 08:55 | 2023-12-14 11:55 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12686428 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-025, C0-02-06 |  | FM008 |  | 2024-02-26 07:59 | 2024-02-26 08:59 | 2024-02-27 08:59 | 24 | 2024-02-26 08:05 | 2024-02-26 11:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12778902 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2024-03-29 13:09 | 2024-03-29 14:09 | 2024-03-30 14:09 | 24 | 2024-03-29 13:10 | 2024-03-29 18:10 | 300 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-10874207 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 FILTER ALARM MECH C0-02-06 |  | FM008 |  | 2022-07-27 15:11 | 2022-07-27 16:11 | 2022-07-28 16:11 | 24 | 2022-07-27 15:15 | 2022-07-27 17:50 | 155 | 95 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11061427 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU LAMP NOT WORKING -C0-02-06 |  | FM008 |  | 2022-09-26 19:05 | 2022-09-26 20:05 | 2022-09-27 20:05 | 24 | 2022-09-26 19:15 | 2022-09-26 23:00 | 225 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11176164 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 - AHU SUPPLY GRILL DIRTY - C0-02-06 |  | FM008 |  | 2022-11-08 19:32 | 2022-11-08 20:32 | 2022-11-09 20:32 | 24 | 2022-11-08 19:40 | 2022-11-08 21:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11232655 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 – COOLING COIL DIRTY-- C0-02-06 |  | FM008 |  | 2022-11-30 19:35 | 2022-11-30 20:35 | 2022-12-01 20:35 | 24 | 2022-11-30 19:45 | 2022-11-30 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11273415 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | DP 1 AND DP3 FILTER ALARM-AHU-A1126-025)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2022-12-16 11:26 | 2022-12-16 12:26 | 2022-12-17 12:26 | 24 | 2022-12-16 11:35 | 2022-12-16 15:00 | 205 | 410 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11680851 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-04-17 19:11 | 2023-04-17 20:11 | 2023-04-18 20:11 | 24 | 2023-04-17 19:20 | 2023-04-17 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12452899 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU CABIN LAMP IS FAULTY |  | FM008 |  | 2023-12-10 00:16 | 2023-12-10 01:16 | 2023-12-11 01:16 | 24 | 2023-12-10 00:25 | 2023-12-10 03:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2023-12463282 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C0-02-06 |  | FM008 |  | 2023-12-10 22:12 | 2023-12-10 23:12 | 2023-12-11 23:12 | 24 | 2023-12-10 22:20 | 2023-12-11 00:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12714439 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-025 |  | FM008 |  | 2024-03-09 07:06 | 2024-03-09 08:06 | 2024-03-10 08:06 | 24 | 2024-03-09 07:10 | 2024-03-09 15:55 | 525 | 500 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12537802 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 DUCT INSULATION DAMAGED |  | FM008 |  | 2024-01-06 20:03 | 2024-01-06 21:03 | 2024-01-07 21:03 | 24 | 2024-01-06 20:10 | 2024-01-06 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2022-10160509 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | SUPPLY DUCT AC GRILL DIRTY - AHU-A1126-025 – C0-02-06 |  | FM008 |  | 2022-02-22 05:02 | 2022-02-22 06:02 | 2022-02-23 06:02 | 24 | 2022-02-22 05:10 | 2022-02-22 06:45 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2022-10221568 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | Ahu-a1126-025- SUPPLY GRILL DIRTY – C0-02-06 |  | FM008 |  | 2022-03-06 13:31 | 2022-03-06 14:31 | 2022-03-07 14:31 | 24 | 2022-03-06 13:35 | 2022-03-06 16:10 | 155 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2022-10772049 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | SUPPLY DUCT AC GRILL DIRTY |  | FM008 |  | 2022-06-21 13:51 | 2022-06-21 14:51 | 2022-06-22 14:51 | 24 | 2022-06-21 14:00 | 2022-06-21 16:20 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 95216 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10988634 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 FILTER ALARM |  | FM008 |  | 2022-08-29 00:44 | 2022-08-29 01:44 | 2022-08-30 01:44 | 24 | 2022-08-29 00:50 | 2022-08-29 05:42 | 292 | 119 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11060756 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025 DP3 FILTER ALARM C0-02-06 |  | FM008 |  | 2022-09-28 13:26 | 2022-09-28 14:26 | 2022-09-29 14:26 | 24 | 2022-09-28 13:35 | 2022-09-28 16:25 | 170 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10032131 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY |  | FM008 |  | 2022-01-07 22:00 | 2022-01-07 23:00 | 2022-01-08 23:00 | 24 | 2022-01-07 22:04 | 2022-01-07 23:30 | 86 | 258 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 95216 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10066662 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-21 03:25 | 2022-01-21 04:25 | 2022-01-22 04:25 | 24 | 2022-01-21 03:30 | 2022-01-21 07:00 | 210 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68060 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | BMS
| CM-2022-10770753 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU-A1126-025-DP3 FILTER ALARM |  | FM008 |  | 2022-06-20 11:10 | 2022-06-20 12:10 | 2022-06-21 12:10 | 24 | 2022-06-20 11:15 | 2022-06-20 13:30 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95217 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-12183942 | ASD-COC-GFL002-AHU117 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY -C0-02-06 |  | FM008 |  | 2023-09-12 19:05 | 2023-09-12 20:05 | 2023-09-13 20:05 | 24 | 2023-09-12 19:10 | 2023-09-12 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 17053 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2022-10042014 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY – C0-02-16 |  | FM008 |  | 2022-01-11 00:04 | 2022-01-11 01:04 | 2022-01-12 01:04 | 24 | 2022-01-11 00:10 | 2022-01-11 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-11158306 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 – AHU CABIN LAMP FAULTY -C0-02-16 |  | FM008 |  | 2022-11-01 15:30 | 2022-11-01 16:30 | 2022-11-02 16:30 | 24 | 2022-11-01 15:40 | 2022-11-01 17:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17154 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11179246 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY GRILL DIRTY - AHU-A1126-026 – C0-02-16 |  | FM008 |  | 2022-11-10 07:17 | 2022-11-10 08:17 | 2022-11-11 08:17 | 24 | 2022-11-10 07:25 | 2022-11-10 12:00 | 275 | 335 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM5803 | SANJEED KUMAR TIWARI, | N - - - |  | Voice Communication
| CM-2022-11188745 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -AHU-A1126-026)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2022-11-13 12:33 | 2022-11-13 13:33 | 2022-11-14 13:33 | 24 | 2022-11-13 12:40 | 2022-11-13 15:05 | 145 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | E-mail
| CM-2023-11342201 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AC SUPPLY GRILL DIRTY – C0-02-16 |  | FM008 |  | 2023-01-02 19:09 | 2023-01-02 20:09 | 2023-01-03 20:09 | 24 | 2023-01-02 19:15 | 2023-01-02 21:30 | 135 | 405 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-12064029 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-08-08 20:14 | 2023-08-08 21:14 | 2023-08-09 21:14 | 24 | 2023-08-08 20:20 | 2023-08-08 22:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12278710 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-10 19:06 | 2023-10-10 20:06 | 2023-10-11 20:06 | 24 | 2023-10-10 19:15 | 2023-10-10 21:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12322762 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026-FILTER DIRTY (C0-02-16) |  | FM008 |  | 2023-10-25 09:18 | 2023-10-25 10:18 | 2023-10-26 10:18 | 24 | 2023-10-25 09:20 | 2023-10-25 16:28 | 428 | 224 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11170683 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1126-026)-CONCOURSE C-GROUND FLOOR AREA 002- C0-02-16 |  | FM008 |  | 2022-11-07 00:12 | 2022-11-07 01:12 | 2022-11-08 01:12 | 24 | 2022-11-07 00:20 | 2022-11-07 04:15 | 235 | 350 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11232500 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | C0-02-16 COOLING COIL DIRTY |  | FM008 |  | 2022-11-30 08:45 | 2022-11-30 09:45 | 2022-12-01 09:45 | 24 | 2022-11-30 08:55 | 2022-11-30 13:00 | 245 | 735 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11345296 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED – AHU-A1126-026 – C0-02-16 |  | FM008 |  | 2023-01-04 12:36 | 2023-01-04 13:36 | 2023-01-05 13:36 | 24 | 2023-01-04 12:40 | 2023-01-04 16:10 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11673097 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 – FILTER DIRTY-- |  | FM008 |  | 2023-04-16 19:08 | 2023-04-16 20:08 | 2023-04-17 20:08 | 24 | 2023-04-16 19:15 | 2023-04-16 21:45 | 150 | 600 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94953 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12163923 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY – C0-02-16 |  | FM008 |  | 2023-09-08 12:04 | 2023-09-08 13:04 | 2023-09-09 13:04 | 24 | 2023-09-08 12:10 | 2023-09-08 18:00 | 350 | 455 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-12425783 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | duct insulation damaged |  | FM008 |  | 2023-11-27 16:38 | 2023-11-27 17:38 | 2023-11-28 17:38 | 24 | 2023-11-27 16:45 | 2023-11-27 18:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12846204 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM -PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP6.CONC0216.AHU026.SYSALM.DP1 / |  | FM008 |  | 2024-04-24 09:40 | 2024-04-24 10:40 | 2024-04-25 10:40 | 24 | 2024-04-24 09:45 | 2024-04-24 12:10 | 145 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 95216 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10874209 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 FILTER ALARM |  | FM008 |  | 2022-07-27 15:12 | 2022-07-27 16:12 | 2022-07-28 16:12 | 24 | 2022-07-27 15:20 | 2022-07-27 18:40 | 200 | 95 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10976331 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | DP1 & DP3 FILTER ALARM - MEC ROOM C0-02-16 |  | FM008 |  | 2022-08-28 09:53 | 2022-08-28 10:53 | 2022-08-29 10:53 | 24 | 2022-08-28 10:00 | 2022-08-28 12:50 | 170 | 395 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2022-11175972 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED – AHU-A1126-026 - C0-02-16 |  | FM008 |  | 2022-11-09 08:48 | 2022-11-09 09:48 | 2022-11-10 09:48 | 24 | 2022-11-09 09:00 | 2022-11-09 11:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17573 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11301679 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-25 08:20 | 2022-12-25 09:20 | 2022-12-26 09:20 | 24 | 2022-12-25 08:30 | 2022-12-25 11:30 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11429243 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 C0-02-16 SUPPLY AC GRILL DIRTY |  | FM008 |  | 2023-02-05 21:02 | 2023-02-05 22:02 | 2023-02-06 22:02 | 24 | 2023-02-05 21:10 | 2023-02-05 23:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 133396 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11759786 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY – C0-02-16 |  | FM008 |  | 2023-05-01 19:08 | 2023-05-01 20:08 | 2023-05-02 20:08 | 24 | 2023-05-01 19:15 | 2023-05-01 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11878317 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 – FILTER IS DIRTY – C0-02-16 |  | FM008 |  | 2023-06-12 14:36 | 2023-06-12 15:36 | 2023-06-13 15:36 | 24 | 2023-06-12 14:40 | 2023-06-12 16:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12144066 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED AHU-A1126-026 |  | FM008 |  | 2023-09-03 13:32 | 2023-09-03 14:32 | 2023-09-04 14:32 | 24 | 2023-09-03 13:40 | 2023-09-03 15:50 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68060 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12568049 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | FILTER DIRTY AIR HANDLING UNIT 118 (TAG NO:AHU-A1126-026)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 |  | FM008 |  | 2024-01-14 13:15 | 2024-01-14 14:15 | 2024-01-15 14:15 | 24 | 2024-01-14 13:20 | 2024-01-14 18:25 | 305 | 265 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 95217 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12615546 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AC SUPPLY GRILL DIRTY |  | FM008 |  | 2024-02-04 08:54 | 2024-02-04 09:54 | 2024-02-05 09:54 | 24 | 2024-02-04 09:00 | 2024-02-04 10:50 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-12476657 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1126-026, C0-02-16 |  | FM008 |  | 2023-12-15 07:55 | 2023-12-15 08:55 | 2023-12-16 08:55 | 24 | 2023-12-15 08:00 | 2023-12-15 14:02 | 362 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12681118 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-026, C0-02-16 |  | FM008 |  | 2024-02-25 11:25 | 2024-02-25 12:25 | 2024-02-26 12:25 | 24 | 2024-02-25 11:30 | 2024-02-25 14:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12694495 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 AC GRILL DIRTY |  | FM008 |  | 2024-03-02 19:31 | 2024-03-02 20:31 | 2024-03-03 20:31 | 24 | 2024-03-02 19:40 | 2024-03-02 22:30 | 170 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-10252524 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 SUPPLY GRILL DIRTY C0-02-16 |  | FM008 |  | 2022-03-14 23:27 | 2022-03-15 00:27 | 2022-03-16 00:27 | 24 | 2022-03-14 23:35 | 2022-03-15 01:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10653722 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AC SUPPLY GRILL DIRTY |  | FM008 |  | 2022-05-13 15:20 | 2022-05-13 16:20 | 2022-05-14 16:20 | 24 | 2022-05-13 15:30 | 2022-05-13 17:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2022-10772050 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY DUCT AC GRILL DIRTY |  | FM008 |  | 2022-06-21 13:51 | 2022-06-21 14:52 | 2022-06-22 14:52 | 24 | 2022-06-21 14:00 | 2022-06-21 16:20 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2023-11604408 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | SUPPLY AIR GRILL DIRTY - AHU-A1126-026 - MECHANICAL ROOM C0-02-16 |  | FM008 |  | 2023-03-27 19:27 | 2023-03-27 20:27 | 2023-03-28 20:27 | 24 | 2023-03-27 19:30 | 2023-03-27 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-10824788 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 –AHU SUPPLY GRILL DIRTY |  | FM008 |  | 2022-07-08 01:14 | 2022-07-08 02:14 | 2022-07-09 02:14 | 24 | 2022-07-08 01:20 | 2022-07-08 03:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10950813 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | AHU-A1126-026 – SUPPLY DUCT INSULATION DAMAGED – C0-02-16 |  | FM008 |  | 2022-08-14 23:03 | 2022-08-15 00:03 | 2022-08-16 00:03 | 24 | 2022-08-14 23:10 | 2022-08-15 01:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 55709 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12156740 | ASD-COC-GFL002-AHU118 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM ASD-COC-GFL002-AHU118 AHU-A1126-026 AIR HANDLING UNIT 118 (TAG NO:AHU-A1126-026)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 002 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP6.CONC0216.AHU026.SYS |  | FM008 |  | 2023-09-05 14:15 | 2023-09-05 15:15 | 2023-09-06 15:15 | 24 | 2023-09-05 14:20 | 2023-09-05 16:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2022-10154099 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-03-06 |  | FM008 |  | 2022-02-19 11:35 | 2022-02-19 12:35 | 2022-02-20 12:35 | 24 | 2022-02-19 11:40 | 2022-02-19 14:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10351482 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DP ONE FILTER DIRTY-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-04-11 07:14 | 2022-04-11 08:14 | 2022-04-12 08:14 | 24 | 2022-04-11 07:20 | 2022-04-11 11:30 | 250 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11263275 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING – C0-03-06 |  | FM008 |  | 2022-12-11 09:55 | 2022-12-11 10:55 | 2022-12-12 10:55 | 24 | 2022-12-11 10:00 | 2022-12-11 13:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11330480 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C0-03-06 |  | FM008 |  | 2022-12-30 19:22 | 2022-12-30 20:22 | 2022-12-31 20:22 | 24 | 2022-12-30 19:30 | 2022-12-30 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-11762447 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009 CHILLER WATER LINE DRAIN PAINT FADED C0-03-06 |  | FM008 |  | 2023-05-03 22:52 | 2023-05-03 23:52 | 2023-05-04 23:52 | 24 | 2023-05-03 23:00 | 2023-05-04 01:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 87807 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11949416 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009-FILTER DIRTY-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-07-06 08:37 | 2023-07-06 09:37 | 2023-07-07 09:37 | 24 | 2023-07-06 08:40 | 2023-07-06 17:30 | 530 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12042608 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | FILTER DIRTY -C0-03-06 |  | FM008 |  | 2023-08-04 19:15 | 2023-08-04 20:15 | 2023-08-05 20:15 | 24 | 2023-08-04 19:20 | 2023-08-04 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12552187 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-009, C0-03-06 |  | FM008 |  | 2024-01-08 13:25 | 2024-01-08 14:25 | 2024-01-09 14:25 | 24 | 2024-01-08 13:30 | 2024-01-08 16:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2024-12555899 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | FILTER DIRTY -(AHU-A1126-009)-C0- 03-6. |  | FM008 |  | 2024-01-14 09:26 | 2024-01-14 10:26 | 2024-01-15 10:26 | 24 | 2024-01-14 09:30 | 2024-01-14 12:50 | 200 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 95217 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12726946 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU RELIEF SIDE ABNORMAL SOUND COMING - AHU-A1126-009 – C0-03-06 |  | FM008 |  | 2024-03-11 08:38 | 2024-03-11 09:38 | 2024-03-12 09:38 | 24 | 2024-03-11 08:40 | 2024-03-11 15:40 | 420 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-11193408 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT-BP1 FILTER ALARM |  | FM008 |  | 2022-11-16 07:06 | 2022-11-16 08:06 | 2022-11-17 08:06 | 24 | 2022-11-16 07:10 | 2022-11-16 08:55 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11569883 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-009 – C0-03-06 |  | FM008 |  | 2023-03-18 13:49 | 2023-03-18 14:49 | 2023-03-19 14:49 | 24 | 2023-03-18 13:58 | 2023-03-18 15:32 | 94 | 188 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11610042 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – C0-03-06 |  | FM008 |  | 2023-04-01 07:04 | 2023-04-01 08:04 | 2023-04-02 08:04 | 24 | 2023-04-01 07:10 | 2023-04-01 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11916969 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-009 – C0-03-06 |  | FM008 |  | 2023-06-24 20:34 | 2023-06-24 21:34 | 2023-06-25 21:34 | 24 | 2023-06-24 20:40 | 2023-06-24 22:50 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12187283 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU LIGHTING SWITCH FAULTY |  | FM008 |  | 2023-09-14 10:20 | 2023-09-14 11:20 | 2023-09-15 11:20 | 24 | 2023-09-14 10:30 | 2023-09-14 18:50 | 500 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 121959 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12464666 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-AIR HANDLING UNIT 102 (TAG NO:AHU-A1126-009)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-12-11 19:43 | 2023-12-11 20:43 | 2023-12-12 20:43 | 24 | 2023-12-11 19:50 | 2023-12-11 21:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12469766 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-009 - MECHANICAL ROOM C0-03-06 |  | FM008 |  | 2023-12-14 08:47 | 2023-12-14 09:47 | 2023-12-15 09:47 | 24 | 2023-12-14 08:55 | 2023-12-14 11:25 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10959421 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-009 – C0-03-06 |  | FM008 |  | 2022-08-23 10:12 | 2022-08-23 11:12 | 2022-08-24 11:12 | 24 | 2022-08-23 10:20 | 2022-08-23 11:40 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11216328 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009 ABNORMAL SOUNDS C0-03-06 |  | FM008 |  | 2022-11-23 10:25 | 2022-11-23 11:25 | 2022-11-24 11:25 | 24 | 2022-11-23 10:30 | 2022-11-23 15:00 | 270 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11760144 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE- C0-03-06 |  | FM008 |  | 2023-05-01 19:10 | 2023-05-01 20:10 | 2023-05-02 20:10 | 24 | 2023-05-01 19:15 | 2023-05-01 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106914 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11819043 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU FILTER DITY – C0-03-06 |  | FM008 |  | 2023-05-24 20:00 | 2023-05-24 21:00 | 2023-05-25 21:00 | 24 | 2023-05-24 20:05 | 2023-05-24 23:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 105233 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11878316 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009 – DUCT INSULLATION IS DAMAGED – C0-03-06 |  | FM008 |  | 2023-06-12 14:35 | 2023-06-12 15:35 | 2023-06-13 15:35 | 24 | 2023-06-12 14:40 | 2023-06-12 17:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 94954 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11883502 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | RELIEF MOTOR FLEXIBLE CONNECTOR DAMAGED , AHU-A1126-009,C0-03-06 |  | FM008 |  | 2023-06-14 16:22 | 2023-06-14 17:22 | 2023-06-15 17:22 | 24 | 2023-06-14 16:31 | 2023-06-14 18:00 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 124475 | 87807 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-11888173 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 102 (TAG NO:AHU-A1126-009 |  | FM008 |  | 2023-06-17 09:22 | 2023-06-17 10:22 | 2023-06-18 10:22 | 24 | 2023-06-17 09:30 | 2023-06-17 13:25 | 235 | 235 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 87807 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-12229461 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT 102 (TAG NO:AHU-A1126-009)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-09-28 19:14 | 2023-09-28 20:14 | 2023-09-29 20:14 | 24 | 2023-09-28 19:20 | 2023-09-28 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12614565 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-DUCT INSULATION DAMAGE -CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2024-02-02 19:22 | 2024-02-02 20:22 | 2024-02-03 20:22 | 24 | 2024-02-02 19:25 | 2024-02-02 22:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12708726 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AIR HANDLING UNIT 102 (TAG NO:AHU-A1126-009)-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2024-03-07 07:38 | 2024-03-07 08:38 | 2024-03-08 08:38 | 24 | 2024-03-07 07:45 | 2024-03-07 13:35 | 350 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12796528 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-009 – C0-03-06 |  | FM008 |  | 2024-04-06 08:07 | 2024-04-06 09:07 | 2024-04-07 09:07 | 24 | 2024-04-06 08:15 | 2024-04-06 10:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10194188 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY -C0-03-06 |  | FM008 |  | 2022-02-28 08:37 | 2022-02-28 09:37 | 2022-03-01 09:37 | 24 | 2022-02-28 08:45 | 2022-02-28 10:15 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10070395 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-21 22:38 | 2022-01-21 23:38 | 2022-01-22 23:38 | 24 | 2022-01-21 22:45 | 2022-01-22 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68060 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | BMS
| CM-2022-10998504 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-009 – C0-03-06 |  | FM008 |  | 2022-09-07 15:45 | 2022-09-07 16:45 | 2022-09-08 16:45 | 24 | 2022-09-07 15:55 | 2022-09-07 18:50 | 175 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-11301279 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-009 - C0-03-06 |  | FM008 |  | 2022-12-23 21:01 | 2022-12-23 22:01 | 2022-12-24 22:01 | 24 | 2022-12-23 21:10 | 2022-12-23 23:10 | 120 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11387626 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009)-FILTER DIRTY-C0-03-06 |  | FM008 |  | 2023-01-21 19:04 | 2023-01-21 20:04 | 2023-01-22 20:04 | 24 | 2023-01-21 19:10 | 2023-01-21 21:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 94954 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10032977 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009 – ACCESS DOOR AIR LEAKAGE – C0-03-06 |  | FM008 |  | 2022-01-09 07:13 | 2022-01-09 08:13 | 2022-01-10 08:13 | 24 | 2022-01-09 07:20 | 2022-01-09 08:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94954 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10358512 | ASD-COC-GFL003-AHU102 | AIR HANDLING UNIT-05 | AHU-A1126-009 COOLING COIL DIRTY C0-03-06 |  | FM008 |  | 2022-04-12 08:56 | 2022-04-12 09:56 | 2022-04-13 09:56 | 24 | 2022-04-12 09:00 | 2022-04-12 12:10 | 190 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-11189927 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING AHU-A1126-010 |  | FM008 |  | 2022-11-15 15:22 | 2022-11-15 16:22 | 2022-11-16 16:22 | 24 | 2022-11-15 15:30 | 2022-11-15 16:58 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106972 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11360630 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | FILTER ALARM-AIR HANDLING UNIT 103 (TAG NO:AHU-A1126-010)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-01-08 13:42 | 2023-01-08 14:42 | 2023-01-09 14:42 | 24 | 2023-01-08 13:45 | 2023-01-08 15:00 | 75 | 225 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5678 | Muhamedkwaja Muhamed Yahya , Mr. Alumkoottathil | N - - - |  | Voice Communication
| CM-2023-11931213 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-010 C0-03-14 |  | FM008 |  | 2023-06-26 08:28 | 2023-06-26 09:28 | 2023-06-27 09:28 | 24 | 2023-06-26 08:35 | 2023-06-26 14:58 | 383 | 361 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12005199 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU-A1126-010-DUCT INSULATION DAMAGE |  | FM008 |  | 2023-07-24 07:42 | 2023-07-24 08:42 | 2023-07-25 08:42 | 24 | 2023-07-24 07:50 | 2023-07-24 13:50 | 360 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11382786 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT (AHU-A1126-010) – PILLAR WATER LINE PAINT FADED – - |  | FM008 |  | 2023-01-17 21:32 | 2023-01-17 22:32 | 2023-01-18 22:32 | 24 | 2023-01-17 21:40 | 2023-01-17 23:55 | 135 | 405 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11765288 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-010 - C0-03-14 |  | FM008 |  | 2023-05-05 23:02 | 2023-05-06 00:02 | 2023-05-07 00:02 | 24 | 2023-05-05 23:10 | 2023-05-06 01:40 | 150 | 600 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-12092977 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU-A1126-010-DUCT INSULATION DAMAGE |  | FM008 |  | 2023-08-15 08:49 | 2023-08-15 09:49 | 2023-08-16 09:49 | 24 | 2023-08-15 09:00 | 2023-08-15 15:05 | 365 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12099684 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULT - AHU-A1126-010 – C0 03 14 |  | FM008 |  | 2023-08-19 14:42 | 2023-08-19 15:42 | 2023-08-20 15:42 | 24 | 2023-08-19 14:50 | 2023-08-19 17:43 | 173 | 301 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 132112 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2024-12755306 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | LIGHTING SWITCH IS NOT WORKING |  | FM008 |  | 2024-03-24 00:19 | 2024-03-24 01:19 | 2024-03-25 01:19 | 24 | 2024-03-24 00:25 | 2024-03-24 02:55 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-11250746 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSTALLATION DAMAGE, C0 03 14 - ASD-COC-GFL003-AHU103 |  | FM008 |  | 2022-12-05 00:32 | 2022-12-05 01:32 | 2022-12-06 01:32 | 24 | 2022-12-05 00:40 | 2022-12-05 03:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11668087 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU-A1126-010 – CHILLED WATER LINE PAINT FADED-C0-03-04- - |  | FM008 |  | 2023-04-15 22:02 | 2023-04-15 23:02 | 2023-04-16 23:02 | 24 | 2023-04-15 22:10 | 2023-04-16 00:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11688903 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-010) |  | FM008 |  | 2023-04-20 15:09 | 2023-04-20 16:09 | 2023-04-21 16:09 | 24 | 2023-04-20 15:20 | 2023-04-20 17:20 | 120 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 94953 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12277877 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 103 (TAG NO:AHU-A1126-010) |  | FM008 |  | 2023-10-09 22:38 | 2023-10-09 23:38 | 2023-10-10 23:38 | 24 | 2023-10-09 22:45 | 2023-10-10 01:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-12230683 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT 103 (TAG NO:AHU-A1126-010)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-09-28 19:16 | 2023-09-28 20:16 | 2023-09-29 20:16 | 24 | 2023-09-28 19:20 | 2023-09-28 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12644412 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-010 – C0-03-14 |  | FM008 |  | 2024-02-11 19:17 | 2024-02-11 20:17 | 2024-02-12 20:17 | 24 | 2024-02-11 19:22 | 2024-02-11 23:45 | 263 | 278 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12430019 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-01 10:57 | 2023-12-01 11:57 | 2023-12-02 11:57 | 24 | 2023-12-01 11:00 | 2023-12-01 18:45 | 465 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12511493 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-27 17:08 | 2023-12-27 18:08 | 2023-12-28 18:08 | 24 | 2023-12-27 17:15 | 2023-12-27 18:50 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-10145693 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE AHU-A1126-010 C0-03-14 |  | FM008 |  | 2022-02-14 15:58 | 2022-02-14 16:58 | 2022-02-15 16:58 | 24 | 2022-02-14 16:05 | 2022-02-14 18:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10045494 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | AHU-A1126-010 - CHILLED WATER LINE PAINT FADED – C0-03-14 |  | FM008 |  | 2022-01-14 10:29 | 2022-01-14 11:29 | 2022-01-15 11:29 | 24 | 2022-01-14 10:35 | 2022-01-14 12:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94954 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10351577 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | Return duct insulation damaged |  | FM008 |  | 2022-04-11 11:54 | 2022-04-11 12:54 | 2022-04-12 12:54 | 24 | 2022-04-11 12:00 | 2022-04-11 14:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11114320 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | ACESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-10-18 07:17 | 2022-10-18 08:17 | 2022-10-19 08:17 | 24 | 2022-10-18 07:20 | 2022-10-18 14:45 | 445 | 320 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 68060 | 95217 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10217684 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - AHU-A1126-010 – C0-03-14 |  | FM008 |  | 2022-03-07 07:20 | 2022-03-07 08:20 | 2022-03-08 08:20 | 24 | 2022-03-07 07:25 | 2022-03-07 09:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10874512 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | FILTER ALARM - (TAG NO:AHU-A1126-010)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-07-28 18:19 | 2022-07-28 19:19 | 2022-07-29 19:19 | 24 | 2022-07-28 18:25 | 2022-07-28 21:20 | 175 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10951370 | ASD-COC-GFL003-AHU103 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1126-010 – C0-04-14 |  | FM008 |  | 2022-08-15 12:15 | 2022-08-15 13:15 | 2022-08-16 13:15 | 24 | 2022-08-15 12:20 | 2022-08-15 14:30 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10146645 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027- DUCT INSULATION DAMAGED – - |  | FM008 |  | 2022-02-16 17:08 | 2022-02-16 18:08 | 2022-02-17 18:08 | 24 | 2022-02-16 17:17 | 2022-02-16 18:40 | 83 | 249 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10771744 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | FILTER IS DIRTY C0-03-06 |  | FM008 |  | 2022-06-20 08:33 | 2022-06-20 09:33 | 2022-06-21 09:33 | 24 | 2022-06-20 08:40 | 2022-06-20 11:00 | 140 | 275 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | BMS
| CM-2022-10777591 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 - DP1 FILTER ALARM – C0-03-06 |  | FM008 |  | 2022-06-26 08:14 | 2022-06-26 09:14 | 2022-06-27 09:14 | 24 | 2022-06-26 08:20 | 2022-06-26 10:55 | 155 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10829404 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1126-027 – C0-03-06 |  | FM008 |  | 2022-07-13 14:13 | 2022-07-13 15:13 | 2022-07-14 15:13 | 24 | 2022-07-13 14:20 | 2022-07-13 17:10 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 95217 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2022-10831797 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027- DP1 FILTER ALARM |  | FM008 |  | 2022-07-14 07:00 | 2022-07-14 08:00 | 2022-07-15 08:00 | 24 | 2022-07-14 07:10 | 2022-07-14 11:20 | 250 | 320 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11105492 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AC GRILL IS DIRTY - AHU-A1126-027 – C0-03-06 |  | FM008 |  | 2022-10-16 10:25 | 2022-10-16 11:25 | 2022-10-17 11:25 | 24 | 2022-10-16 10:30 | 2022-10-16 15:00 | 270 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 55709 |  |  | FM5803 | SANJEED KUMAR TIWARI, | N - - - |  | Voice Communication
| CM-2023-11783667 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 SUPPLY AC GRILL DIRTY C0-03-06 |  | FM008 |  | 2023-05-12 19:17 | 2023-05-12 20:17 | 2023-05-13 20:17 | 24 | 2023-05-12 19:20 | 2023-05-12 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11801206 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-18 07:57 | 2023-05-18 08:57 | 2023-05-19 08:57 | 24 | 2023-05-18 08:05 | 2023-05-18 12:40 | 275 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11938603 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU- FILTER ALARM |  | FM008 |  | 2023-07-02 20:15 | 2023-07-02 21:15 | 2023-07-03 21:15 | 24 | 2023-07-02 20:20 | 2023-07-02 22:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12039847 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-07-31 11:34 | 2023-07-31 12:34 | 2023-08-01 12:34 | 24 | 2023-07-31 11:40 | 2023-07-31 14:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-11150042 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027- FILTER DIRTY – C0-03-06 |  | FM008 |  | 2022-11-01 07:19 | 2022-11-01 08:19 | 2022-11-02 08:19 | 24 | 2022-11-01 07:25 | 2022-11-01 11:35 | 250 | 455 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17154 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11273354 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM |  | FM008 |  | 2022-12-16 06:58 | 2022-12-16 07:58 | 2022-12-17 07:58 | 24 | 2022-12-16 07:07 | 2022-12-16 09:35 | 148 | 444 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11350338 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 - DUCT INSULATION IS DAMAGED – C0-03-06 |  | FM008 |  | 2023-01-06 00:10 | 2023-01-06 01:10 | 2023-01-07 01:10 | 24 | 2023-01-06 00:15 | 2023-01-06 03:45 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11453630 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-02-12 23:38 | 2023-02-13 00:38 | 2023-02-14 00:38 | 24 | 2023-02-12 23:45 | 2023-02-13 02:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11630765 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – (AHU-A1126-027) - C0 03 06 |  | FM008 |  | 2023-04-08 21:43 | 2023-04-08 22:43 | 2023-04-09 22:43 | 24 | 2023-04-08 21:50 | 2023-04-09 00:30 | 160 | 320 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-11877998 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-027 – C0-03-06 |  | FM008 |  | 2023-06-14 20:46 | 2023-06-14 21:46 | 2023-06-15 21:46 | 24 | 2023-06-14 20:50 | 2023-06-14 23:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11877924 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED - AHU-A1126-027 – C0-03-06 |  | FM008 |  | 2023-06-14 14:01 | 2023-06-14 15:01 | 2023-06-15 15:01 | 24 | 2023-06-14 14:11 | 2023-06-14 16:10 | 119 | 238 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 106973 | 87807 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | BMS
| CM-2023-12040975 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY AIR LOW ALARM - AHU-A1126-027 - GROUND FLOOR AREA 003 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP7.CONC0306.AHU027.SYSALM.SUFLOALM / |  | FM008 |  | 2023-08-02 12:48 | 2023-08-02 13:48 | 2023-08-03 13:48 | 24 | 2023-08-02 12:55 | 2023-08-02 14:30 | 95 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 106973 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2023-12110210 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY AIR FLOW NOT ACHIEVING AS PER DESIGN - C0-03-06 |  | FM008 |  | 2023-08-22 08:30 | 2023-08-22 09:30 | 2023-08-23 09:30 | 24 | 2023-08-22 08:35 | 2023-08-22 10:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 17573 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | E-mail
| CM-2023-11661207 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 – FILTER DIRTY- |  | FM008 |  | 2023-04-15 19:22 | 2023-04-15 20:22 | 2023-04-16 20:22 | 24 | 2023-04-15 19:30 | 2023-04-15 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12671494 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AC GRILL DIRTY AHU-A1126-027 -C0-03-06 |  | FM008 |  | 2024-02-21 19:39 | 2024-02-21 20:39 | 2024-02-22 20:39 | 24 | 2024-02-21 19:45 | 2024-02-21 22:40 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106914 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12714441 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-027 |  | FM008 |  | 2024-03-09 07:08 | 2024-03-09 08:08 | 2024-03-10 08:08 | 24 | 2024-03-09 07:15 | 2024-03-09 18:45 | 690 | 500 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12312622 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1126-027, C0-03-06 |  | FM008 |  | 2023-10-22 20:34 | 2023-10-22 21:34 | 2023-10-23 21:34 | 24 | 2023-10-22 20:40 | 2023-10-22 23:10 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12278455 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY AIR LOW ALARM LOCATION: AIR HANDLING UNIT 119 (TAG NO:AHU-A1126-027)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 EXTRA REMARKS: PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP7.CONC0306.AHU027.SYSALM.SUFLOALM / |  | FM008 |  | 2023-10-12 07:55 | 2023-10-12 08:55 | 2023-10-13 08:55 | 24 | 2023-10-12 08:00 | 2023-10-12 14:30 | 390 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 138627 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2023-12457283 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU CABILLAMP FAULTY, AHU-A1126-027,C0-03-06 |  | FM008 |  | 2023-12-10 13:18 | 2023-12-10 14:18 | 2023-12-11 14:18 | 24 | 2023-12-10 13:25 | 2023-12-10 18:40 | 315 | 345 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2024-12537803 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 DUCT INSULATION DAMAGED |  | FM008 |  | 2024-01-06 20:05 | 2024-01-06 21:05 | 2024-01-07 21:05 | 24 | 2024-01-06 20:10 | 2024-01-06 23:00 | 170 | 340 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-10045555 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY A/C GRILL DIRTY |  | FM008 |  | 2022-01-15 00:13 | 2022-01-15 01:13 | 2022-01-16 01:13 | 24 | 2022-01-15 00:15 | 2022-01-15 02:20 | 125 | 320 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10107725 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL DIRTY AHU-A1126-027 C0-03-06 |  | FM008 |  | 2022-02-05 09:48 | 2022-02-05 10:48 | 2022-02-06 10:48 | 24 | 2022-02-05 09:55 | 2022-02-05 11:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10217683 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY - AHU-A1126-027 – C0-03-06 |  | FM008 |  | 2022-03-07 07:19 | 2022-03-07 08:19 | 2022-03-08 08:19 | 24 | 2022-03-07 07:25 | 2022-03-07 09:35 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10727949 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AIR HANDLING UNIT 119 (TAG NO:AHU-A1126-027)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-06-06 10:12 | 2022-06-06 11:12 | 2022-06-07 11:12 | 24 | 2022-06-06 10:20 | 2022-06-06 15:29 | 309 | 243 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 121959 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10988636 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 FILTER ALARM |  | FM008 |  | 2022-08-29 00:45 | 2022-08-29 01:45 | 2022-08-30 01:45 | 24 | 2022-08-29 00:50 | 2022-08-29 06:45 | 355 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11355497 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027-AC GRILL DIRTY |  | FM008 |  | 2023-01-08 21:48 | 2023-01-08 22:48 | 2023-01-09 22:48 | 24 | 2023-01-08 21:55 | 2023-01-09 00:30 | 155 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10214774 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 DP1 FILTER DIRTY C0-03-06 |  | FM008 |  | 2022-03-06 07:21 | 2022-03-06 08:21 | 2022-03-07 08:21 | 24 | 2022-03-06 07:30 | 2022-03-06 10:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10321640 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY AIRFLOW LOW ALARM |  | FM008 |  | 2022-04-05 07:30 | 2022-04-05 08:30 | 2022-04-06 08:30 | 24 | 2022-04-05 07:35 | 2022-04-05 17:00 | 565 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 106972 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10877469 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | AHU-A1126-027 FILTER ALARM - T0-03-06 |  | FM008 |  | 2022-07-27 19:19 | 2022-07-27 20:19 | 2022-07-28 20:19 | 24 | 2022-07-27 19:25 | 2022-07-27 20:45 | 80 | 85 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10953870 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2022-08-16 16:17 | 2022-08-16 17:17 | 2022-08-17 17:17 | 24 | 2022-08-16 16:25 | 2022-08-16 18:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 55709 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11498195 | ASD-COC-GFL003-AHU119 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY |  | FM008 |  | 2023-02-26 21:11 | 2023-02-26 22:11 | 2023-02-27 22:11 | 24 | 2023-02-26 21:15 | 2023-02-26 23:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10829931 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AC GRILL DIRTY AHU-A1126-028 C0-03-14 |  | FM008 |  | 2022-07-10 00:06 | 2022-07-10 01:06 | 2022-07-11 01:06 | 24 | 2022-07-10 00:10 | 2022-07-10 01:45 | 95 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11232503 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY C0-03-14 |  | FM008 |  | 2022-11-30 08:47 | 2022-11-30 09:47 | 2022-12-01 09:47 | 24 | 2022-11-30 08:55 | 2022-11-30 13:00 | 245 | 735 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11828653 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028-SUPPLY AC GRILL DIRTY -CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2023-05-28 09:54 | 2023-05-28 10:54 | 2023-05-29 10:54 | 24 | 2023-05-28 10:00 | 2023-05-28 12:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12645090 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | C0-03-14- FILTER DIRTY-AIR HANDLING UNIT 120 (TAG NO:AHU-A1126-028) - |  | FM008 |  | 2024-02-13 19:21 | 2024-02-13 20:21 | 2024-02-14 20:21 | 24 | 2024-02-13 19:30 | 2024-02-13 21:45 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10976351 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | DP1 AND CP3 FILTER ALARM TAG NO:AHU-A1126- |  | FM008 |  | 2022-08-28 12:12 | 2022-08-28 13:12 | 2022-08-29 13:12 | 24 | 2022-08-28 12:20 | 2022-08-28 14:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11687554 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028 FILTER DIRTY |  | FM008 |  | 2023-04-18 19:06 | 2023-04-18 20:06 | 2023-04-19 20:06 | 24 | 2023-04-18 19:10 | 2023-04-18 22:40 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12035140 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028-FILTER ALARM-C0-03-14 |  | FM008 |  | 2023-07-31 11:16 | 2023-07-31 12:16 | 2023-08-01 12:16 | 24 | 2023-07-31 11:20 | 2023-07-31 13:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12113759 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH FAULTY - AHU-A1126-028 – C0-03-14 |  | FM008 |  | 2023-08-23 17:00 | 2023-08-23 18:00 | 2023-08-24 18:00 | 24 | 2023-08-23 17:05 | 2023-08-23 18:45 | 100 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-12365244 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-11-08 07:19 | 2023-11-08 08:19 | 2023-11-09 08:19 | 24 | 2023-11-08 07:25 | 2023-11-08 10:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2022-10952204 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-08-16 20:41 | 2022-08-16 21:41 | 2022-08-17 21:41 | 24 | 2022-08-16 20:45 | 2022-08-16 22:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 55709 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11158019 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028 – DP1 & DP3 FILTER ALARM- |  | FM008 |  | 2022-11-04 06:56 | 2022-11-04 07:56 | 2022-11-05 07:56 | 24 | 2022-11-04 07:05 | 2022-11-04 09:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11932463 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C0-03-14 |  | FM008 |  | 2023-06-27 11:29 | 2023-06-27 12:29 | 2023-06-28 12:29 | 24 | 2023-06-27 11:35 | 2023-06-27 16:30 | 295 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12274645 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1126-028) - |  | FM008 |  | 2023-10-08 21:11 | 2023-10-08 22:11 | 2023-10-09 22:11 | 24 | 2023-10-08 21:20 | 2023-10-09 00:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12820380 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-AIR HANDLING UNIT 120 (TAG NO:AHU-A1126-028)-CONCOURSE C-GROUND FLOOR AREA 003 |  | FM008 |  | 2024-04-09 20:34 | 2024-04-09 21:34 | 2024-04-10 21:34 | 24 | 2024-04-09 20:40 | 2024-04-09 23:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12364175 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-028 |  | FM008 |  | 2023-11-09 07:38 | 2023-11-09 08:38 | 2023-11-10 08:38 | 24 | 2023-11-09 07:45 | 2023-11-09 10:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2024-12611864 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2024-02-02 08:47 | 2024-02-02 09:47 | 2024-02-03 09:47 | 24 | 2024-02-02 08:55 | 2024-02-02 10:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12822806 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED - AHU-A1126-028 – C0-04-15 |  | FM008 |  | 2024-04-13 20:16 | 2024-04-13 21:16 | 2024-04-14 21:16 | 24 | 2024-04-13 20:20 | 2024-04-13 23:00 | 160 | 320 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12822908 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS |  | FM008 |  | 2024-04-11 08:29 | 2024-04-11 09:29 | 2024-04-12 09:29 | 24 | 2024-04-11 08:40 | 2024-04-11 12:35 | 235 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10048349 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL IS DIRTY |  | FM008 |  | 2022-01-12 22:28 | 2022-01-12 23:28 | 2022-01-13 23:28 | 24 | 2022-01-12 22:35 | 2022-01-12 23:55 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68060 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | BMS
| CM-2022-11195180 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028 – AHU CABIN LAMP NOT WORKING – C0-03-14 |  | FM008 |  | 2022-11-16 13:19 | 2022-11-16 14:19 | 2022-11-17 14:19 | 24 | 2022-11-16 13:28 | 2022-11-16 14:56 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10237478 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | SUPPLY DIRTY GRILL AHU-A1126-028-C0-03-14 |  | FM008 |  | 2022-03-12 00:06 | 2022-03-12 01:06 | 2022-03-13 01:06 | 24 | 2022-03-12 00:15 | 2022-03-12 02:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10276073 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL DIRTY -AHU-A1126-028-C0-03-14 |  | FM008 |  | 2022-03-24 14:01 | 2022-03-24 15:01 | 2022-03-25 15:01 | 24 | 2022-03-24 14:10 | 2022-03-24 15:55 | 105 | 315 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10706584 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY - C0-03-14 |  | FM008 |  | 2022-05-29 12:55 | 2022-05-29 13:55 | 2022-05-30 13:55 | 24 | 2022-05-29 13:00 | 2022-05-29 15:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10771115 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL DIRTY-C0-03-14 |  | FM008 |  | 2022-06-22 08:45 | 2022-06-22 09:45 | 2022-06-23 09:45 | 24 | 2022-06-22 08:55 | 2022-06-22 11:25 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10877470 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028 - FILTER ALARM - T0-03-14 |  | FM008 |  | 2022-07-27 19:20 | 2022-07-27 20:20 | 2022-07-28 20:20 | 24 | 2022-07-27 19:25 | 2022-07-27 21:35 | 130 | 95 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11934589 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | FILTER DIRTY – C0-03-14 |  | FM008 |  | 2023-06-29 07:06 | 2023-06-29 08:06 | 2023-06-30 08:06 | 24 | 2023-06-29 07:10 | 2023-06-29 09:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12234006 | ASD-COC-GFL003-AHU120 | AIR HANDLING UNIT-05 | AHU-A1126-028 FILTER DIRTY |  | FM008 |  | 2023-09-30 09:17 | 2023-09-30 10:17 | 2023-10-01 10:17 | 24 | 2023-09-30 09:25 | 2023-09-30 11:45 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10049327 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-14 00:11 | 2022-01-14 01:11 | 2022-01-15 01:11 | 24 | 2022-01-14 00:20 | 2022-01-14 02:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68060 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | BMS
| CM-2022-10162106 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-23 07:16 | 2022-02-23 08:16 | 2022-02-24 08:16 | 24 | 2022-02-23 07:25 | 2022-02-23 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10252094 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU BELT DAMAGED |  | FM008 |  | 2022-03-17 11:39 | 2022-03-17 12:39 | 2022-03-18 12:39 | 24 | 2022-03-17 11:45 | 2022-03-17 15:35 | 230 | 245 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | BMS
| CM-2022-10568538 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-04-19 15:54 | 2022-04-19 16:54 | 2022-04-20 16:54 | 24 | 2022-04-19 16:00 | 2022-04-19 18:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10818194 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -AHU-A1126-011-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-07-04 12:36 | 2022-07-04 13:36 | 2022-07-05 13:36 | 24 | 2022-07-04 12:40 | 2022-07-04 14:10 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11341065 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY -C0-04-07 |  | FM008 |  | 2023-01-05 09:14 | 2023-01-05 10:14 | 2023-01-06 10:14 | 24 | 2023-01-05 09:20 | 2023-01-05 11:00 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2023-11775151 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AHU-A1126-011- C0-04-08 |  | FM008 |  | 2023-05-07 20:06 | 2023-05-07 21:06 | 2023-05-08 21:06 | 24 | 2023-05-07 20:10 | 2023-05-07 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2024-12552887 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - C0-04-07 |  | FM008 |  | 2024-01-10 20:27 | 2024-01-10 21:27 | 2024-01-11 21:27 | 24 | 2024-01-10 20:35 | 2024-01-10 23:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-11215891 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU-A1126-011 ACCESS DOOR AIR LEAKAGE C0-04-07 |  | FM008 |  | 2022-11-25 21:38 | 2022-11-25 22:38 | 2022-11-26 22:38 | 24 | 2022-11-25 21:45 | 2022-11-25 23:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11345187 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C0-04-08 |  | FM008 |  | 2023-01-03 19:20 | 2023-01-03 20:20 | 2023-01-04 20:20 | 24 | 2023-01-03 19:30 | 2023-01-03 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11350726 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU-A1126-011-COOLING COIL DIRTY |  | FM008 |  | 2023-01-07 21:40 | 2023-01-07 22:40 | 2023-01-08 22:40 | 24 | 2023-01-07 21:45 | 2023-01-08 00:30 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12040486 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU-A1126-011 FILTER DIRTY |  | FM008 |  | 2023-07-31 19:36 | 2023-07-31 20:36 | 2023-08-01 20:36 | 24 | 2023-07-31 19:45 | 2023-07-31 23:35 | 230 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12095155 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU-A1126-011 DUCT INSULATION DAMAGED C0-04-08 |  | FM008 |  | 2023-08-15 19:55 | 2023-08-15 20:55 | 2023-08-16 20:55 | 24 | 2023-08-15 20:00 | 2023-08-15 23:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12575243 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2024-01-17 16:02 | 2024-01-17 17:02 | 2024-01-18 17:02 | 24 | 2024-01-17 16:10 | 2024-01-17 17:50 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12851118 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-011 – C0-04-07 |  | FM008 |  | 2024-04-27 08:16 | 2024-04-27 09:16 | 2024-04-28 09:16 | 24 | 2024-04-27 08:20 | 2024-04-27 10:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11175982 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-11-09 09:07 | 2022-11-09 10:07 | 2022-11-10 10:07 | 24 | 2022-11-09 09:15 | 2022-11-09 13:10 | 235 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2024-12689936 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY |  | FM008 |  | 2024-02-29 07:24 | 2024-02-29 08:24 | 2024-03-01 08:24 | 24 | 2024-02-29 07:30 | 2024-02-29 11:35 | 245 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12819543 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2024-04-08 19:44 | 2024-04-08 20:44 | 2024-04-09 20:44 | 24 | 2024-04-08 19:50 | 2024-04-08 22:15 | 145 | 580 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12420163 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY AHU-A1126-011 |  | FM008 |  | 2023-11-28 07:25 | 2023-11-28 08:25 | 2023-11-29 08:25 | 24 | 2023-11-28 07:30 | 2023-11-28 09:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106972 | 87807 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2023-11577500 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | SUPPLY MOTOR TERMINAL BLOCK DAMAGED - C0-04-07 |  | FM008 |  | 2023-03-19 22:22 | 2023-03-19 23:22 | 2023-03-20 23:22 | 24 | 2023-03-19 22:32 | 2023-03-19 23:59 | 87 | 174 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10116851 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | AHU-A1126-011 - SUPPLY DUCT INSULATION DAMAGED C0-04-08 |  | FM008 |  | 2022-02-07 22:07 | 2022-02-07 23:07 | 2022-02-08 23:07 | 24 | 2022-02-07 22:15 | 2022-02-08 01:00 | 165 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 55709 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-11932392 | ASD-COC-GFL004-AHU104 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-06-27 07:05 | 2023-06-27 08:05 | 2023-06-28 08:05 | 24 | 2023-06-27 07:10 | 2023-06-27 15:00 | 470 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10818195 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -:AHU-A1126-012)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-07-04 12:38 | 2022-07-04 13:38 | 2022-07-05 13:38 | 24 | 2022-07-04 12:45 | 2022-07-04 15:40 | 175 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11063687 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | BELT DAMAGED AHU-A1126-01 |  | FM008 |  | 2022-09-28 13:29 | 2022-09-28 14:29 | 2022-09-29 14:29 | 24 | 2022-09-28 13:35 | 2022-09-28 15:00 | 85 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM5678 | Muhamedkwaja Muhamed Yahya , Mr. Alumkoottathil | N - - - |  | Voice Communication
| CM-2022-11178208 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 – AHU CABIN LAMP NOT WORKING – C0-04-15 |  | FM008 |  | 2022-11-09 12:36 | 2022-11-09 13:36 | 2022-11-10 13:36 | 24 | 2022-11-09 12:42 | 2022-11-09 14:10 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | SUPPLY POWER FAILURE | RESET THE BREAKER | 17154 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11667860 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE ,AHU-A1126-012,C0-04-15 |  | FM008 |  | 2023-04-14 20:07 | 2023-04-14 21:07 | 2023-04-15 21:07 | 24 | 2023-04-14 20:16 | 2023-04-14 23:16 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11828651 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012-ACCESS DOOR AIR LEAKAGE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-05-28 09:50 | 2023-05-28 10:50 | 2023-05-29 10:50 | 24 | 2023-05-28 10:00 | 2023-05-28 12:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11113676 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-10-19 21:23 | 2022-10-19 22:23 | 2022-10-20 22:23 | 24 | 2022-10-19 21:30 | 2022-10-19 23:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11283187 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-18 20:24 | 2022-12-18 21:24 | 2022-12-19 21:24 | 24 | 2022-12-18 20:30 | 2022-12-18 23:30 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-11448294 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 DUCT INSULATION DAMAGED C0-04-15 - C0-04-15 - CM-01-0103 |  | FM008 |  | 2023-02-12 23:46 | 2023-02-13 00:46 | 2023-02-14 00:46 | 24 | 2023-02-12 23:50 | 2023-02-13 02:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 17053 |  |  | FM11844 | SELVARAJ | - - - |  | Voice Communication
| CM-2023-11934955 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED |  | FM008 |  | 2023-06-29 20:57 | 2023-06-29 21:57 | 2023-06-30 21:57 | 24 | 2023-06-29 21:05 | 2023-06-29 23:55 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12553518 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – C0-04-15 |  | FM008 |  | 2024-01-09 19:49 | 2024-01-09 20:49 | 2024-01-10 20:49 | 24 | 2024-01-09 19:55 | 2024-01-09 22:55 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12624076 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-012 C0-04-15 |  | FM008 |  | 2024-02-07 08:56 | 2024-02-07 09:56 | 2024-02-08 09:56 | 24 | 2024-02-07 09:05 | 2024-02-07 10:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12565016 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | CONDENSATION NOTICED ON CHILLED WATER PIPE - INSULATION IN A NUMBER OF LOCATION - AHU ROOM C0 04 15 |  | FM008 |  | 2024-01-15 09:17 | 2024-01-15 10:17 | 2024-01-16 10:17 | 24 | 2024-01-15 09:25 | 2024-01-15 11:25 | 120 | 145 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 95217 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2024-12794537 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 DUCT INSULATION DAMAGED C0-04-15 |  | FM008 |  | 2024-04-03 19:12 | 2024-04-03 20:12 | 2024-04-04 20:12 | 24 | 2024-04-03 19:20 | 2024-04-03 22:10 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10262802 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-20 11:05 | 2022-03-20 12:05 | 2022-03-21 12:05 | 24 | 2022-03-20 11:10 | 2022-03-20 13:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10045493 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 – CHILLED WATER LINE PAINT FADED – C0-04-15 |  | FM008 |  | 2022-01-14 10:28 | 2022-01-14 11:28 | 2022-01-15 11:28 | 24 | 2022-01-14 10:35 | 2022-01-14 12:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94954 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11179436 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C0-04-15 |  | FM008 |  | 2022-11-11 07:13 | 2022-11-11 08:13 | 2022-11-12 08:13 | 24 | 2022-11-11 07:20 | 2022-11-11 10:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11342222 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - (FCU-A1126142) - -AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-01-02 21:29 | 2023-01-02 22:29 | 2023-01-03 22:29 | 24 | 2023-01-02 21:35 | 2023-01-02 23:55 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 132112 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10123164 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 SUPPLY DUCT INSULATION DAMAGED C0-04-15 |  | FM008 |  | 2022-02-10 22:08 | 2022-02-10 23:08 | 2022-02-11 23:08 | 24 | 2022-02-10 22:15 | 2022-02-11 00:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10695396 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 RETURN DUCT INSULATION DAMAGED C0-04-15 |  | FM008 |  | 2022-05-25 22:10 | 2022-05-25 23:10 | 2022-05-26 23:10 | 24 | 2022-05-25 22:15 | 2022-05-25 23:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10874513 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | FILTER ALARM - C0-04-15 CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-07-28 18:21 | 2022-07-28 19:21 | 2022-07-29 19:21 | 24 | 2022-07-28 18:25 | 2022-07-28 22:25 | 240 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12159195 | ASD-COC-GFL004-AHU105 | AIR HANDLING UNIT-05 | AHU-A1126-012 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-08 19:11 | 2023-09-08 20:11 | 2023-09-09 20:11 | 24 | 2023-09-08 19:20 | 2023-09-08 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10045438 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | CHILLED WATER PAINT FADED |  | FM008 |  | 2022-01-13 21:51 | 2022-01-13 22:51 | 2022-01-14 22:51 | 24 | 2022-01-13 22:00 | 2022-01-13 23:55 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68060 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11040950 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | DP3 FILTER ALATM |  | FM008 |  | 2022-09-23 00:12 | 2022-09-23 01:12 | 2022-09-24 01:12 | 24 | 2022-09-23 00:20 | 2022-09-23 04:30 | 250 | 250 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11105491 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AC GRILL IS DIRTY - AHU-A1126-029 – C0-04-07 |  | FM008 |  | 2022-10-16 10:23 | 2022-10-16 11:23 | 2022-10-17 11:23 | 24 | 2022-10-16 10:30 | 2022-10-16 12:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM5803 | SANJEED KUMAR TIWARI, | N - - - |  | Voice Communication
| CM-2022-11165727 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AC GRILL DIRTY - AHU-A1126-029)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-11-07 21:55 | 2022-11-07 22:55 | 2022-11-08 22:55 | 24 | 2022-11-07 22:00 | 2022-11-07 23:55 | 115 | 345 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11601654 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | CHILLED WATER LINE INSULATION DAMAGED – C0-04-07 |  | FM008 |  | 2023-03-27 07:07 | 2023-03-27 08:07 | 2023-03-28 08:07 | 24 | 2023-03-27 07:15 | 2023-03-27 14:40 | 445 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11841535 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | FILTER DIRTY -C0-04-07 |  | FM008 |  | 2023-06-01 10:23 | 2023-06-01 11:23 | 2023-06-02 11:23 | 24 | 2023-06-01 10:30 | 2023-06-01 13:10 | 160 | 425 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12041205 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C0-04-07 |  | FM008 |  | 2023-08-01 19:13 | 2023-08-01 20:13 | 2023-08-02 20:13 | 24 | 2023-08-01 19:20 | 2023-08-01 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 105233 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2022-10877508 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - AHU-A1126-029 - MECHANICAL ROOM C0-04-07 |  | FM008 |  | 2022-07-28 07:33 | 2022-07-28 08:33 | 2022-07-29 08:33 | 24 | 2022-07-28 07:40 | 2022-07-28 16:00 | 500 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10988823 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU-A1126-029 FILTER ALARM |  | FM008 |  | 2022-08-29 21:33 | 2022-08-29 22:33 | 2022-08-30 22:33 | 24 | 2022-08-29 21:40 | 2022-08-29 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11161279 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AC GRILL DIRTY - AHU-A1126-029 – C0-04-07 |  | FM008 |  | 2022-11-04 22:35 | 2022-11-04 23:35 | 2022-11-05 23:35 | 24 | 2022-11-04 22:40 | 2022-11-05 00:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11231305 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | A/C SUPPLY GRILL DIRY C0-04-07 |  | FM008 |  | 2022-11-28 20:39 | 2022-11-28 21:39 | 2022-11-29 21:39 | 24 | 2022-11-28 20:45 | 2022-11-28 23:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11284110 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-04-07 |  | FM008 |  | 2022-12-18 15:05 | 2022-12-18 16:05 | 2022-12-19 16:05 | 24 | 2022-12-18 15:10 | 2022-12-18 18:35 | 205 | 410 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11934679 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1126-029- C0-04-07 |  | FM008 |  | 2023-06-29 10:35 | 2023-06-29 11:35 | 2023-06-30 11:35 | 24 | 2023-06-29 10:40 | 2023-06-29 13:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11937625 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - C0-04-07 – AHU-A1126-029 |  | FM008 |  | 2023-07-01 14:23 | 2023-07-01 15:23 | 2023-07-02 15:23 | 24 | 2023-07-01 14:32 | 2023-07-01 17:00 | 148 | 148 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | BMS
| CM-2023-12217938 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU-A1126-029 â?? COOLING COIL IS DIRTY â?? C0-04-07 |  | FM008 |  | 2023-09-25 08:41 | 2023-09-25 09:41 | 2023-09-26 09:41 | 24 | 2023-09-25 08:50 | 2023-09-25 10:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94954 | 87807 |  |  | FM12472 | Arumuga Nainar Senthilkumar, | N - - - |  | Voice Communication
| CM-2023-12422706 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-11-29 12:58 | 2023-11-29 13:58 | 2023-11-30 13:58 | 24 | 2023-11-29 13:05 | 2023-11-29 16:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | NOT WORKING | CIRCUIT TRIP DUE TO OVERLOAD | RESET THE BREAKER | 68060 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2024-12714799 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU-A1126-029 AC GRILL DIRTY -C0-04-07/ |  | FM008 |  | 2024-03-09 19:17 | 2024-03-09 20:17 | 2024-03-10 20:17 | 24 | 2024-03-09 19:25 | 2024-03-09 22:15 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2024-12851120 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-029 – C0-04-07 |  | FM008 |  | 2024-04-27 08:18 | 2024-04-27 09:18 | 2024-04-28 09:18 | 24 | 2024-04-27 08:25 | 2024-04-27 13:25 | 300 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11422667 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-029 – C0-04-07 |  | FM008 |  | 2023-01-30 22:15 | 2023-01-30 23:15 | 2023-01-31 23:15 | 24 | 2023-01-30 22:20 | 2023-01-31 01:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11884990 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY ,AHU-A1126-029, C0-04-07 |  | FM008 |  | 2023-06-15 12:53 | 2023-06-15 13:53 | 2023-06-16 13:53 | 24 | 2023-06-15 13:00 | 2023-06-15 15:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12488499 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY |  | FM008 |  | 2023-12-19 20:12 | 2023-12-19 21:12 | 2023-12-20 21:12 | 24 | 2023-12-19 20:20 | 2023-12-19 23:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2024-12599459 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU-A1126-029 AC SUPPLY GRILL DIRTY |  | FM008 |  | 2024-01-29 08:55 | 2024-01-29 09:55 | 2024-01-30 09:55 | 24 | 2024-01-29 09:00 | 2024-01-29 11:20 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12407468 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AC VENTS DIRTY - BAGGAGE AREA NEAR MU 31/32 |  | FM008 |  | 2023-11-25 07:02 | 2023-11-25 08:02 | 2023-11-26 08:02 | 24 | 2023-11-25 07:10 | 2023-11-25 10:10 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | 132149 | Palubag, Ms. Roxan Bahian | N - - - |  | Voice Communication
| CM-2024-12692061 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 121 (TAG NO:AHU-A1126-029)-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2024-02-29 19:21 | 2024-02-29 20:21 | 2024-03-01 20:21 | 24 | 2024-02-29 19:25 | 2024-02-29 21:55 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2022-10147207 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL DIRTY – C0-04-07 |  | FM008 |  | 2022-02-17 08:14 | 2022-02-17 09:14 | 2022-02-18 09:14 | 24 | 2022-02-17 08:20 | 2022-02-17 11:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10251789 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | AHU-A1126-029 – SUPPLY GRILL DIRTY – C0-04-07 |  | FM008 |  | 2022-03-15 23:18 | 2022-03-16 00:18 | 2022-03-17 00:18 | 24 | 2022-03-15 23:25 | 2022-03-16 01:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-9959253 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | SUPPLY DUCT AC GRILL DIRTY - AHU-A1126-029 – C0-04-07 |  | FM008 |  | 2022-01-04 21:56 | 2022-01-04 22:56 | 2022-01-05 22:56 | 24 | 2022-01-04 22:05 | 2022-01-04 23:55 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106973 | 55709 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2022-10775176 | ASD-COC-GFL004-AHU121 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL DIRTY - AHU-A1126-029 – C0-04-07 |  | FM008 |  | 2022-06-20 14:14 | 2022-06-20 15:14 | 2022-06-21 15:14 | 24 | 2022-06-20 14:20 | 2022-06-20 16:40 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10041986 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030- SUPPLY DUCT GRILL DIRTY – C0-04-15 |  | FM008 |  | 2022-01-10 16:11 | 2022-01-10 17:11 | 2022-01-11 17:11 | 24 | 2022-01-10 16:15 | 2022-01-10 18:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10060197 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-21 19:06 | 2022-01-21 20:06 | 2022-01-22 20:06 | 24 | 2022-01-21 19:10 | 2022-01-21 21:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68060 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10252695 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030 – SUPPLY GRILL IS DIRTY – C0-04-15 |  | FM008 |  | 2022-03-15 19:35 | 2022-03-15 20:35 | 2022-03-16 20:35 | 24 | 2022-03-15 19:40 | 2022-03-15 23:10 | 210 | 140 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10770748 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -C0-04-15 |  | FM008 |  | 2022-06-20 10:04 | 2022-06-20 11:04 | 2022-06-21 11:04 | 24 | 2022-06-20 10:10 | 2022-06-20 16:10 | 360 | 265 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11082367 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030 - SUPPLY AC GRILL IS DIRTY – C0-04-15 |  | FM008 |  | 2022-10-08 13:35 | 2022-10-08 14:35 | 2022-10-09 14:35 | 24 | 2022-10-08 13:40 | 2022-10-08 17:00 | 200 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94954 | 95217 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11836681 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030)-FILTER DIRTY -CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-05-30 18:59 | 2023-05-30 19:59 | 2023-05-31 19:59 | 24 | 2023-05-30 19:02 | 2023-05-30 21:59 | 177 | 531 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM11824 | Rain, Mr. Mojmil | N - - - |  | Voice Communication
| CM-2023-12041207 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C0-04-15 |  | FM008 |  | 2023-08-01 19:14 | 2023-08-01 20:14 | 2023-08-02 20:14 | 24 | 2023-08-01 19:20 | 2023-08-01 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2022-10877509 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030 - MECHANICAL ROOM C0-04-15 |  | FM008 |  | 2022-07-28 07:36 | 2022-07-28 08:36 | 2022-07-29 08:36 | 24 | 2022-07-28 07:44 | 2022-07-28 17:10 | 566 | 136 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | E-mail
| CM-2022-10988143 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030 – FILTER ALARM |  | FM008 |  | 2022-08-30 20:52 | 2022-08-30 21:52 | 2022-08-31 21:52 | 24 | 2022-08-30 21:00 | 2022-08-30 23:45 | 165 | 280 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11208894 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY -C0-04-15 |  | FM008 |  | 2022-11-22 00:03 | 2022-11-22 01:03 | 2022-11-23 01:03 | 24 | 2022-11-22 00:10 | 2022-11-22 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11836585 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | SUPPLY FAN CABIN LIGHT FAULTY -AIR HANDLING UNIT 122 (TAG NO:AHU-A1126-030)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2023-05-30 13:44 | 2023-05-30 14:44 | 2023-05-31 14:44 | 24 | 2023-05-30 13:54 | 2023-05-30 15:51 | 117 | 234 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 17336 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11937627 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - AHU-A1126-030 – C0-04-15 |  | FM008 |  | 2023-07-01 14:25 | 2023-07-01 15:25 | 2023-07-02 15:25 | 24 | 2023-07-01 14:32 | 2023-07-01 17:00 | 148 | 296 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | BMS
| CM-2024-12609140 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AC SUPPLY GRILL DIRTY - AHU-A1126-030 - MECHANICAL ROOM C0-04-15 |  | FM008 |  | 2024-01-31 16:17 | 2024-01-31 17:17 | 2024-02-01 17:17 | 24 | 2024-01-31 16:25 | 2024-01-31 17:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12850536 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-030 – C0-04-15 |  | FM008 |  | 2024-04-27 11:07 | 2024-04-27 12:07 | 2024-04-28 12:07 | 24 | 2024-04-27 11:20 | 2024-04-27 16:00 | 280 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11065808 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | NEAR C 7 GATE WATER LEAK LINES FOUND IN WALLS |  | FM008 |  | 2022-10-02 08:47 | 2022-10-02 09:47 | 2022-10-03 09:47 | 24 | 2022-10-02 08:56 | 2022-10-02 09:35 | 39 | 78 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 55709 |  |  | 122231 | Naushad, Mr. Muhammed Aadhil | N - - - |  | E-mail
| CM-2022-11181984 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -AHU-A1126-030)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-11-14 10:39 | 2022-11-14 11:39 | 2022-11-15 11:39 | 24 | 2022-11-14 10:45 | 2022-11-14 13:15 | 150 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11226945 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | COOILING COIL DIRTY - AHU-A1126-030 - C0-04-15 |  | FM008 |  | 2022-11-29 19:24 | 2022-11-29 20:24 | 2022-11-30 20:24 | 24 | 2022-11-29 19:30 | 2022-11-29 22:30 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2022-11276586 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030- DUCT INSULATION DAMAGED – C0-04-15 |  | FM008 |  | 2022-12-18 08:04 | 2022-12-18 09:04 | 2022-12-19 09:04 | 24 | 2022-12-18 08:10 | 2022-12-18 12:00 | 230 | 460 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11422668 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU GRILL DIRTY - AHU-A1126-030 – C0-04-15 |  | FM008 |  | 2023-01-30 22:21 | 2023-01-30 23:21 | 2023-01-31 23:21 | 24 | 2023-01-30 22:30 | 2023-01-31 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12565015 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | COVER SHARP END OF DUCT SUPPORT TO PREVENT INJURY - PTC CONCOURSE C AHU ROOM C0 04 15 |  | FM008 |  | 2024-01-15 09:14 | 2024-01-15 10:14 | 2024-01-16 10:14 | 24 | 2024-01-15 09:20 | 2024-01-15 10:10 | 50 | 100 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 95217 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2024-12692391 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 122 (TAG NO:AHU-A1126-030)-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2024-02-29 19:22 | 2024-02-29 20:22 | 2024-03-01 20:22 | 24 | 2024-02-29 19:30 | 2024-03-01 00:30 | 300 | 455 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2024-12822805 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED - AHU-A1126-030 – C0-04-15 |  | FM008 |  | 2024-04-13 20:14 | 2024-04-13 21:14 | 2024-04-14 21:14 | 24 | 2024-04-13 20:20 | 2024-04-13 22:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12346647 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-030 - C0-04-15 |  | FM008 |  | 2023-11-03 08:44 | 2023-11-03 09:44 | 2023-11-04 09:44 | 24 | 2023-11-03 08:50 | 2023-11-03 14:00 | 310 | 292 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12422353 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU LIGHTING SWITCH FAULTY - AHU-A1126-030 - C0-04-15 |  | FM008 |  | 2023-11-28 11:02 | 2023-11-28 12:02 | 2023-11-29 12:02 | 24 | 2023-11-28 11:10 | 2023-11-28 13:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 133396 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2024-12689443 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-030 C0-04-15 |  | FM008 |  | 2024-02-27 07:35 | 2024-02-27 08:35 | 2024-02-28 08:35 | 24 | 2024-02-27 07:40 | 2024-02-27 10:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10124639 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU-A1126-030 – SUPPLY DUCT AC GRILL IS DIRTY – C0-04-15 |  | FM008 |  | 2022-02-11 22:00 | 2022-02-11 23:00 | 2022-02-12 23:00 | 24 | 2022-02-11 22:05 | 2022-02-11 23:55 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94954 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10776798 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | SUPPLY DUCT GRILL DIRTY - (TAG NO:AHU-A1126-030)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 004 |  | FM008 |  | 2022-06-23 08:00 | 2022-06-23 09:00 | 2022-06-24 09:00 | 24 | 2022-06-23 08:05 | 2022-06-23 10:40 | 155 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10825279 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | SUPPLY GRILL DIRTY |  | FM008 |  | 2022-07-10 12:59 | 2022-07-10 13:59 | 2022-07-11 13:59 | 24 | 2022-07-10 13:08 | 2022-07-10 15:45 | 157 | 314 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 95217 |  |  | FM5803 | Tiwari, Mr. Sanjeed Kumar | N - - - |  | Voice Communication
| CM-2022-10826180 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AC GRILL DIRTY- AHU-A1126-030 /C0-04-15 |  | FM008 |  | 2022-07-10 22:21 | 2022-07-10 23:21 | 2022-07-11 23:21 | 24 | 2022-07-10 22:30 | 2022-07-11 00:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 95217 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-11931935 | ASD-COC-GFL004-AHU122 | AIR HANDLING UNIT-05 | AHU MAIN FILTER DIRTY - AHU-A1126-030 - MECHANICAL ROOM C0-04-15 |  | FM008 |  | 2023-06-29 11:28 | 2023-06-29 12:28 | 2023-06-30 12:28 | 24 | 2023-06-29 11:35 | 2023-06-29 16:45 | 310 | 635 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10048803 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | RAD OPEN FAIL ALARM- - |  | FM008 |  | 2022-01-15 16:31 | 2022-01-15 17:31 | 2022-01-16 17:31 | 24 | 2022-01-15 16:40 | 2022-01-15 18:00 | 80 | 160 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 94953 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2022-11303621 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AHU-A1126-013 – C0-05-12 |  | FM008 |  | 2022-12-25 21:46 | 2022-12-25 22:46 | 2022-12-26 22:46 | 24 | 2022-12-25 21:55 | 2022-12-25 23:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12420943 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AHU-A1126-013 AHU CABIN LAMP FAULTY C0-05-12 |  | FM008 |  | 2023-11-26 22:48 | 2023-11-26 23:48 | 2023-11-27 23:48 | 24 | 2023-11-26 22:55 | 2023-11-27 01:40 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12847786 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-013, C0-05-12 |  | FM008 |  | 2024-04-22 07:19 | 2024-04-22 08:19 | 2024-04-23 08:19 | 24 | 2024-04-22 07:25 | 2024-04-22 10:00 | 155 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11465800 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-05-12 |  | FM008 |  | 2023-02-16 19:01 | 2023-02-16 20:01 | 2023-02-17 20:01 | 24 | 2023-02-16 19:10 | 2023-02-16 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11637797 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AHU-A1126-013 DRAIN LINE BLOCKED - MECHANICAL ROOM C0-05-12 - CM-2023-05-1470 |  | FM008 |  | 2023-04-09 22:48 | 2023-04-09 23:48 | 2023-04-10 23:48 | 24 | 2023-04-09 22:55 | 2023-04-10 00:30 | 95 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17053 | 17053 |  |  | FM11198 | MALIK | - - - |  | Voice Communication
| CM-2023-11835487 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AHU CABINET LAMP FUSED |  | FM008 |  | 2023-05-29 15:15 | 2023-05-29 16:15 | 2023-05-30 16:15 | 24 | 2023-05-29 15:20 | 2023-05-29 17:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 68060 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11839925 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-06-01 16:49 | 2023-06-01 17:49 | 2023-06-02 17:49 | 24 | 2023-06-01 16:55 | 2023-06-01 18:45 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12689935 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY |  | FM008 |  | 2024-02-29 07:23 | 2024-02-29 08:23 | 2024-03-01 08:23 | 24 | 2024-02-29 07:30 | 2024-02-29 09:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12749498 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-013 - C0-05-12 |  | FM008 |  | 2024-03-21 06:57 | 2024-03-21 07:57 | 2024-03-22 07:57 | 24 | 2024-03-21 07:05 | 2024-03-21 10:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12772362 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-013 |  | FM008 |  | 2024-03-27 10:55 | 2024-03-27 11:55 | 2024-03-28 11:55 | 24 | 2024-03-27 11:05 | 2024-03-27 14:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12595343 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AHU-FILTER DIRTY -GROUND FLOOR AREA 005 |  | FM008 |  | 2024-01-25 19:24 | 2024-01-25 20:24 | 2024-01-26 20:24 | 24 | 2024-01-25 19:30 | 2024-01-25 21:50 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11304771 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AHU-A1126-013 – COOLING COIL DIRTY – C0-05-12 |  | FM008 |  | 2022-12-28 08:35 | 2022-12-28 09:35 | 2022-12-29 09:35 | 24 | 2022-12-28 08:40 | 2022-12-28 12:00 | 200 | 5 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10209411 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-013 |  | FM008 |  | 2022-03-03 07:21 | 2022-03-03 08:21 | 2022-03-04 08:21 | 24 | 2022-03-03 07:30 | 2022-03-03 09:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10221751 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - AHU-A1126-013 – C0-05-12 |  | FM008 |  | 2022-03-07 12:08 | 2022-03-07 13:08 | 2022-03-08 13:08 | 24 | 2022-03-07 12:18 | 2022-03-07 14:18 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10820772 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-07-06 11:25 | 2022-07-06 12:25 | 2022-07-07 12:25 | 24 | 2022-07-06 11:35 | 2022-07-06 16:00 | 265 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12165509 | ASD-COC-GFL005-AHU106 | AIR HANDLING UNIT-05 | AHU-A1126-013 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-08 19:13 | 2023-09-08 20:13 | 2023-09-09 20:13 | 24 | 2023-09-08 19:20 | 2023-09-08 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10128506 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – C0-05-19 |  | FM008 |  | 2022-02-10 15:07 | 2022-02-10 16:07 | 2022-02-11 16:07 | 24 | 2022-02-10 15:15 | 2022-02-10 17:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11845986 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-014 - C0-05-19 |  | FM008 |  | 2023-06-05 14:36 | 2023-06-05 15:36 | 2023-06-06 15:36 | 24 | 2023-06-05 14:40 | 2023-06-05 18:40 | 240 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | BMS
| CM-2023-11959126 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - C0-05-19 |  | FM008 |  | 2023-07-07 07:12 | 2023-07-07 08:12 | 2023-07-08 08:12 | 24 | 2023-07-07 07:20 | 2023-07-07 09:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12118606 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE-AIR HANDLING UNIT 107 (TAG NO:AHU-A1126-014)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2023-08-27 12:38 | 2023-08-27 13:38 | 2023-08-28 13:38 | 24 | 2023-08-27 12:45 | 2023-08-27 14:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12134145 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | HEATER FLEXIBLE CONNECTOR DAMAGED- AIR HANDLING UNIT 107 (TAG NO:AHU-A1126-014)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2023-08-30 19:04 | 2023-08-30 20:04 | 2023-08-31 20:04 | 24 | 2023-08-30 19:10 | 2023-08-31 02:00 | 410 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 17336 | 17053 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2023-12208914 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | AHU-A1126-014 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-22 15:50 | 2023-09-22 16:50 | 2023-09-23 16:50 | 24 | 2023-09-22 15:55 | 2023-09-22 18:35 | 160 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12224225 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED - AHU-A1126-014 â?? C0 05 19 |  | FM008 |  | 2023-09-26 13:38 | 2023-09-26 14:38 | 2023-09-27 14:38 | 24 | 2023-09-26 13:45 | 2023-09-26 18:15 | 270 | 455 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12423518 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FAULTY – C0-05-19 |  | FM008 |  | 2023-11-29 19:18 | 2023-11-29 20:18 | 2023-11-30 20:18 | 24 | 2023-11-29 19:25 | 2023-11-29 22:10 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12586790 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | AHU-A1126-014 DUCT INSULATION DAMAGED C0-05-16 |  | FM008 |  | 2024-01-21 14:36 | 2024-01-21 15:36 | 2024-01-22 15:36 | 24 | 2024-01-21 14:40 | 2024-01-21 17:05 | 145 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12750007 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-05-19 |  | FM008 |  | 2024-03-21 07:58 | 2024-03-21 08:58 | 2024-03-22 08:58 | 24 | 2024-03-21 08:05 | 2024-03-21 17:00 | 535 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2023-11463387 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT ACCESS DOOR AIR LEAKAGE - ROOM C0-05-19 |  | FM008 |  | 2023-02-13 19:03 | 2023-02-13 20:03 | 2023-02-14 20:03 | 24 | 2023-02-13 19:10 | 2023-02-13 21:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 17573 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11630744 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | AHU-A1126-014 – ACCESS DOOR AIR LEAKAGE- - |  | FM008 |  | 2023-04-08 19:07 | 2023-04-08 20:07 | 2023-04-09 20:07 | 24 | 2023-04-08 19:15 | 2023-04-08 21:40 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11782097 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | TRANSFER C - NEAR C0-05-19 - AC NOT WORKING/HOT |  | FM008 |  | 2023-05-10 06:28 | 2023-05-10 07:28 | 2023-05-11 07:28 | 24 | 2023-05-10 06:35 | 2023-05-10 07:45 | 70 | 50 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 106972 |  |  | 114501 | Kumar, Mr. Daniel Pradeep | N - - - |  | Voice Communication
| CM-2023-11842067 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C 0 08 16 |  | FM008 |  | 2023-06-03 14:50 | 2023-06-03 15:50 | 2023-06-04 15:50 | 24 | 2023-06-03 14:59 | 2023-06-03 17:29 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 89127 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11195388 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | AHU-A1126-014 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-11-17 07:02 | 2022-11-17 08:02 | 2022-11-18 08:02 | 24 | 2022-11-17 07:10 | 2022-11-17 09:20 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11196502 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1126-014 – C0-05-15 |  | FM008 |  | 2022-11-19 07:33 | 2022-11-19 08:33 | 2022-11-20 08:33 | 24 | 2022-11-19 07:40 | 2022-11-19 09:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11329757 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE -AHU-A1126-014) |  | FM008 |  | 2022-12-29 19:38 | 2022-12-29 20:38 | 2022-12-30 20:38 | 24 | 2022-12-29 19:45 | 2022-12-29 23:15 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12133042 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-014 – C0-05-19 |  | FM008 |  | 2023-08-28 19:39 | 2023-08-28 20:39 | 2023-08-29 20:39 | 24 | 2023-08-28 19:45 | 2023-08-28 22:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12364373 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – (AHU-A1126-014) – C0 05 19 |  | FM008 |  | 2023-11-09 19:22 | 2023-11-09 20:22 | 2023-11-10 20:22 | 24 | 2023-11-09 19:30 | 2023-11-09 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 132112 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12690504 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | CABIN LAMP HOLDER FAULTY – C0-05-19 |  | FM008 |  | 2024-02-27 15:26 | 2024-02-27 16:26 | 2024-02-28 16:26 | 24 | 2024-02-27 15:30 | 2024-02-27 17:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 17053 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2024-12756115 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-014) T0 05 19 |  | FM008 |  | 2024-03-23 07:04 | 2024-03-23 08:04 | 2024-03-24 08:04 | 24 | 2024-03-23 07:10 | 2024-03-23 13:15 | 365 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12844819 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-014, C0-05-19 |  | FM008 |  | 2024-04-22 07:19 | 2024-04-22 08:19 | 2024-04-23 08:19 | 24 | 2024-04-22 07:25 | 2024-04-22 09:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12595346 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | AHU-FILTER DIRTY -CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2024-01-25 19:35 | 2024-01-25 20:35 | 2024-01-26 20:35 | 24 | 2024-01-25 19:40 | 2024-01-25 22:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11934214 | ASD-COC-GFL005-AHU107 | AIR HANDLING UNIT-05 | THIRD INSULATION DAMAGED –(AHU-A1126-014)– C0 05 19 |  | FM008 |  | 2023-06-27 20:34 | 2023-06-27 21:34 | 2023-06-28 21:34 | 24 | 2023-06-27 20:40 | 2023-06-27 22:40 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | 11844 | Dantes, Mr. Arun William | N - - - |  | Voice Communication
| CM-2022-10100007 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - ROOM C0-05-12 |  | FM008 |  | 2022-02-02 14:04 | 2022-02-02 15:04 | 2022-02-03 15:04 | 24 | 2022-02-02 14:10 | 2022-02-02 15:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11567609 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-05-12 |  | FM008 |  | 2023-03-15 20:55 | 2023-03-15 21:55 | 2023-03-16 21:55 | 24 | 2023-03-15 21:05 | 2023-03-15 23:30 | 145 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2024-12538873 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM ACCESS DOOR - AHU-A1126-021 – C0-05-12 |  | FM008 |  | 2024-01-08 08:31 | 2024-01-08 09:31 | 2024-01-09 09:31 | 24 | 2024-01-08 08:35 | 2024-01-08 11:00 | 145 | 435 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12589776 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – AHU-A1126-021 – MECHANICAL ROOM C0-05-12 |  | FM008 |  | 2024-01-22 13:37 | 2024-01-22 14:37 | 2024-01-23 14:37 | 24 | 2024-01-22 13:45 | 2024-01-22 15:20 | 95 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12847209 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AC TOO WARM -REMOTE GATE C87 |  | FM008 |  | 2024-04-23 08:49 | 2024-04-23 09:49 | 2024-04-24 09:49 | 24 | 2024-04-23 08:55 | 2024-04-23 09:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | T23661 | Jalaludeen, Mr. Jasid | N - - - |  | Voice Communication
| CM-2022-11160561 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | FILTER DIRTY – AHU-A1126-021 – C0-06-16 |  | FM008 |  | 2022-11-05 19:22 | 2022-11-05 20:22 | 2022-11-06 20:22 | 24 | 2022-11-05 19:30 | 2022-11-05 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11562391 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-03-13 18:56 | 2023-03-13 19:56 | 2023-03-14 19:56 | 24 | 2023-03-13 19:05 | 2023-03-13 22:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | BMS
| CM-2023-11661208 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AHU-A1126-021 – FILTER DIRTY- |  | FM008 |  | 2023-04-15 19:23 | 2023-04-15 20:23 | 2023-04-16 20:23 | 24 | 2023-04-15 19:30 | 2023-04-15 22:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11940120 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-05-12 |  | FM008 |  | 2023-07-04 19:04 | 2023-07-04 20:04 | 2023-07-05 20:04 | 24 | 2023-07-04 19:10 | 2023-07-04 22:00 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12603496 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-021 |  | FM008 |  | 2024-01-29 12:07 | 2024-01-29 13:07 | 2024-01-30 13:07 | 24 | 2024-01-29 12:15 | 2024-01-29 14:35 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12382885 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AC TOO HOT - C88 HOLDING AREA |  | FM008 |  | 2023-11-14 17:56 | 2023-11-14 18:26 | 2023-11-14 22:26 | 4 | 2023-11-14 18:00 | 2023-11-14 18:35 | 35 | 35 | 1 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | 106383 | Ramakrishnan, Ms. Reeshma | N - - - |  | Voice Communication
| CM-2024-12673090 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AHU-A1126-021 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2024-02-24 22:28 | 2024-02-24 23:28 | 2024-02-25 23:28 | 24 | 2024-02-24 22:35 | 2024-02-25 01:15 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12731576 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AHU CABIN LAMP IS FAULTY |  | FM008 |  | 2024-03-14 19:03 | 2024-03-14 20:03 | 2024-03-15 20:03 | 24 | 2024-03-14 19:10 | 2024-03-14 21:35 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 68060 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2024-12616675 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-021 – C0-05-12 |  | FM008 |  | 2024-02-04 08:47 | 2024-02-04 09:47 | 2024-02-05 09:47 | 24 | 2024-02-04 08:55 | 2024-02-04 10:40 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12768127 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-021) – C0 05 12 |  | FM008 |  | 2024-03-25 19:09 | 2024-03-25 20:09 | 2024-03-26 20:09 | 24 | 2024-03-25 19:15 | 2024-03-25 20:55 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12791796 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AHU-A1126-021 C0-05-28 CHILL WATER LINE PAINT FADED |  | FM008 |  | 2024-04-03 19:14 | 2024-04-03 20:14 | 2024-04-04 20:14 | 24 | 2024-04-03 19:20 | 2024-04-03 21:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 138627 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-10123550 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – C0-05-12 |  | FM008 |  | 2022-02-10 08:48 | 2022-02-10 09:48 | 2022-02-11 09:48 | 24 | 2022-02-10 09:00 | 2022-02-10 11:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11648574 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | AHU-A1126-021 – ACCESS DOOR AIR LEAKAGE – C0-05-12 |  | FM008 |  | 2023-04-10 19:12 | 2023-04-10 20:12 | 2023-04-11 20:12 | 24 | 2023-04-10 19:20 | 2023-04-10 22:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 94954 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10221750 | ASD-COC-GFL005-AHU113 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - AHU-A1126-021 – C0-05-12 |  | FM008 |  | 2022-03-07 12:08 | 2022-03-07 13:08 | 2022-03-08 13:08 | 24 | 2022-03-07 12:15 | 2022-03-07 16:25 | 250 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10118395 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – C0-05-19 |  | FM008 |  | 2022-02-09 08:35 | 2022-02-09 09:35 | 2022-02-10 09:35 | 24 | 2022-02-09 08:40 | 2022-02-09 15:00 | 380 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10321486 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DP1 ALARM AHU-A1126-022 C0-05-19 |  | FM008 |  | 2022-04-04 10:56 | 2022-04-04 11:56 | 2022-04-05 11:56 | 24 | 2022-04-04 11:06 | 2022-04-04 12:15 | 69 | 138 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 85125 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11321592 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-26 19:21 | 2022-12-26 20:21 | 2022-12-27 20:21 | 24 | 2022-12-26 19:30 | 2022-12-26 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11842005 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU-A1126-022 DUCT INSULATION DAMAGED C0-05-19 |  | FM008 |  | 2023-06-03 10:42 | 2023-06-03 11:42 | 2023-06-04 11:42 | 24 | 2023-06-03 10:45 | 2023-06-03 13:30 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 89127 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12367297 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AC TOO HOT - BOARDING GATE AREA REMOTE GATE C82 TO C93 |  | FM008 |  | 2023-11-12 07:14 | 2023-11-12 08:14 | 2023-11-13 08:14 | 24 | 2023-11-12 07:20 | 2023-11-12 13:00 | 340 | 50 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 87807 |  |  | 82878 | Mbuyazi, Ms. Mbali Emelda | N - - - |  | Voice Communication
| CM-2024-12600022 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C0-05-19 |  | FM008 |  | 2024-01-31 10:45 | 2024-01-31 11:45 | 2024-02-01 11:45 | 24 | 2024-01-31 10:50 | 2024-01-31 16:10 | 320 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11568820 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AC DUCT AIR LEAKAGE & DUST ACCUMULATED- NEAR C0-06-36 |  | FM008 |  | 2023-03-18 09:48 | 2023-03-18 10:48 | 2023-03-19 10:48 | 24 | 2023-03-18 09:55 | 2023-03-18 11:20 | 85 | 255 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17573 | 87807 |  |  | 128087 | Hasan, Mr. MD Ziaul | N - - - |  | Voice Communication
| CM-2023-11941875 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE ,AHU-A1126-022, C0-05-19 |  | FM008 |  | 2023-07-03 19:17 | 2023-07-03 20:17 | 2023-07-04 20:17 | 24 | 2023-07-03 19:21 | 2023-07-03 21:55 | 154 | 308 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-11160562 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-022 – C0-05-19 |  | FM008 |  | 2022-11-05 19:23 | 2022-11-05 20:23 | 2022-11-06 20:23 | 24 | 2022-11-05 19:30 | 2022-11-05 23:35 | 245 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11637765 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-022 - C0-05-19 - CM-2023-01-1426 |  | FM008 |  | 2023-04-09 22:48 | 2023-04-09 23:48 | 2023-04-10 23:48 | 24 | 2023-04-09 22:55 | 2023-04-10 00:55 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 17053 |  |  | FM10657 | RAJA | - - - |  | Voice Communication
| CM-2023-12087121 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-08-14 07:29 | 2023-08-14 08:29 | 2023-08-15 08:29 | 24 | 2023-08-14 07:35 | 2023-08-14 12:03 | 268 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12521363 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU-A1126-022 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2023-12-31 14:30 | 2023-12-31 15:30 | 2024-01-01 15:30 | 24 | 2023-12-31 14:35 | 2023-12-31 18:30 | 235 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 119320 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12690591 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU-A1126-022 CHILLER WATER LINE PAINT FADED |  | FM008 |  | 2024-02-28 00:46 | 2024-02-28 01:46 | 2024-02-29 01:46 | 24 | 2024-02-28 00:50 | 2024-02-28 03:00 | 130 | 260 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 119320 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12780936 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-AIR HANDLING UNIT 114 (TAG NO:AHU-A1126-022)-CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2024-03-31 07:42 | 2024-03-31 08:42 | 2024-04-01 08:42 | 24 | 2024-03-31 07:50 | 2024-03-31 10:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12818006 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU-A1126-022 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-04-07 23:08 | 2024-04-08 00:08 | 2024-04-09 00:08 | 24 | 2024-04-07 23:15 | 2024-04-08 01:45 | 150 | 600 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12515010 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-29 20:05 | 2023-12-29 21:05 | 2023-12-30 21:05 | 24 | 2023-12-29 20:10 | 2023-12-29 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10267823 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | AHU-A1126-022 - DUCT INSULATION DAMAGED - C0-05-19 |  | FM008 |  | 2022-03-20 13:32 | 2022-03-20 14:32 | 2022-03-21 14:32 | 24 | 2022-03-20 13:40 | 2022-03-20 15:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 87807 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10932811 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM - CON C, LEVEL-0, C0-05-19 |  | FM008 |  | 2022-08-12 19:52 | 2022-08-12 20:52 | 2022-08-13 20:52 | 24 | 2022-08-12 20:00 | 2022-08-12 20:30 | 30 | 30 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 55709 |  |  | FM0459 | MANHANDAVIDA SHAHEEL | N - - - |  | BMS
| CM-2022-10171261 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-02-24 07:49 | 2022-02-24 08:49 | 2022-02-25 08:49 | 24 | 2022-02-24 07:55 | 2022-02-24 14:55 | 420 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11512724 | ASD-COC-GFL005-AHU114 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1126-022 |  | FM008 |  | 2023-03-04 15:00 | 2023-03-04 16:00 | 2023-03-05 16:00 | 24 | 2023-03-04 15:10 | 2023-03-04 17:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10154629 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AHU123 BELT DAMAGED - BELT DAMAGED |  | FM008 |  | 2022-02-22 07:18 | 2022-02-22 08:18 | 2022-02-23 08:18 | 24 | 2022-02-22 07:25 | 2022-02-22 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106976 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10162107 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-23 07:17 | 2022-02-23 08:17 | 2022-02-24 08:17 | 24 | 2022-02-23 07:25 | 2022-02-23 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-12140477 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) - CONCOURSE C ENTIRE BAGGAGE HALL AREA |  | FM008 |  | 2023-09-01 06:01 | 2023-09-01 07:01 | 2023-09-02 07:01 | 24 | 2023-09-01 06:05 | 2023-09-01 08:05 | 120 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | 99335 | Mohammed, Mr. Zuhebuddin | N - - - |  | Voice Communication
| CM-2023-12151914 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2023-09-04 15:22 | 2023-09-04 16:22 | 2023-09-05 16:22 | 24 | 2023-09-04 15:30 | 2023-09-04 18:15 | 165 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12252827 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C0-05-12 |  | FM008 |  | 2023-10-05 08:15 | 2023-10-05 09:15 | 2023-10-06 09:15 | 24 | 2023-10-05 08:20 | 2023-10-05 10:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12385353 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC VENTS DIRTY - NEAR BELTS TX-07 & TX-09 BAGGAGE AREA CON C |  | FM008 |  | 2023-11-17 15:41 | 2023-11-17 16:41 | 2023-11-18 16:41 | 24 | 2023-11-17 15:45 | 2023-11-17 22:00 | 375 | 545 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 17053 |  |  | 132149 | Palubag, Ms. Roxan Bahian | N - - - |  | Voice Communication
| CM-2023-12422407 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-031 – C0-05-12 |  | FM008 |  | 2023-11-28 14:53 | 2023-11-28 15:53 | 2023-11-29 15:53 | 24 | 2023-11-28 15:00 | 2023-11-28 18:15 | 195 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11782845 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-05-10 07:23 | 2023-05-10 08:23 | 2023-05-11 08:23 | 24 | 2023-05-10 07:30 | 2023-05-10 09:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 106972 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11885686 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER IS DIRTY |  | FM008 |  | 2023-06-16 21:19 | 2023-06-16 22:19 | 2023-06-17 22:19 | 24 | 2023-06-16 21:25 | 2023-06-16 23:55 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11994976 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-031- C0 05 12 |  | FM008 |  | 2023-07-18 12:38 | 2023-07-18 13:38 | 2023-07-19 13:38 | 24 | 2023-07-18 12:45 | 2023-07-18 14:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12041679 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | WATER LEAKING FROM THE CEILING – NEAR TO C0-05-34 |  | FM008 |  | 2023-08-03 13:09 | 2023-08-03 14:09 | 2023-08-04 14:09 | 24 | 2023-08-03 13:15 | 2023-08-03 14:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 132112 | 17053 |  |  | C09031 | AMAN KUMAR | N - - - |  | Voice Communication
| CM-2023-12064681 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | C0-05-04 AC NOT WORKING |  | FM008 |  | 2023-08-09 01:15 | 2023-08-09 02:15 | 2023-08-10 02:15 | 24 | 2023-08-09 01:20 | 2023-08-09 03:30 | 130 | 35 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | FM11723 | Nakanwagi, Ms. Safinah | N - - - |  | Voice Communication
| CM-2023-12067017 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS-AHU-A1126-031-MECHANICAL ROOM C0-05-12 |  | FM008 |  | 2023-08-12 13:09 | 2023-08-12 14:09 | 2023-08-13 14:09 | 24 | 2023-08-12 13:15 | 2023-08-12 19:00 | 345 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12137396 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) - CONCOURSE C ENTIRE BAGGAGE HALL AREA |  | FM008 |  | 2023-08-31 13:50 | 2023-08-31 14:50 | 2023-09-01 14:50 | 24 | 2023-08-31 13:55 | 2023-08-31 14:00 | 5 | 5 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 72520 | Sanin, Mr. Fedee Ollet | N - - - |  | Voice Communication
| CM-2023-12164500 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AIR HANDLING UNIT 123 (TAG NO:AHU-A1126-031)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2023-09-07 19:15 | 2023-09-07 20:15 | 2023-09-08 20:15 | 24 | 2023-09-07 19:20 | 2023-09-07 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | E-mail
| CM-2023-12159266 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC NOT COOLING ENOUGH IN BHS CONVEYOR AREA – NEAR C0-05-25 |  | FM008 |  | 2023-09-09 06:07 | 2023-09-09 07:07 | 2023-09-10 07:07 | 24 | 2023-09-09 06:15 | 2023-09-09 08:00 | 105 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 95217 |  |  | 126689 | Rajkumar, Mr. Vinothkumar | N - - - |  | Voice Communication
| CM-2023-12184500 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED – (AHU-A1126-031 ) – C0 05 12 |  | FM008 |  | 2023-09-13 12:53 | 2023-09-13 13:53 | 2023-09-14 13:53 | 24 | 2023-09-13 13:00 | 2023-09-13 18:00 | 300 | 295 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 132112 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12571836 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2024-01-18 18:59 | 2024-01-18 19:59 | 2024-01-19 19:59 | 24 | 2024-01-18 19:05 | 2024-01-18 21:25 | 140 | 280 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2024-12690538 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC GRILL DIRTY - AHU-A1126-031 – C0-04-15 |  | FM008 |  | 2024-02-27 19:34 | 2024-02-27 20:34 | 2024-02-28 20:34 | 24 | 2024-02-27 19:40 | 2024-02-27 23:30 | 230 | 460 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12793797 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C0-05-12 |  | FM008 |  | 2024-04-04 21:22 | 2024-04-04 22:22 | 2024-04-05 22:22 | 24 | 2024-04-04 21:30 | 2024-04-04 23:35 | 125 | 250 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17053 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12087133 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -C0-05-12 |  | FM008 |  | 2023-08-14 07:54 | 2023-08-14 08:54 | 2023-08-15 08:54 | 24 | 2023-08-14 08:00 | 2023-08-14 16:15 | 495 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM12472 | Arumuga Nainar Senthilkumar, | N - - - |  | BMS
| CM-2023-12163656 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC NOT COOLING ENOUGH IN BHS CONVEYOR AREA – NEAR C0-05-25 |  | FM008 |  | 2023-09-08 06:13 | 2023-09-08 07:13 | 2023-09-09 07:13 | 24 | 2023-09-08 06:20 | 2023-09-08 08:05 | 105 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 99335 | Mohammed, Mr. Zuhebuddin | N - - - |  | Voice Communication
| CM-2023-12187173 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC NOT WORKING |  | FM008 |  | 2023-09-13 19:00 | 2023-09-13 20:00 | 2023-09-14 20:00 | 24 | 2023-09-13 19:05 | 2023-09-13 20:05 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 114502 | Khan, Mr. Mohammadshahjad Mohammadsiraj | N - - - |  | Voice Communication
| CM-2023-12277878 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 123 (TAG NO:AHU-A1126-031 |  | FM008 |  | 2023-10-09 22:40 | 2023-10-09 23:40 | 2023-10-10 23:40 | 24 | 2023-10-09 22:45 | 2023-10-10 01:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2024-12606012 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2024-01-28 19:11 | 2024-01-28 20:11 | 2024-01-29 20:11 | 24 | 2024-01-28 19:20 | 2024-01-28 21:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12741786 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AHU-A1126-031 DUCT INSULATION DAMAGE C0-05-21 |  | FM008 |  | 2024-03-22 07:36 | 2024-03-22 08:36 | 2024-03-23 08:36 | 24 | 2024-03-22 07:40 | 2024-03-22 11:00 | 200 | 515 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12258111 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-06 19:24 | 2023-10-06 20:24 | 2023-10-07 20:24 | 24 | 2023-10-06 19:35 | 2023-10-06 22:05 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12505200 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER DIRTY – AHU-A1126-031- C0 0512 |  | FM008 |  | 2023-12-26 09:58 | 2023-12-26 10:58 | 2023-12-27 10:58 | 24 | 2023-12-26 10:05 | 2023-12-26 11:30 | 85 | 255 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12603493 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-031 |  | FM008 |  | 2024-01-29 12:05 | 2024-01-29 13:05 | 2024-01-30 13:05 | 24 | 2024-01-29 12:10 | 2024-01-29 14:25 | 135 | 405 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12754573 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | BAGGAGE BELT AREA TX06&09 AC VENT DUSTY- C0-04-15 |  | FM008 |  | 2024-03-23 11:42 | 2024-03-23 12:42 | 2024-03-24 12:42 | 24 | 2024-03-23 11:50 | 2024-03-23 14:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | 132149 | Palubag, Ms. Roxan Bahian | N - - - |  | Voice Communication
| CM-2024-12671796 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | FILTER DIRTY -AIR HANDLING UNIT 123 (TAG NO:AHU-A1126-031) |  | FM008 |  | 2024-02-22 19:12 | 2024-02-22 20:12 | 2024-02-23 20:12 | 24 | 2024-02-22 19:20 | 2024-02-22 21:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2022-10230312 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | D1 FILTER ALARM -C0-05-12 |  | FM008 |  | 2022-03-09 22:05 | 2022-03-09 23:05 | 2022-03-10 23:05 | 24 | 2022-03-09 22:10 | 2022-03-10 00:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-10044795 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-01-14 20:26 | 2022-01-14 21:26 | 2022-01-15 21:26 | 24 | 2022-01-14 20:30 | 2022-01-14 22:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | BLOCKAGE OF AIR FLOW | REPAIR/REPLACE | 68060 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | BMS
| CM-2023-12155127 | ASD-COC-GFL005-AHU123 | AIR HANDLING UNIT-05 | AC NOT COOLING ENOUGH IN BHS CONVEYOR AREA – NEAR C0-05-25 |  | FM008 |  | 2023-09-06 16:01 | 2023-09-06 17:01 | 2023-09-07 17:01 | 24 | 2023-09-06 16:10 | 2023-09-06 18:00 | 110 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | 74736 | Cyriac, Mr. Shibu | N - - - |  | Voice Communication
| CM-2022-10154627 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU124– FILTER BLOCKED – C0-07-12 |  | FM008 |  | 2022-02-22 07:14 | 2022-02-22 08:14 | 2022-02-23 08:14 | 24 | 2022-02-22 07:20 | 2022-02-22 08:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106976 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2023-12007275 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-07-24 14:12 | 2023-07-24 15:12 | 2023-07-25 15:12 | 24 | 2023-07-24 14:20 | 2023-07-24 16:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12151916 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-09-04 15:23 | 2023-09-04 16:23 | 2023-09-05 16:23 | 24 | 2023-09-04 15:30 | 2023-09-04 18:10 | 160 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12385482 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-11-18 07:10 | 2023-11-18 08:10 | 2023-11-19 08:10 | 24 | 2023-11-18 07:15 | 2023-11-18 14:00 | 405 | 305 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12422699 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-032 – C0-05-12 |  | FM008 |  | 2023-11-29 12:26 | 2023-11-29 13:26 | 2023-11-30 13:26 | 24 | 2023-11-29 12:35 | 2023-11-29 16:15 | 220 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2024-12606048 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2024-01-28 21:22 | 2024-01-28 22:22 | 2024-01-29 22:22 | 24 | 2024-01-28 21:30 | 2024-01-28 23:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11782846 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | FILTER DIRTY TAG NO:AHU-A1126-032)- |  | FM008 |  | 2023-05-10 07:24 | 2023-05-10 08:24 | 2023-05-11 08:24 | 24 | 2023-05-10 07:30 | 2023-05-10 09:20 | 110 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 106972 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11885687 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER IS DIRTY |  | FM008 |  | 2023-06-16 21:20 | 2023-06-16 22:20 | 2023-06-17 22:20 | 24 | 2023-06-16 21:25 | 2023-06-16 23:55 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12004926 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU-A1126-032-(FILTER DIRTY ) |  | FM008 |  | 2023-07-25 07:21 | 2023-07-25 08:21 | 2023-07-26 08:21 | 24 | 2023-07-25 07:30 | 2023-07-25 09:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12163744 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - AHU-A1126-032 - MECHANICAL ROOM C0-05-12 |  | FM008 |  | 2023-09-08 11:20 | 2023-09-08 12:20 | 2023-09-09 12:20 | 24 | 2023-09-08 11:25 | 2023-09-08 13:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12408377 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | FILTER DIRTY -C0-05-12 |  | FM008 |  | 2023-11-25 19:55 | 2023-11-25 20:55 | 2023-11-26 20:55 | 24 | 2023-11-25 20:05 | 2023-11-25 22:40 | 155 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12483593 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C0-05-12 |  | FM008 |  | 2023-12-15 15:42 | 2023-12-15 16:42 | 2023-12-16 16:42 | 24 | 2023-12-15 15:50 | 2023-12-15 16:50 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12571837 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2024-01-18 19:01 | 2024-01-18 20:01 | 2024-01-19 20:01 | 24 | 2024-01-18 19:10 | 2024-01-18 23:55 | 285 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 68060 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2024-12793798 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C0-05-12 |  | FM008 |  | 2024-04-04 21:23 | 2024-04-04 22:23 | 2024-04-05 22:23 | 24 | 2024-04-04 21:30 | 2024-04-04 23:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11175984 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2022-11-09 09:09 | 2022-11-09 10:09 | 2022-11-10 10:09 | 24 | 2022-11-09 09:15 | 2022-11-09 16:30 | 435 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-12087120 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-08-14 07:28 | 2023-08-14 08:28 | 2023-08-15 08:28 | 24 | 2023-08-14 07:35 | 2023-08-14 14:15 | 400 | 370 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2024-12612333 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKING -C3-05-03 |  | FM008 |  | 2024-02-01 09:50 | 2024-02-01 10:50 | 2024-02-02 10:50 | 24 | 2024-02-01 09:55 | 2024-02-01 16:30 | 395 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2024-12610092 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1126-032, C0-05-12 |  | FM008 |  | 2024-02-02 12:28 | 2024-02-02 13:28 | 2024-02-03 13:28 | 24 | 2024-02-02 12:35 | 2024-02-02 14:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12319726 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-032 – C0-05-12 |  | FM008 |  | 2023-10-24 07:06 | 2023-10-24 08:06 | 2023-10-25 08:06 | 24 | 2023-10-24 07:10 | 2023-10-24 09:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12491337 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU-A1126-032 SUPPLY AIR LOW ALARM |  | FM008 |  | 2023-12-20 08:13 | 2023-12-20 09:13 | 2023-12-21 09:13 | 24 | 2023-12-20 08:20 | 2023-12-20 18:45 | 625 | 215 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12505201 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | FILTER DIRTY – AHU-A1126-032 – C0 0512 |  | FM008 |  | 2023-12-26 10:02 | 2023-12-26 11:02 | 2023-12-27 11:02 | 24 | 2023-12-26 10:05 | 2023-12-26 11:45 | 100 | 300 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12756114 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-032) T0 05 12 |  | FM008 |  | 2024-03-23 07:02 | 2024-03-23 08:02 | 2024-03-24 08:02 | 24 | 2024-03-23 07:10 | 2024-03-23 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12343942 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU-A1126-032 SUPPLY AIR LOW ALARM |  | FM008 |  | 2023-11-02 09:27 | 2023-11-02 10:27 | 2023-11-03 10:27 | 24 | 2023-11-02 09:35 | 2023-11-02 17:45 | 490 | 320 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 68485 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2024-12671797 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | FILTER DIRTY -AIR HANDLING UNIT 124 (TAG NO:AHU-A1126-032)-CONCOURSE C-GROUND FLOOR AREA 005 |  | FM008 |  | 2024-02-22 19:15 | 2024-02-22 20:15 | 2024-02-23 20:15 | 24 | 2024-02-22 19:20 | 2024-02-22 21:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2024-12855485 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS, AHU-A1126-032, MECHANICAL ROOM C0-05-12 |  | FM008 |  | 2024-04-29 11:05 | 2024-04-29 12:05 | 2024-04-30 12:05 | 24 | 2024-04-29 11:10 | 2024-04-29 12:15 | 65 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10313796 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ASD-COC-GFL005-AHU124-FIL877 AHU-A1126-032 FILTERS 877-AIR HANDLING UNIT 124 (TAG NO:AHU-A1126-032)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 005 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP12.CONC0512.AHU032.SYSALM. |  | FM008 |  | 2022-04-04 14:40 | 2022-04-04 15:40 | 2022-04-05 15:40 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | GROUND FLOOR AREA 005 | N | DAMAGED |  |  | 94953 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - | ASSET NOT HANDED OVER | E-mail
| CM-2023-12256421 | ASD-COC-GFL005-AHU124 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C0-05-12 |  | FM008 |  | 2023-10-07 21:16 | 2023-10-07 22:16 | 2023-10-08 22:16 | 24 | 2023-10-07 21:20 | 2023-10-08 00:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-11178265 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | AHU-A1126-015 SUPPLY DUCT INSULATION DAMAGED C0-06-07 |  | FM008 |  | 2022-11-09 19:32 | 2022-11-09 20:32 | 2022-11-10 20:32 | 24 | 2022-11-09 19:40 | 2022-11-10 01:15 | 335 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11385176 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | AHU-A1126-015 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-18 14:00 | 2023-01-18 15:00 | 2023-01-19 15:00 | 24 | 2023-01-18 14:05 | 2023-01-18 17:35 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12810162 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-015) |  | FM008 |  | 2024-04-08 07:22 | 2024-04-08 08:22 | 2024-04-09 08:22 | 24 | 2024-04-08 07:30 | 2024-04-08 13:35 | 365 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10949600 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | INSULATION DAMAGED - AHU-A1126-015 – C0-06-07 |  | FM008 |  | 2022-08-15 16:03 | 2022-08-15 17:03 | 2022-08-16 17:03 | 24 | 2022-08-15 16:10 | 2022-08-15 18:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11502975 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-015 |  | FM008 |  | 2023-03-01 20:22 | 2023-03-01 21:22 | 2023-03-02 21:22 | 24 | 2023-03-01 20:31 | 2023-03-01 23:31 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11691418 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-015 – C0-06-07 |  | FM008 |  | 2023-04-21 21:09 | 2023-04-21 22:09 | 2023-04-22 22:09 | 24 | 2023-04-21 21:15 | 2023-04-21 23:55 | 160 | 480 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11956826 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AIR HANDLING UNIT 108 (TAG NO:AHU-A1126-015)-CONCOURSE C-GROUND FLOOR AREA 006 |  | FM008 |  | 2023-07-05 21:44 | 2023-07-05 22:44 | 2023-07-06 22:44 | 24 | 2023-07-05 21:50 | 2023-07-06 00:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12164167 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | AHU-A1126-015 DUCT INSULATION DAMAGED C0-06-07 |  | FM008 |  | 2023-09-08 22:24 | 2023-09-08 23:24 | 2023-09-09 23:24 | 24 | 2023-09-08 22:30 | 2023-09-09 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11235573 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -C0-06-17 |  | FM008 |  | 2022-12-04 11:21 | 2022-12-04 12:21 | 2022-12-05 12:21 | 24 | 2022-12-04 11:30 | 2022-12-04 15:00 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12749499 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-015 – C0-06-07 |  | FM008 |  | 2024-03-21 06:59 | 2024-03-21 07:59 | 2024-03-22 07:59 | 24 | 2024-03-21 07:10 | 2024-03-21 13:10 | 360 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10045407 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | AHU-A1126-015 – CHILLED WATER LINE PAINT FADED- - |  | FM008 |  | 2022-01-13 12:29 | 2022-01-13 13:29 | 2022-01-14 13:29 | 24 | 2022-01-13 12:35 | 2022-01-13 14:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11195354 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | AHU-A1126-015 MARINE LIGHT NOT WORKING C0-06-07 |  | FM008 |  | 2022-11-17 00:18 | 2022-11-17 01:18 | 2022-11-18 01:18 | 24 | 2022-11-17 00:25 | 2022-11-17 02:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10226402 | ASD-COC-GFL006-AHU108 | AIR HANDLING UNIT-05 | AHU108 DUCT INSULATION DAMAGED – C0-06-07 |  | FM008 |  | 2022-03-09 16:22 | 2022-03-09 17:22 | 2022-03-10 17:22 | 24 | 2022-03-09 16:30 | 2022-03-09 18:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106976 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-11138247 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | V BELT DAMAGED -C0-06-10 |  | FM008 |  | 2022-10-27 22:58 | 2022-10-27 23:58 | 2022-10-28 23:58 | 24 | 2022-10-27 23:04 | 2022-10-28 03:30 | 266 | 186 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11178264 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AHU-A1126-016 RETURN DUCT INSULATION DAMAGED C0-06-10 |  | FM008 |  | 2022-11-09 19:32 | 2022-11-09 20:32 | 2022-11-10 20:32 | 24 | 2022-11-09 19:35 | 2022-11-09 21:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11250698 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - C0-06-10 |  | FM008 |  | 2022-12-04 20:03 | 2022-12-04 21:03 | 2022-12-05 21:03 | 24 | 2022-12-04 20:10 | 2022-12-04 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11885594 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | CABIN LAMP NOT WORKING-AIR HANDLING UNIT 109 (TAG NO:AHU-A1126-016 |  | FM008 |  | 2023-06-16 13:21 | 2023-06-16 14:21 | 2023-06-17 14:21 | 24 | 2023-06-16 13:25 | 2023-06-16 17:18 | 233 | 181 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17336 | 87807 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-12229423 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-09-28 16:05 | 2023-09-28 17:05 | 2023-09-29 17:05 | 24 | 2023-09-28 16:10 | 2023-09-28 18:10 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12586791 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AHU-A1126-016 C0-06-10 DUCT INSULATION DAMAGED |  | FM008 |  | 2024-01-21 14:37 | 2024-01-21 15:37 | 2024-01-22 15:37 | 24 | 2024-01-21 14:45 | 2024-01-21 16:40 | 115 | 345 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11495182 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-06-10 |  | FM008 |  | 2023-03-01 12:05 | 2023-03-01 13:05 | 2023-03-02 13:05 | 24 | 2023-03-01 12:10 | 2023-03-01 14:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 94954 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11938338 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AHU-A1126-016-DUCT INSULATION DAMAGE -CONCOURSE C-GROUND FLOOR AREA 006 |  | FM008 |  | 2023-07-01 22:20 | 2023-07-01 23:20 | 2023-07-02 23:20 | 24 | 2023-07-01 22:25 | 2023-07-02 01:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12044327 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-05 07:16 | 2023-08-05 08:16 | 2023-08-06 08:16 | 24 | 2023-08-05 07:20 | 2023-08-05 10:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12067015 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-AHU-A1126-016-MECHANICAL ROOM C0-06-10 |  | FM008 |  | 2023-08-12 13:07 | 2023-08-12 14:07 | 2023-08-13 14:07 | 24 | 2023-08-12 13:15 | 2023-08-12 18:15 | 300 | 155 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 87807 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12410180 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - C0-06-10 |  | FM008 |  | 2023-11-25 14:24 | 2023-11-25 15:24 | 2023-11-26 15:24 | 24 | 2023-11-25 14:30 | 2023-11-25 16:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17053 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-11201198 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-016 – C0-06-10 |  | FM008 |  | 2022-11-20 12:30 | 2022-11-20 13:30 | 2022-11-21 13:30 | 24 | 2022-11-20 12:39 | 2022-11-20 17:40 | 301 | 456 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12178472 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY - AHU-A1126-016 – C0-06-10 – |  | FM008 |  | 2023-09-12 02:27 | 2023-09-12 03:27 | 2023-09-13 03:27 | 24 | 2023-09-12 02:35 | 2023-09-12 06:30 | 235 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2024-12624077 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-016 C0-06-10 |  | FM008 |  | 2024-02-07 08:58 | 2024-02-07 09:58 | 2024-02-08 09:58 | 24 | 2024-02-07 09:05 | 2024-02-07 10:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 138627 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2024-12714147 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-016 – C0-06-10 |  | FM008 |  | 2024-03-10 07:25 | 2024-03-10 08:25 | 2024-03-11 08:25 | 24 | 2024-03-10 07:35 | 2024-03-10 13:35 | 360 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12343359 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-10-30 20:35 | 2023-10-30 21:35 | 2023-10-31 21:35 | 24 | 2023-10-30 20:45 | 2023-10-30 23:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12689658 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-06-10 |  | FM008 |  | 2024-02-28 07:02 | 2024-02-28 08:02 | 2024-02-29 08:02 | 24 | 2024-02-28 07:10 | 2024-02-28 13:15 | 365 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10099530 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-016 |  | FM008 |  | 2022-01-30 22:43 | 2022-01-30 23:43 | 2022-01-31 23:43 | 24 | 2022-01-30 22:50 | 2022-01-31 00:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 85125 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10224530 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DP1- ALARM – C0-06-10 AIR HANDLING UNIT 109 (TAG NO:AHU-A1126-016)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 006 |  | FM008 |  | 2022-03-08 22:44 | 2022-03-08 23:44 | 2022-03-09 23:44 | 24 | 2022-03-08 22:50 | 2022-03-09 00:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 17154 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10251811 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AHU-A1126-016 – SUPPLY DUCT ACCESS DOOR AIR LEAKAGE – C0-06-10 |  | FM008 |  | 2022-03-16 01:46 | 2022-03-16 02:46 | 2022-03-17 02:46 | 24 | 2022-03-16 01:50 | 2022-03-16 03:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10998505 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-016 – C0-06-10 |  | FM008 |  | 2022-09-07 15:48 | 2022-09-07 16:48 | 2022-09-08 16:48 | 24 | 2022-09-07 15:55 | 2022-09-07 17:48 | 113 | 179 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-11327010 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-27 19:42 | 2022-12-27 20:42 | 2022-12-28 20:42 | 24 | 2022-12-27 19:50 | 2022-12-27 23:20 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-10226403 | ASD-COC-GFL006-AHU109 | AIR HANDLING UNIT-05 | AHU109 DUCT INSULATION DAMAGED – C0-06-07 |  | FM008 |  | 2022-03-09 16:27 | 2022-03-09 17:27 | 2022-03-10 17:27 | 24 | 2022-03-09 16:35 | 2022-03-09 18:35 | 120 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106976 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-10050150 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | BOARDING GATE C12 – AC IS NOT WORKING (PASSENGER'S COMPLAINT) |  | FM008 |  | 2022-01-16 06:34 | 2022-01-16 07:04 | 2022-01-16 11:04 | 4 | 2022-01-16 06:40 | 2022-01-16 08:00 | 80 | 65 | 2 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94954 | 55709 |  |  | 97963 | Qureshi, Mr. Shaqib Mohammed Adil | N - - - |  | Voice Communication
| CM-2022-10128509 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | AHU-A1126-017 - CHILL WATER LINE PAINT FADED – C0-08-04 |  | FM008 |  | 2022-02-10 15:08 | 2022-02-10 16:08 | 2022-02-11 16:08 | 24 | 2022-02-10 15:15 | 2022-02-10 17:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11081261 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - TAG NO:AHU-A1126-017 |  | FM008 |  | 2022-10-07 07:13 | 2022-10-07 08:13 | 2022-10-08 08:13 | 24 | 2022-10-07 07:20 | 2022-10-07 11:05 | 225 | 110 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11298100 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-12-21 10:50 | 2022-12-21 11:50 | 2022-12-22 11:50 | 24 | 2022-12-21 10:55 | 2022-12-21 15:30 | 275 | 635 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11502758 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-02-28 20:03 | 2023-02-28 21:03 | 2023-03-01 21:03 | 24 | 2023-02-28 20:10 | 2023-02-28 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 94954 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11614766 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | AHU-A1126-017)-DUCT INSULATION DAMAGE]-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2023-04-02 10:45 | 2023-04-02 11:45 | 2023-04-03 11:45 | 24 | 2023-04-02 10:50 | 2023-04-02 13:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12007875 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-017 – C0-08-04 |  | FM008 |  | 2023-07-27 07:01 | 2023-07-27 08:01 | 2023-07-28 08:01 | 24 | 2023-07-27 07:10 | 2023-07-27 10:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11177067 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR AIR LEAKAGE – C0-08-04 |  | FM008 |  | 2022-11-12 15:02 | 2022-11-12 16:02 | 2022-11-13 16:02 | 24 | 2022-11-12 15:10 | 2022-11-12 17:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 87807 |  |  | FM5678 | Muhamedkwaja Muhamed Yahya , Mr. Alumkoottathil | N - - - |  | Voice Communication
| CM-2022-11231339 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C0-08-04 |  | FM008 |  | 2022-11-29 00:05 | 2022-11-29 01:05 | 2022-11-30 01:05 | 24 | 2022-11-29 00:10 | 2022-11-29 03:10 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12164168 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | AHU-A1126-017 DUCT INSULATION DAMAGED C0-08-04 |  | FM008 |  | 2023-09-08 22:27 | 2023-09-08 23:27 | 2023-09-09 23:27 | 24 | 2023-09-08 22:30 | 2023-09-09 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12427665 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-017 - MECHANICAL ROOM C0-08-04 |  | FM008 |  | 2023-11-29 19:26 | 2023-11-29 20:26 | 2023-11-30 20:26 | 24 | 2023-11-29 19:30 | 2023-11-29 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17573 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11568972 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | AHU-A1126-017 – AHU CABIN LIGHT IS NOT WORKING – C0-08-04 |  | FM008 |  | 2023-03-19 05:06 | 2023-03-19 06:06 | 2023-03-20 06:06 | 24 | 2023-03-19 05:10 | 2023-03-19 06:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94954 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2024-12741785 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | AHU-A1126-017 DUCT INSULATION DAMAGE C0-08-04 |  | FM008 |  | 2024-03-22 07:35 | 2024-03-22 08:35 | 2024-03-23 08:35 | 24 | 2024-03-22 07:40 | 2024-03-22 11:00 | 200 | 515 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12345915 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | AHU-A1126-017 ACCESS DOOR AIR LEAKAGE C0-08-04 |  | FM008 |  | 2023-11-02 14:50 | 2023-11-02 15:50 | 2023-11-03 15:50 | 24 | 2023-11-02 14:55 | 2023-11-02 17:30 | 155 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12595243 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-017 – C0-08-04 |  | FM008 |  | 2024-01-25 10:58 | 2024-01-25 11:58 | 2024-01-26 11:58 | 24 | 2024-01-25 11:05 | 2024-01-25 12:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12673015 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | FILTER DIRTY;AHU-A1126-017 – CO-08-04 |  | FM008 |  | 2024-02-24 11:42 | 2024-02-24 12:42 | 2024-02-25 12:42 | 24 | 2024-02-24 11:50 | 2024-02-24 14:20 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10145695 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE AHU-A1126-017 |  | FM008 |  | 2022-02-14 16:00 | 2022-02-14 17:00 | 2022-02-15 17:00 | 24 | 2022-02-14 16:05 | 2022-02-14 18:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2023-11960146 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-017 – C0-08-04 |  | FM008 |  | 2023-07-08 11:29 | 2023-07-08 12:29 | 2023-07-09 12:29 | 24 | 2023-07-08 11:35 | 2023-07-08 14:10 | 155 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-10121247 | ASD-COC-GFL008-AHU110 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED - AHU-1126-017 – C0-08-04 |  | FM008 |  | 2022-02-09 15:08 | 2022-02-09 16:08 | 2022-02-10 16:08 | 24 | 2022-02-09 15:15 | 2022-02-09 17:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 55709 |  |  | FM10078 | Abdulwahab, Mr. Mohamed Nasir | N - - - |  | Voice Communication
| CM-2022-10679529 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1126-018 – C0-08-16 |  | FM008 |  | 2022-05-21 22:31 | 2022-05-21 23:31 | 2022-05-22 23:31 | 24 | 2022-05-21 22:35 | 2022-05-21 23:55 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11620856 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-08-16 |  | FM008 |  | 2023-04-04 12:34 | 2023-04-04 13:34 | 2023-04-05 13:34 | 24 | 2023-04-04 12:40 | 2023-04-04 15:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11762792 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS,,PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP19.CONC0816.AHU018.SYSALM.DP1 / MECHANICAL ROOM C0-08-16 |  | FM008 |  | 2023-05-06 18:11 | 2023-05-06 19:11 | 2023-05-07 19:11 | 24 | 2023-05-06 18:15 | 2023-05-06 21:05 | 170 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 105233 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12103200 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-018 |  | FM008 |  | 2023-08-21 10:07 | 2023-08-21 11:07 | 2023-08-22 11:07 | 24 | 2023-08-21 10:15 | 2023-08-21 13:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2022-11177844 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - C0-08-16 |  | FM008 |  | 2022-11-12 09:20 | 2022-11-12 10:20 | 2022-11-13 10:20 | 24 | 2022-11-12 09:30 | 2022-11-12 11:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11214954 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | AHU-A1126-018 – DUCT INSULATION DAMAGED- |  | FM008 |  | 2022-11-21 11:20 | 2022-11-21 12:20 | 2022-11-22 12:20 | 24 | 2022-11-21 11:29 | 2022-11-21 14:00 | 151 | 453 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11363118 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1126-018)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2023-01-10 19:35 | 2023-01-10 20:35 | 2023-01-11 20:35 | 24 | 2023-01-10 19:40 | 2023-01-10 23:50 | 250 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11938292 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-08-16 |  | FM008 |  | 2023-07-01 19:01 | 2023-07-01 20:01 | 2023-07-02 20:01 | 24 | 2023-07-01 19:05 | 2023-07-01 22:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12124484 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-018 – C0-08-18 |  | FM008 |  | 2023-08-27 22:29 | 2023-08-27 23:29 | 2023-08-28 23:29 | 24 | 2023-08-27 22:35 | 2023-08-28 01:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12140977 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WOKRING - AHU-A1126-018 – C0-08-16 |  | FM008 |  | 2023-09-03 01:55 | 2023-09-03 02:55 | 2023-09-04 02:55 | 24 | 2023-09-03 02:00 | 2023-09-03 05:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 133396 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-12231482 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-28 13:14 | 2023-09-28 14:14 | 2023-09-29 14:14 | 24 | 2023-09-28 13:20 | 2023-09-28 15:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 87807 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2024-12745848 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-08-16 |  | FM008 |  | 2024-03-20 20:15 | 2024-03-20 21:15 | 2024-03-21 21:15 | 24 | 2024-03-20 20:20 | 2024-03-20 23:20 | 180 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12362270 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1121-018, C0-08-16 |  | FM008 |  | 2023-11-08 19:03 | 2023-11-08 20:03 | 2023-11-09 20:03 | 24 | 2023-11-08 19:10 | 2023-11-08 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2024-12568047 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | FILTER DIRTY AIR HANDLING UNIT 111 (TAG NO:AHU-A1126-018)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2024-01-14 13:12 | 2024-01-14 14:12 | 2024-01-15 14:12 | 24 | 2024-01-14 13:20 | 2024-01-14 16:00 | 160 | 215 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 95217 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12673016 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | FILTER DIRTY ;AHU-A1126-018 – C0-08-16 |  | FM008 |  | 2024-02-24 11:43 | 2024-02-24 12:43 | 2024-02-25 12:43 | 24 | 2024-02-24 11:50 | 2024-02-24 14:20 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10146740 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-018 |  | FM008 |  | 2022-02-17 11:59 | 2022-02-17 12:59 | 2022-02-18 12:59 | 24 | 2022-02-17 12:05 | 2022-02-17 14:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10190099 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | AHU-A1126-018; CHILLED WATER LINE PAINT FADED – C0-08-16 |  | FM008 |  | 2022-02-25 07:11 | 2022-02-25 08:11 | 2022-02-26 08:11 | 24 | 2022-02-25 07:20 | 2022-02-25 09:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11691465 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FUSED |  | FM008 |  | 2023-04-22 02:50 | 2023-04-22 03:50 | 2023-04-23 03:50 | 24 | 2023-04-22 02:55 | 2023-04-22 04:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11498193 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-02-26 21:09 | 2023-02-26 22:09 | 2023-02-27 22:09 | 24 | 2023-02-26 21:15 | 2023-02-26 23:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11526184 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | AHU-A1126-018 DUCT INSULATION DAMAGED C0-08-16 |  | FM008 |  | 2023-03-08 18:59 | 2023-03-08 19:59 | 2023-03-09 19:59 | 24 | 2023-03-08 19:05 | 2023-03-08 21:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12750729 | ASD-COC-GFL008-AHU111 | AIR HANDLING UNIT-05 | AHU-A1126-018 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-03-23 09:31 | 2024-03-23 10:31 | 2024-03-24 10:31 | 24 | 2024-03-23 09:40 | 2024-03-23 17:00 | 440 | 185 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10118393 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-08-21 |  | FM008 |  | 2022-02-09 08:33 | 2022-02-09 09:33 | 2022-02-10 09:33 | 24 | 2022-02-09 08:40 | 2022-02-09 11:30 | 170 | 455 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10145850 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023 DUCT INSULATION DAMAGED C0-08-21 |  | FM008 |  | 2022-02-15 11:48 | 2022-02-15 12:48 | 2022-02-16 12:48 | 24 | 2022-02-15 11:55 | 2022-02-15 13:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10354334 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP ONE FILTER DIRTY-C0-08-21 |  | FM008 |  | 2022-04-11 07:12 | 2022-04-11 08:12 | 2022-04-12 08:12 | 24 | 2022-04-11 07:20 | 2022-04-11 09:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10570643 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-04-19 10:40 | 2022-04-19 11:40 | 2022-04-20 11:40 | 24 | 2022-04-19 10:50 | 2022-04-19 15:55 | 305 | 295 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10781859 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – C0-08-21 |  | FM008 |  | 2022-06-27 10:06 | 2022-06-27 11:06 | 2022-06-28 11:06 | 24 | 2022-06-27 10:15 | 2022-06-27 11:44 | 89 | 267 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11177368 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-10 00:03 | 2022-11-10 01:03 | 2022-11-11 01:03 | 24 | 2022-11-10 00:10 | 2022-11-10 03:30 | 200 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11216102 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C0-08-21 |  | FM008 |  | 2022-11-23 00:04 | 2022-11-23 01:04 | 2022-11-24 01:04 | 24 | 2022-11-23 00:10 | 2022-11-23 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11620532 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PIPE PAINT FADED - AHU-A1126-023 – C0-08-21 |  | FM008 |  | 2023-04-03 20:06 | 2023-04-03 21:06 | 2023-04-04 21:06 | 24 | 2023-04-03 20:10 | 2023-04-03 23:30 | 200 | 600 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 17573 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11764065 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1126-023 - AIR HANDLING UNIT 115 (TAG NO:AHU-A1126-023)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU023.SYSALM.DP1 / |  | FM008 |  | 2023-05-03 14:48 | 2023-05-03 15:48 | 2023-05-04 15:48 | 24 | 2023-05-03 14:55 | 2023-05-03 18:20 | 205 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 17573 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2023-11973252 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-07-13 08:39 | 2023-07-13 09:39 | 2023-07-14 09:39 | 24 | 2023-07-13 08:45 | 2023-07-13 11:55 | 190 | 356 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-12065617 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1126-023 |  | FM008 |  | 2023-08-10 11:16 | 2023-08-10 12:16 | 2023-08-11 12:16 | 24 | 2023-08-10 11:20 | 2023-08-10 13:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12101244 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS- AIR HANDLING UNIT 115 (TAG NO:AHU-A1126-023)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2023-08-21 11:20 | 2023-08-21 12:20 | 2023-08-22 12:20 | 24 | 2023-08-21 11:25 | 2023-08-21 12:25 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 119320 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12139568 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | C0-07-90- AC TEMP VERY WARM. |  | FM008 |  | 2023-09-01 06:41 | 2023-09-01 07:41 | 2023-09-02 07:41 | 24 | 2023-09-01 06:45 | 2023-09-01 09:10 | 145 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 68241 | Abdul Razak, Mr. Amir Affiq Bin | N - - - |  | Voice Communication
| CM-2023-12278712 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-10 19:07 | 2023-10-10 20:07 | 2023-10-11 20:07 | 24 | 2023-10-10 19:15 | 2023-10-10 21:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2024-12612995 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023- C0-08-21- FILTER DIRTY |  | FM008 |  | 2024-02-03 15:35 | 2024-02-03 16:35 | 2024-02-04 16:35 | 24 | 2024-02-03 15:40 | 2024-02-03 17:35 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11161477 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-11-06 08:47 | 2022-11-06 09:47 | 2022-11-07 09:47 | 24 | 2022-11-06 09:00 | 2022-11-06 11:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11193781 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -C0-08-21 |  | FM008 |  | 2022-11-18 06:50 | 2022-11-18 07:50 | 2022-11-19 07:50 | 24 | 2022-11-18 07:00 | 2022-11-18 09:35 | 155 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11977089 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – C0-08-21 |  | FM008 |  | 2023-07-16 07:17 | 2023-07-16 08:17 | 2023-07-17 08:17 | 24 | 2023-07-16 07:25 | 2023-07-16 09:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12113765 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023 DUCT INSULATION DAMAGED C0-08-21 |  | FM008 |  | 2023-08-23 19:52 | 2023-08-23 20:52 | 2023-08-24 20:52 | 24 | 2023-08-23 20:00 | 2023-08-23 23:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12140510 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023-DP1-FILTER ALARM-C0-08-04 |  | FM008 |  | 2023-09-01 09:04 | 2023-09-01 10:04 | 2023-09-02 10:04 | 24 | 2023-09-01 09:10 | 2023-09-01 17:00 | 470 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11175973 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - FCU-A1126-023 - MECHANICAL ROOM C0-08-21 |  | FM008 |  | 2022-11-09 08:50 | 2022-11-09 09:50 | 2022-11-10 09:50 | 24 | 2022-11-09 09:00 | 2022-11-09 14:00 | 300 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11250846 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU INSIDE LAMP NOT WORKING - AHU-A1126-023 – C0-08-21 |  | FM008 |  | 2022-12-05 13:51 | 2022-12-05 14:51 | 2022-12-06 14:51 | 24 | 2022-12-05 14:00 | 2022-12-05 17:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2022-11322014 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS- AHU-A1126-023- PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU023.SYSALM.DP1 / |  | FM008 |  | 2022-12-28 14:09 | 2022-12-28 15:09 | 2022-12-29 15:09 | 24 | 2022-12-28 14:19 | 2022-12-28 17:00 | 161 | 246 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | Y - - - |  | BMS
| CM-2023-11332886 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023– DUCT INSULATION DAMAGED-- |  | FM008 |  | 2023-01-01 19:08 | 2023-01-01 20:08 | 2023-01-02 20:08 | 24 | 2023-01-01 19:15 | 2023-01-01 21:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11559319 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU023.SYSALM.DP1 / |  | FM008 |  | 2023-03-13 11:44 | 2023-03-13 12:44 | 2023-03-14 12:44 | 24 | 2023-03-13 11:50 | 2023-03-13 13:00 | 70 | 210 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 95216 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11836954 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | FILTER DIRTY – C0 08 21 |  | FM008 |  | 2023-05-31 14:08 | 2023-05-31 15:08 | 2023-06-01 15:08 | 24 | 2023-05-31 14:15 | 2023-05-31 16:30 | 135 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11877616 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-023 - C0-08-21 |  | FM008 |  | 2023-06-13 12:45 | 2023-06-13 13:45 | 2023-06-14 13:45 | 24 | 2023-06-13 12:50 | 2023-06-13 14:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | BMS
| CM-2024-12825127 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-023 |  | FM008 |  | 2024-04-12 20:27 | 2024-04-12 21:27 | 2024-04-13 21:27 | 24 | 2024-04-12 20:35 | 2024-04-12 23:05 | 150 | 600 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2024-12748937 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023 DUCT INSULATION DAMAGED C0-08-21 |  | FM008 |  | 2024-03-18 19:20 | 2024-03-18 20:20 | 2024-03-19 20:20 | 24 | 2024-03-18 19:30 | 2024-03-18 22:15 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 95217 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12796529 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-023 – C0-08-21 |  | FM008 |  | 2024-04-06 08:09 | 2024-04-06 09:09 | 2024-04-07 09:09 | 24 | 2024-04-06 08:15 | 2024-04-06 13:50 | 335 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10225382 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP1 ALARM - AHU-A1126-023 - C0-08-21 |  | FM008 |  | 2022-03-08 19:04 | 2022-03-08 20:04 | 2022-03-09 20:04 | 24 | 2022-03-08 19:10 | 2022-03-08 21:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-9958635 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE-AHU-A1126-023)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-01-04 00:06 | 2022-01-04 01:06 | 2022-01-05 01:06 | 24 | 2022-01-04 00:15 | 2022-01-04 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 55709 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10365497 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023 FILTER DIRTY |  | FM008 |  | 2022-04-15 07:31 | 2022-04-15 08:31 | 2022-04-16 08:31 | 24 | 2022-04-15 07:40 | 2022-04-15 10:00 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10992581 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-08-31 13:37 | 2022-08-31 14:37 | 2022-09-01 14:37 | 24 | 2022-08-31 13:45 | 2022-08-31 14:45 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11113178 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | FILTER ALARMING - AHU-A1126-023 – C0-08-21 |  | FM008 |  | 2022-10-17 11:30 | 2022-10-17 12:30 | 2022-10-18 12:30 | 24 | 2022-10-17 11:40 | 2022-10-17 16:30 | 290 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10122587 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | SUPPLY FAN FAIL ALARM – C0-08-21 |  | FM008 |  | 2022-02-09 14:55 | 2022-02-09 15:55 | 2022-02-10 15:55 | 24 | 2022-02-09 15:05 | 2022-02-09 18:49 | 224 | 183 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 105233 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11498434 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | AHU-A1126-023 – DUCT INSULATION DAMAGED- |  | FM008 |  | 2023-02-27 19:02 | 2023-02-27 20:02 | 2023-02-28 20:02 | 24 | 2023-02-27 19:10 | 2023-02-27 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11624664 | ASD-COC-GFL008-AHU115 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY, AHU-A1126-023 , C0-08-21 |  | FM008 |  | 2023-04-06 19:22 | 2023-04-06 20:22 | 2023-04-07 20:22 | 24 | 2023-04-06 19:30 | 2023-04-06 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10146072 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-02-16 15:02 | 2022-02-16 16:02 | 2022-02-17 16:02 | 24 | 2022-02-16 15:10 | 2022-02-16 17:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10217855 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP1 ALARM - AHU-A1126-024 – C0-08-46 |  | FM008 |  | 2022-03-07 19:03 | 2022-03-07 20:03 | 2022-03-08 20:03 | 24 | 2022-03-07 19:10 | 2022-03-07 21:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-10771745 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | FILTER IS DIRTY C0-08-46 |  | FM008 |  | 2022-06-20 08:34 | 2022-06-20 09:34 | 2022-06-21 09:34 | 24 | 2022-06-20 08:40 | 2022-06-20 18:00 | 560 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | BMS
| CM-2022-11177369 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAAMGED |  | FM008 |  | 2022-11-10 00:05 | 2022-11-10 01:05 | 2022-11-11 01:05 | 24 | 2022-11-10 00:10 | 2022-11-10 03:00 | 170 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11230256 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED -AHU-A1126-024 |  | FM008 |  | 2022-11-28 09:09 | 2022-11-28 10:09 | 2022-11-29 10:09 | 24 | 2022-11-28 09:15 | 2022-11-28 11:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-11301119 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP1 AND DP FILTER ALARM - AHU-A1126-024)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-12-23 06:50 | 2022-12-23 07:50 | 2022-12-24 07:50 | 24 | 2022-12-23 07:00 | 2022-12-23 09:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11398798 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-024 - C0-08-46 |  | FM008 |  | 2023-01-25 19:02 | 2023-01-25 20:02 | 2023-01-26 20:02 | 24 | 2023-01-25 19:10 | 2023-01-25 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11667716 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024 – C0-08-46- FILTER DIRTY |  | FM008 |  | 2023-04-14 07:45 | 2023-04-14 08:45 | 2023-04-15 08:45 | 24 | 2023-04-14 07:50 | 2023-04-14 15:45 | 475 | 265 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11836885 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU024.SYSALM.DP3 / |  | FM008 |  | 2023-05-31 11:18 | 2023-05-31 12:18 | 2023-06-01 12:18 | 24 | 2023-05-31 11:25 | 2023-05-31 16:30 | 305 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 95216 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11868382 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ASD-COC-GFL008-AHU116(AHU-A1126-024)-MECHANICAL ROOM C0-08-46 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU024.SYSALM.DP1 / |  | FM008 |  | 2023-06-11 07:08 | 2023-06-11 08:08 | 2023-06-12 08:08 | 24 | 2023-06-11 07:15 | 2023-06-11 08:00 | 45 | 90 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12035034 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T0-08-46 |  | FM008 |  | 2023-07-30 21:59 | 2023-07-30 22:59 | 2023-07-31 22:59 | 24 | 2023-07-30 22:05 | 2023-07-31 01:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17053 | 17053 |  |  | 11844 | Dantes, Mr. Arun William | N - - - |  | Voice Communication
| CM-2023-12098975 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU024.SYSALM.DP1 / |  | FM008 |  | 2023-08-19 16:46 | 2023-08-19 17:46 | 2023-08-20 17:46 | 24 | 2023-08-19 16:55 | 2023-08-19 18:50 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12184722 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C0-08-46 |  | FM008 |  | 2023-09-14 12:12 | 2023-09-14 13:12 | 2023-09-15 13:12 | 24 | 2023-09-14 12:20 | 2023-09-14 13:35 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-12199243 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C0-08-46 |  | FM008 |  | 2023-09-19 15:55 | 2023-09-19 16:55 | 2023-09-20 16:55 | 24 | 2023-09-19 16:00 | 2023-09-19 18:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 87807 |  |  | FM12472 | Arumuga Nainar Senthilkumar, | N - - - |  | Voice Communication
| CM-2023-12420266 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-28 19:25 | 2023-11-28 20:25 | 2023-11-29 20:25 | 24 | 2023-11-28 19:30 | 2023-11-28 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12426755 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-12-02 08:18 | 2023-12-02 09:18 | 2023-12-03 09:18 | 24 | 2023-12-02 08:25 | 2023-12-02 11:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2024-12612996 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024- C0-08-46 FILTER DIRTY |  | FM008 |  | 2024-02-03 15:37 | 2024-02-03 16:37 | 2024-02-04 16:37 | 24 | 2024-02-03 15:45 | 2024-02-03 17:40 | 115 | 230 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11150041 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024- FILTER DIRTY – C0-08-46 |  | FM008 |  | 2022-11-01 07:17 | 2022-11-01 08:17 | 2022-11-02 08:17 | 24 | 2022-11-01 07:25 | 2022-11-01 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11179723 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED – C0-08-24 |  | FM008 |  | 2022-11-12 07:21 | 2022-11-12 08:21 | 2022-11-13 08:21 | 24 | 2022-11-12 07:30 | 2022-11-12 09:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11621057 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULLATION DAMAGED – (AHU-- A1126-024-C0 08 46 |  | FM008 |  | 2023-04-05 13:09 | 2023-04-05 14:09 | 2023-04-06 14:09 | 24 | 2023-04-05 13:19 | 2023-04-05 16:19 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11688321 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C0-08-46 |  | FM008 |  | 2023-04-19 19:32 | 2023-04-19 20:32 | 2023-04-20 20:32 | 24 | 2023-04-19 19:40 | 2023-04-19 22:10 | 150 | 600 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11861315 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING -C0-08-46 |  | FM008 |  | 2023-06-06 13:38 | 2023-06-06 14:38 | 2023-06-07 14:38 | 24 | 2023-06-06 13:48 | 2023-06-06 15:45 | 117 | 234 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17333 | 94954 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12015442 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-024 – C0-08-46 |  | FM008 |  | 2023-07-29 07:06 | 2023-07-29 08:06 | 2023-07-30 08:06 | 24 | 2023-07-29 07:10 | 2023-07-29 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12117952 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-024 – C0-08-46 |  | FM008 |  | 2023-08-27 22:23 | 2023-08-27 23:23 | 2023-08-28 23:23 | 24 | 2023-08-27 22:30 | 2023-08-28 01:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12163922 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY – C0-08-46 |  | FM008 |  | 2023-09-08 12:03 | 2023-09-08 13:03 | 2023-09-09 13:03 | 24 | 2023-09-08 12:05 | 2023-09-08 16:30 | 265 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-11865967 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - MECHANICAL ROOM C0-08-46 |  | FM008 |  | 2023-06-10 10:15 | 2023-06-10 11:15 | 2023-06-11 11:15 | 24 | 2023-06-10 10:20 | 2023-06-10 17:30 | 430 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11929903 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024 DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-06-26 10:08 | 2023-06-26 11:08 | 2023-06-27 11:08 | 24 | 2023-06-26 10:17 | 2023-06-26 16:15 | 358 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11995001 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-ASD-COC-GFL008-AHU116(AHU-A1126-024) MECHANICAL ROOM C0-08-46 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.GNDP20.CONC0821.AHU024.SYSALM.DP1 / |  | FM008 |  | 2023-07-18 14:54 | 2023-07-18 15:54 | 2023-07-19 15:54 | 24 | 2023-07-18 15:00 | 2023-07-18 16:00 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2024-12727209 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2024-03-11 19:08 | 2024-03-11 20:08 | 2024-03-12 20:08 | 24 | 2024-03-11 19:15 | 2024-03-11 22:05 | 170 | 510 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12755426 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-024 |  | FM008 |  | 2024-03-24 08:08 | 2024-03-24 09:08 | 2024-03-25 09:08 | 24 | 2024-03-24 08:15 | 2024-03-24 11:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12850345 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C0-08-40 |  | FM008 |  | 2024-04-26 13:02 | 2024-04-26 14:02 | 2024-04-27 14:02 | 24 | 2024-04-26 13:10 | 2024-04-26 15:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12526869 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-024) |  | FM008 |  | 2024-01-02 17:14 | 2024-01-02 18:14 | 2024-01-03 18:14 | 24 | 2024-01-02 17:20 | 2024-01-02 18:30 | 70 | 210 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM11109 | Franklin, Mr. Jeyaraj Bensigar | N - - - |  | Voice Communication
| CM-2022-10099531 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-024 C0-08-16 |  | FM008 |  | 2022-01-30 22:46 | 2022-01-30 23:46 | 2022-01-31 23:46 | 24 | 2022-01-30 22:50 | 2022-01-31 00:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 85125 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10238494 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024 – SUPPLY DUCT ACCESS DOOR LEAKAGE- |  | FM008 |  | 2022-03-13 10:55 | 2022-03-13 11:55 | 2022-03-14 11:55 | 24 | 2022-03-13 11:05 | 2022-03-13 12:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10780751 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024 – DP 1 FILTER ALARM C0-08-46 |  | FM008 |  | 2022-06-26 08:27 | 2022-06-26 09:27 | 2022-06-27 09:27 | 24 | 2022-06-26 08:35 | 2022-06-26 16:45 | 490 | 215 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11060757 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024 FILTER ALARM C0-08-46 |  | FM008 |  | 2022-09-28 13:29 | 2022-09-28 14:29 | 2022-09-29 14:29 | 24 | 2022-09-28 13:38 | 2022-09-28 16:10 | 152 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11330718 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED AHU-A1126-024 - C0-08-46 |  | FM008 |  | 2022-12-31 20:51 | 2022-12-31 21:51 | 2023-01-01 21:51 | 24 | 2022-12-31 21:00 | 2022-12-31 23:55 | 175 | 525 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10121246 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED - AHU-1126-024 – C0-08-46 |  | FM008 |  | 2022-02-09 15:07 | 2022-02-09 16:07 | 2022-02-10 16:07 | 24 | 2022-02-09 15:10 | 2022-02-09 17:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 55709 |  |  | FM10078 | Abdulwahab, Mr. Mohamed Nasir | N - - - |  | Voice Communication
| CM-2022-10251793 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED-AHU-A1126-024)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-03-15 23:59 | 2022-03-16 00:59 | 2022-03-17 00:59 | 24 | 2022-03-16 00:05 | 2022-03-16 01:45 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11526185 | ASD-COC-GFL008-AHU116 | AIR HANDLING UNIT-05 | AHU-A1126-024 ACCESS DOOR AIR LEAKAGE C0-08-46 |  | FM008 |  | 2023-03-08 19:00 | 2023-03-08 20:00 | 2023-03-09 20:00 | 24 | 2023-03-08 19:05 | 2023-03-08 21:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12427666 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-034 - MECHANICAL ROOM C0-08-04 |  | FM008 |  | 2023-11-29 19:29 | 2023-11-29 20:29 | 2023-11-30 20:29 | 24 | 2023-11-29 19:35 | 2023-11-29 22:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2024-12847085 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C0-08-04 |  | FM008 |  | 2024-04-22 19:21 | 2024-04-22 20:21 | 2024-04-23 20:21 | 24 | 2024-04-22 19:30 | 2024-04-22 21:45 | 135 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2023-11363119 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1126-034)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2023-01-10 19:37 | 2023-01-10 20:37 | 2023-01-11 20:37 | 24 | 2023-01-10 19:40 | 2023-01-10 21:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11822487 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | FILTER DIRTY – C0-08-04 |  | FM008 |  | 2023-05-22 23:24 | 2023-05-23 00:24 | 2023-05-24 00:24 | 24 | 2023-05-22 23:30 | 2023-05-23 01:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12066755 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | TECHNICAL LINE STORE TEMPERATURE INCREASED TO 26°C, AS PER THE TEMPERATURE SHOULD BE 20°C TO 25°C IN STORE TO MAINTAIN AIRCRAFT SPARES-WATER IS LEAKING IN AIR COOLER IN BONDED STORAGE AREA AT TECHNICAL LINE STORES-Near Aircraft Stand Bay |  | FM008 |  | 2023-08-11 10:08 | 2023-08-11 11:08 | 2023-08-12 11:08 | 24 | 2023-08-11 10:10 | 2023-08-11 11:35 | 85 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 87807 |  |  | 35988 | Saleem, Mr. Azim | N - - - |  | E-mail
| CM-2022-10998026 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM AIR CONDITIONER DUCT - C13 LINE MAINTENANCE WAREHOUSE DOOR # C0-08-11, 02 |  | FM008 |  | 2022-09-05 08:11 | 2022-09-05 09:11 | 2022-09-06 09:11 | 24 | 2022-09-05 08:21 | 2022-09-05 10:58 | 157 | 56 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17573 | 94954 |  |  | 23893 | Seyan Shahul Hameed, Mr. Abdul Ajees | N - - - |  | E-mail
| CM-2022-11235574 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C0-08-04 |  | FM008 |  | 2022-12-04 11:21 | 2022-12-04 12:21 | 2022-12-05 12:21 | 24 | 2022-12-04 11:30 | 2022-12-04 14:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11326922 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | AHU-A1126-034 – COOLING COIL IS DIRTY – C0-08-04 |  | FM008 |  | 2022-12-27 12:35 | 2022-12-27 13:35 | 2022-12-28 13:35 | 24 | 2022-12-27 12:45 | 2022-12-27 16:30 | 225 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94954 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11784439 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-05-12 01:06 | 2023-05-12 02:06 | 2023-05-13 02:06 | 24 | 2023-05-12 01:10 | 2023-05-12 02:10 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11859892 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | WATER LEAKAGE IN STORE - GATE C11, DOOR # C0-08-11 |  | FM008 |  | 2023-06-05 22:52 | 2023-06-05 23:52 | 2023-06-06 23:52 | 24 | 2023-06-05 23:00 | 2023-06-05 23:45 | 45 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 94954 |  |  | 63910 | Ahmad, Mr. Akeel | N - - - |  | E-mail
| CM-2023-11862348 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING -C0-08-04 |  | FM008 |  | 2023-06-06 15:10 | 2023-06-06 16:10 | 2023-06-07 16:10 | 24 | 2023-06-06 15:20 | 2023-06-06 17:54 | 154 | 248 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 95217 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12133989 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | water is leaking in Center Air Condition in Bonded storage area at Technical Line Stores C0 08 11 Near Aircraft Stand Bay : 12 |  | FM008 |  | 2023-08-30 12:48 | 2023-08-30 13:48 | 2023-08-31 13:48 | 24 | 2023-08-30 12:50 | 2023-08-30 17:45 | 295 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 17053 |  |  | 35988 | Saleem, Mr. Azim | N - - - |  | E-mail
| CM-2023-12325877 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | DUCT INSULLATION IS DAMAGED |  | FM008 |  | 2023-10-27 21:14 | 2023-10-27 22:14 | 2023-10-28 22:14 | 24 | 2023-10-27 21:20 | 2023-10-27 23:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10221887 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | DP1- FILTER DIRTY |  | FM008 |  | 2022-03-08 12:04 | 2022-03-08 13:04 | 2022-03-09 13:04 | 24 | 2022-03-08 12:14 | 2022-03-08 14:14 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11091011 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | AHU-A1126-034 – FILTER ALARM-- |  | FM008 |  | 2022-10-12 07:03 | 2022-10-12 08:03 | 2022-10-13 08:03 | 24 | 2022-10-12 07:10 | 2022-10-12 13:05 | 355 | 200 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11948569 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | AHU-A1126-034-FILTER DIRTY -CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2023-07-06 09:04 | 2023-07-06 10:04 | 2023-07-07 10:04 | 24 | 2023-07-06 09:10 | 2023-07-06 15:00 | 350 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 94954 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2022-10363496 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | DP1 ALARM - AHU-11126-034 - CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-04-14 11:17 | 2022-04-14 12:17 | 2022-04-15 12:17 | 24 | 2022-04-14 11:20 | 2022-04-14 15:14 | 234 | 213 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 17053 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | E-mail
| CM-2022-10825420 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | SUPPLY GRILL DIRTY -AHU-A1126-034)-AIRSIDE-CONCOURSE C-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-07-11 15:50 | 2022-07-11 16:50 | 2022-07-12 16:50 | 24 | 2022-07-11 15:59 | 2022-07-11 17:59 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 95217 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2024-12793107 | ASD-COC-GFL008-AHU125 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-034) – C0 08 04 |  | FM008 |  | 2024-04-01 21:59 | 2024-04-01 22:59 | 2024-04-02 22:59 | 24 | 2024-04-01 22:05 | 2024-04-02 00:50 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10075424 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED; AHU-A1126-314 - C3-08-02 |  | FM008 |  | 2022-01-24 10:37 | 2022-01-24 11:37 | 2022-01-25 11:37 | 24 | 2022-01-24 10:45 | 2022-01-24 12:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10709388 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU-A1126-314 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-06-02 20:31 | 2022-06-02 21:31 | 2022-06-03 21:31 | 24 | 2022-06-02 20:35 | 2022-06-02 22:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | DOOR HINGES LOOSE/DAMAGED | REPAIRED/REPLACED | 106972 | 17053 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-11081262 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - TAG NO:AHU-A1126-314 |  | FM008 |  | 2022-10-07 07:16 | 2022-10-07 08:16 | 2022-10-08 08:16 | 24 | 2022-10-07 07:20 | 2022-10-07 12:30 | 310 | 245 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12274101 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU-A1126-314 FILTER DIRTY |  | FM008 |  | 2023-10-10 23:04 | 2023-10-11 00:04 | 2023-10-12 00:04 | 24 | 2023-10-10 23:10 | 2023-10-11 01:40 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10887264 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU-A1126-314- FILTER ALARM- C3-04-03- |  | FM008 |  | 2022-07-31 17:08 | 2022-07-31 18:08 | 2022-08-01 18:08 | 24 | 2022-07-31 17:15 | 2022-07-31 20:45 | 210 | 95 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11060298 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -C3-04-03 |  | FM008 |  | 2022-09-26 03:25 | 2022-09-26 04:25 | 2022-09-27 04:25 | 24 | 2022-09-26 03:35 | 2022-09-26 04:35 | 60 | 180 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11189548 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | CHILLER LINE PAINT FADED- AHU-A1126-314 - C3-04-03 |  | FM008 |  | 2022-11-13 19:26 | 2022-11-13 20:26 | 2022-11-14 20:26 | 24 | 2022-11-13 19:30 | 2022-11-13 21:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12552636 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKING -C3-04-03 |  | FM008 |  | 2024-01-09 17:19 | 2024-01-09 18:19 | 2024-01-10 18:19 | 24 | 2024-01-09 17:20 | 2024-01-09 18:45 | 85 | 340 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2022-11255600 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU-A1126-314- DUCT INSULATION DAMAGED-C3-04-03-- |  | FM008 |  | 2022-12-08 15:30 | 2022-12-08 16:30 | 2022-12-09 16:30 | 24 | 2022-12-08 15:35 | 2022-12-08 18:40 | 185 | 555 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11972725 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU FILTER ALARM |  | FM008 |  | 2023-07-12 19:11 | 2023-07-12 20:11 | 2023-07-13 20:11 | 24 | 2023-07-12 19:15 | 2023-07-12 21:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 95216 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12182959 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – AHU-A1126-314 – C3-04-03 |  | FM008 |  | 2023-09-11 20:14 | 2023-09-11 21:14 | 2023-09-12 21:14 | 24 | 2023-09-11 20:20 | 2023-09-11 23:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17573 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12692345 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-04-03-AIR HANDLING UNIT 140 (TAG NO:AHU-A1126-314)- |  | FM008 |  | 2024-03-02 00:05 | 2024-03-02 01:05 | 2024-03-03 01:05 | 24 | 2024-03-02 00:15 | 2024-03-02 03:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17336 | 95217 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12367311 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-12 08:30 | 2023-11-12 09:30 | 2023-11-13 09:30 | 24 | 2023-11-12 08:35 | 2023-11-12 10:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12777933 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | Chilled water supply line support is detached - C2 04 10 |  | FM008 |  | 2024-03-29 09:42 | 2024-03-29 10:42 | 2024-03-30 10:42 | 24 | 2024-03-29 09:50 | 2024-03-29 12:25 | 155 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 119320 | 17053 |  |  | 17123 | Paramban, Mr. Vinod Kumar | N - - - |  | E-mail
| CM-2022-10122801 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-04-03 |  | FM008 |  | 2022-02-10 08:00 | 2022-02-10 09:00 | 2022-02-11 09:00 | 24 | 2022-02-10 08:10 | 2022-02-10 10:45 | 155 | 310 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM7717 | R W Herath Mudiyanselage Giddawa Gedara, Mr. Gamini Rajaguru | N - - - |  | Voice Communication
| CM-2022-9957724 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU-A1126-314 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-01-01 05:10 | 2022-01-01 06:10 | 2022-01-02 06:10 | 24 | 2022-01-01 05:15 | 2022-01-01 06:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | DARIN AIR FLOW | RECTIFIED | 68485 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10570706 | ASD-COC-TFL004-AHU140 | AIR HANDLING UNIT-05 | AHU-A1126-314-SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-04-19 20:55 | 2022-04-19 21:55 | 2022-04-20 21:55 | 24 | 2022-04-19 21:00 | 2022-04-19 23:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11040948 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-09-23 00:11 | 2022-09-23 01:11 | 2022-09-24 01:11 | 24 | 2022-09-23 00:15 | 2022-09-23 02:25 | 130 | 250 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11219653 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | MARINA LIGHT NOT ILLUMINATING - AHU-A1126-315 – C3-04-01 |  | FM008 |  | 2022-11-26 21:29 | 2022-11-26 22:29 | 2022-11-27 22:29 | 24 | 2022-11-26 21:35 | 2022-11-26 23:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | E-mail
| CM-2023-11590285 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | SUPPLY DOOR AIR LEAKAGE |  | FM008 |  | 2023-03-26 07:06 | 2023-03-26 08:06 | 2023-03-27 08:06 | 24 | 2023-03-26 07:15 | 2023-03-26 10:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 68060 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11679716 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU-A1126-315 AHU HEATER FLEXIBLE CONNECTOR DAMAGED C3-04-01 |  | FM008 |  | 2023-04-17 19:12 | 2023-04-17 20:12 | 2023-04-18 20:12 | 24 | 2023-04-17 19:20 | 2023-04-17 21:40 | 140 | 280 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 89127 | 87807 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-11691399 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU-A1126-315- LIGHTING FLEXIBLE CONNECTOR DAMAGED-- |  | FM008 |  | 2023-04-21 16:25 | 2023-04-21 17:25 | 2023-04-22 17:25 | 24 | 2023-04-21 16:30 | 2023-04-21 17:56 | 86 | 172 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11785323 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU-A1126-315 DUCT INSULATION DAMAGED C3-04-01 |  | FM008 |  | 2023-05-11 20:04 | 2023-05-11 21:04 | 2023-05-12 21:04 | 24 | 2023-05-11 20:10 | 2023-05-11 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12068594 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED ,AHU-A1126-315, C3-04-01 |  | FM008 |  | 2023-08-13 00:12 | 2023-08-13 01:12 | 2023-08-14 01:12 | 24 | 2023-08-13 00:18 | 2023-08-13 02:45 | 147 | 294 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-11001149 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU-A1126-315 SUPPLY DUCT INSULATION DAMAGED C3-04-01 |  | FM008 |  | 2022-09-06 22:12 | 2022-09-06 23:12 | 2022-09-07 23:12 | 24 | 2022-09-06 22:20 | 2022-09-07 00:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11040264 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | LAMP INSIDE AHU NOT WORKING - AHU-A1126-315 – C3-04-01 |  | FM008 |  | 2022-09-19 00:05 | 2022-09-19 01:05 | 2022-09-20 01:05 | 24 | 2022-09-19 00:14 | 2022-09-19 01:42 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | EXPANSION VALVE MALFUNCTION | REPLACED THE EXPANSION VALVE | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11588222 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU-A1126-315 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-03-24 19:28 | 2023-03-24 20:28 | 2023-03-25 20:28 | 24 | 2023-03-24 19:30 | 2023-03-24 21:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12628879 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AHU-A1126-315)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 004 |  | FM008 |  | 2024-02-05 19:12 | 2024-02-05 20:12 | 2024-02-06 20:12 | 24 | 2024-02-05 19:20 | 2024-02-05 21:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12322231 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-315 |  | FM008 |  | 2023-10-26 20:30 | 2023-10-26 21:30 | 2023-10-27 21:30 | 24 | 2023-10-26 20:35 | 2023-10-26 22:35 | 120 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2023-12367312 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-12 08:31 | 2023-11-12 09:31 | 2023-11-13 09:31 | 24 | 2023-11-12 08:35 | 2023-11-12 10:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11071055 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-315) |  | FM008 |  | 2022-10-05 09:55 | 2022-10-05 10:55 | 2022-10-06 10:55 | 24 | 2022-10-05 10:05 | 2022-10-05 16:30 | 385 | 215 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11196466 | ASD-COC-TFL004-AHU141 | AIR HANDLING UNIT-05 | AHU-A1126-315- DUCT INSULATION DAMAGED -C3-04-01 |  | FM008 |  | 2022-11-18 21:59 | 2022-11-18 22:59 | 2022-11-19 22:59 | 24 | 2022-11-18 22:05 | 2022-11-18 23:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11378799 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | INSULATION DAMAGED -:AHU-A1126-316)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 004 |  | FM008 |  | 2023-01-15 16:50 | 2023-01-15 17:50 | 2023-01-16 17:50 | 24 | 2023-01-15 17:00 | 2023-01-15 18:30 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11775096 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-AHU-A1126-316)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 004 |  | FM008 |  | 2023-05-07 13:06 | 2023-05-07 14:06 | 2023-05-08 14:06 | 24 | 2023-05-07 13:12 | 2023-05-07 16:10 | 178 | 416 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-12184648 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-04-03 |  | FM008 |  | 2023-09-14 03:17 | 2023-09-14 04:17 | 2023-09-15 04:17 | 24 | 2023-09-14 03:20 | 2023-09-14 06:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12383711 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU-A1126-316 DUCT INSULATION DAMAGED – C3-04-03 |  | FM008 |  | 2023-11-15 07:35 | 2023-11-15 08:35 | 2023-11-16 08:35 | 24 | 2023-11-15 07:40 | 2023-11-15 10:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 87807 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2022-11189549 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | CHILLER LINE PAINT FADED - AHU-A1126-316 - C3-04-03 |  | FM008 |  | 2022-11-13 19:27 | 2022-11-13 20:27 | 2022-11-14 20:27 | 24 | 2022-11-13 19:30 | 2022-11-13 23:35 | 245 | 245 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12092980 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU-A1126-316-DUCT INSULATION DAMAGE . |  | FM008 |  | 2023-08-15 08:53 | 2023-08-15 09:53 | 2023-08-16 09:53 | 24 | 2023-08-15 09:00 | 2023-08-15 12:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11255601 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU-A1126-316- DUCT ACCESS DOOR AIR LEAKAGE-C3-04-03-- |  | FM008 |  | 2022-12-08 15:31 | 2022-12-08 16:31 | 2022-12-09 16:31 | 24 | 2022-12-08 15:35 | 2022-12-08 18:40 | 185 | 370 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12095716 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU ACCESS DOOR AIR LEAKAGE- C3-04-03 – AHU-A1126-316 |  | FM008 |  | 2023-08-16 07:25 | 2023-08-16 08:25 | 2023-08-17 08:25 | 24 | 2023-08-16 07:30 | 2023-08-16 10:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12794353 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | DUCT ACCESS DOOR AIR LEAKAGE - AHU-A1126-316 - C3-08-01 |  | FM008 |  | 2024-04-03 07:08 | 2024-04-03 08:08 | 2024-04-04 08:08 | 24 | 2024-04-03 07:15 | 2024-04-03 10:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12278988 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY |  | FM008 |  | 2023-10-11 19:05 | 2023-10-11 20:05 | 2023-10-12 20:05 | 24 | 2023-10-11 19:10 | 2023-10-11 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-9950907 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED NO:AHU-A1126-316 |  | FM008 |  | 2022-01-02 00:05 | 2022-01-02 01:05 | 2022-01-03 01:05 | 24 | 2022-01-02 00:10 | 2022-01-02 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10873495 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU-A1126-316 FILTER ALARM CONCOURSE C-THIRD FLOOR AREA 004 |  | FM008 |  | 2022-07-29 03:08 | 2022-07-29 04:08 | 2022-07-30 04:08 | 24 | 2022-07-29 03:15 | 2022-07-29 04:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11071054 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - CONCOURSE C-THIRD FLOOR AREA 004 |  | FM008 |  | 2022-10-05 09:53 | 2022-10-05 10:53 | 2022-10-06 10:53 | 24 | 2022-10-05 10:00 | 2022-10-05 12:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11104740 | ASD-COC-TFL004-AHU142 | AIR HANDLING UNIT-05 | AHU-A1126-316 – SUPPLY DUCT INSULATION DAMAGED – C3-04-03 |  | FM008 |  | 2022-10-15 14:17 | 2022-10-15 15:16 | 2022-10-16 15:16 | 24 | 2022-10-15 14:20 | 2022-10-15 17:10 | 170 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10608121 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU-A1126-355 DUCT INSULATON DAMAGED |  | FM008 |  | 2022-05-04 14:56 | 2022-05-04 15:56 | 2022-05-05 15:56 | 24 | 2022-05-04 15:05 | 2022-05-04 16:50 | 105 | 315 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 17053 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-11161321 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING – C3-04-01 MEC ROOM |  | FM008 |  | 2022-11-05 07:47 | 2022-11-05 08:47 | 2022-11-06 08:47 | 24 | 2022-11-05 07:50 | 2022-11-05 09:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12064814 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | INSULATION DAMAGED -C3-04-01 |  | FM008 |  | 2023-08-09 09:20 | 2023-08-09 10:20 | 2023-08-10 10:20 | 24 | 2023-08-09 09:32 | 2023-08-09 11:02 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | 118925 | Datla, Mr. Anil Varma | N - - - |  | E-mail
| CM-2023-12141662 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1126-355,C3-04-01 |  | FM008 |  | 2023-09-02 09:20 | 2023-09-02 10:20 | 2023-09-03 10:20 | 24 | 2023-09-02 09:25 | 2023-09-02 11:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12476603 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-04-01 |  | FM008 |  | 2023-12-14 21:06 | 2023-12-14 22:06 | 2023-12-15 22:06 | 24 | 2023-12-14 21:10 | 2023-12-14 23:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12609282 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED ,AHU-A1126-355, C3-04-01 |  | FM008 |  | 2024-01-29 19:16 | 2024-01-29 20:16 | 2024-01-30 20:16 | 24 | 2024-01-29 19:25 | 2024-01-29 21:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12737524 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU-A1126-355-DUCT INSULATION DAMAGE -C3-04-03 |  | FM008 |  | 2024-03-18 07:12 | 2024-03-18 08:12 | 2024-03-19 08:12 | 24 | 2024-03-18 07:15 | 2024-03-18 10:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2024-12625297 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU-A1126-355 FILTER DIRTY C3-04-01 |  | FM008 |  | 2024-02-05 09:13 | 2024-02-05 10:13 | 2024-02-06 10:13 | 24 | 2024-02-05 09:20 | 2024-02-05 11:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11387460 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU-A1126-355- DUCT INSULATION DAMAGED-- |  | FM008 |  | 2023-01-21 00:05 | 2023-01-21 01:05 | 2023-01-22 01:05 | 24 | 2023-01-21 00:10 | 2023-01-21 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 94954 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12346662 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY – T3-04-01 |  | FM008 |  | 2023-11-03 09:55 | 2023-11-03 10:55 | 2023-11-04 10:55 | 24 | 2023-11-03 10:04 | 2023-11-03 14:10 | 246 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 105233 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12364777 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-355,C3-04-01 |  | FM008 |  | 2023-11-07 19:32 | 2023-11-07 20:32 | 2023-11-08 20:32 | 24 | 2023-11-07 19:40 | 2023-11-07 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11381927 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU DUCT INSOLATION DAMAGED – AHU-A1126-355 ,C3-04-01 |  | FM008 |  | 2023-01-16 23:43 | 2023-01-17 00:43 | 2023-01-18 00:43 | 24 | 2023-01-16 23:50 | 2023-01-17 01:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11972529 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1126-355 – C3-04-01 |  | FM008 |  | 2023-07-11 22:09 | 2023-07-11 23:09 | 2023-07-12 23:09 | 24 | 2023-07-11 22:15 | 2023-07-12 00:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-11969289 | ASD-COC-TFL004-AHU160 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-355 - C3 04 01 |  | FM008 |  | 2023-07-11 07:10 | 2023-07-11 08:10 | 2023-07-12 08:10 | 24 | 2023-07-11 07:15 | 2023-07-11 10:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10608124 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | AHU-A1126-356 DUCT INSULATON DAMAGED |  | FM008 |  | 2022-05-04 14:57 | 2022-05-04 15:57 | 2022-05-05 15:57 | 24 | 2022-05-04 15:05 | 2022-05-04 17:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 17053 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-11081264 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - TAG NO:AHU-A1126-356 |  | FM008 |  | 2022-10-07 07:20 | 2022-10-07 08:20 | 2022-10-08 08:20 | 24 | 2022-10-07 07:25 | 2022-10-07 13:35 | 370 | 185 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12634282 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2024-02-10 07:23 | 2024-02-10 08:23 | 2024-02-11 08:23 | 24 | 2024-02-10 07:25 | 2024-02-10 10:00 | 155 | 310 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12820414 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DUCT INSUALTION DAMAGED -AIR HANDLING UNIT 161 (TAG NO:AHU-A1126-356)-C3-04-03 |  | FM008 |  | 2024-04-10 00:28 | 2024-04-10 01:28 | 2024-04-11 01:28 | 24 | 2024-04-10 00:35 | 2024-04-10 03:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11835213 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | AHU-A1126-356 COOLING COIL IS DIRTY |  | FM008 |  | 2023-05-30 12:54 | 2023-05-30 13:54 | 2023-05-31 13:54 | 24 | 2023-05-30 13:00 | 2023-05-30 16:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11971149 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-07-10 07:00 | 2023-07-10 08:00 | 2023-07-11 08:00 | 24 | 2023-07-10 07:00 | 2023-07-10 10:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11256534 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-08 21:28 | 2022-12-08 22:28 | 2022-12-09 22:28 | 24 | 2022-12-08 21:35 | 2022-12-08 23:25 | 110 | 450 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11387462 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | AHU-A1126-356- DUCT INSULATION DAMAGED-- |  | FM008 |  | 2023-01-21 00:06 | 2023-01-21 01:06 | 2023-01-22 01:06 | 24 | 2023-01-21 00:15 | 2023-01-21 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 94954 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12085179 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AIR HANDLING UNIT 161 (TAG NO:AHU-A1126-356)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 004 |  | FM008 |  | 2023-08-14 22:41 | 2023-08-14 23:41 | 2023-08-15 23:41 | 24 | 2023-08-14 22:45 | 2023-08-15 01:30 | 165 | 495 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12858239 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C3-04-03 |  | FM008 |  | 2024-04-28 19:13 | 2024-04-28 20:13 | 2024-04-29 20:13 | 24 | 2024-04-28 19:18 | 2024-04-28 20:48 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12398755 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DUCT NSULATION DAMAGED - AHU-A1126-356 - MECHANICAL ROOM C3-04-03 |  | FM008 |  | 2023-11-20 07:42 | 2023-11-20 08:42 | 2023-11-21 08:42 | 24 | 2023-11-20 07:50 | 2023-11-20 11:00 | 190 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10786477 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - C3-04-03 |  | FM008 |  | 2022-06-26 21:01 | 2022-06-26 22:01 | 2022-06-27 22:01 | 24 | 2022-06-26 21:10 | 2022-06-26 22:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 95217 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11381928 | ASD-COC-TFL004-AHU161 | AIR HANDLING UNIT-05 | AHU DUCT INSOLATION DAMAGED AHU-A1126-356 - C3-04-03 |  | FM008 |  | 2023-01-16 23:44 | 2023-01-17 00:44 | 2023-01-18 00:44 | 24 | 2023-01-16 23:50 | 2023-01-17 01:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12231938 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | FILTER DIRTY -C3-05-02 |  | FM008 |  | 2023-09-29 21:40 | 2023-09-29 22:40 | 2023-09-30 22:40 | 24 | 2023-09-29 21:45 | 2023-09-29 23:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12595849 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED ,AHU-A1126-317, C3-05-01 |  | FM008 |  | 2024-01-27 19:22 | 2024-01-27 20:22 | 2024-01-28 20:22 | 24 | 2024-01-27 19:30 | 2024-01-27 22:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10887265 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | AHU-A1126-317- FILTER ALARM- C3-05-01- - |  | FM008 |  | 2022-07-31 17:08 | 2022-07-31 18:08 | 2022-08-01 18:08 | 24 | 2022-07-31 17:15 | 2022-07-31 21:35 | 260 | 95 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11429313 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-:AHU-A1126-317(C3-05-01) |  | FM008 |  | 2023-02-06 07:06 | 2023-02-06 08:06 | 2023-02-07 08:06 | 24 | 2023-02-06 07:15 | 2023-02-06 08:35 | 80 | 160 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 133396 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12043036 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | FILTER DIRTY –AHU-A1126-317 - C3 05 01 |  | FM008 |  | 2023-08-03 11:35 | 2023-08-03 12:35 | 2023-08-04 12:35 | 24 | 2023-08-03 11:40 | 2023-08-03 13:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11936038 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING -AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 005 |  | FM008 |  | 2023-07-03 09:49 | 2023-07-03 10:49 | 2023-07-04 10:49 | 24 | 2023-07-03 09:58 | 2023-07-03 18:10 | 492 | 190 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2024-12734849 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | AC TOO COLD – AL DAR EXCHANGE OPP GATE C8 |  | FM008 |  | 2024-03-18 08:48 | 2024-03-18 09:48 | 2024-03-19 09:48 | 24 | 2024-03-18 08:55 | 2024-03-18 11:30 | 155 | 65 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  |  | HADHY | N - - - |  | Voice Communication
| CM-2023-12338640 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-317 - MECHANICAL ROOM C3-05-01 |  | FM008 |  | 2023-10-29 21:22 | 2023-10-29 22:22 | 2023-10-30 22:22 | 24 | 2023-10-29 21:30 | 2023-10-30 00:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10098163 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT IS FADED - AHU-A1126-317 - C3-05-01 |  | FM008 |  | 2022-01-31 15:08 | 2022-01-31 16:08 | 2022-02-01 16:08 | 24 | 2022-01-31 15:18 | 2022-01-31 17:18 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11196476 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | AHU-A1126-317 – DUCT INSULATION DAMAGED – C3-05-01 |  | FM008 |  | 2022-11-19 00:07 | 2022-11-19 01:07 | 2022-11-20 01:07 | 24 | 2022-11-19 00:15 | 2022-11-19 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10142786 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | AHU-A1126-317 – DUCT INSULATION DAMAGED – C3-05-01 |  | FM008 |  | 2022-02-17 16:36 | 2022-02-17 17:36 | 2022-02-18 17:36 | 24 | 2022-02-17 16:40 | 2022-02-17 18:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10214776 | ASD-COC-TFL005-AHU143 | AIR HANDLING UNIT-05 | AHU-A1126-317 DUCT INSULATION DAMAGED C3-05-01 |  | FM008 |  | 2022-03-06 07:22 | 2022-03-06 08:22 | 2022-03-07 08:22 | 24 | 2022-03-06 07:30 | 2022-03-06 10:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10251634 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | C3-05-03 SYPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-15 01:58 | 2022-03-15 02:58 | 2022-03-16 02:58 | 24 | 2022-03-15 02:00 | 2022-03-15 04:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2023-11825386 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-05-03 |  | FM008 |  | 2023-05-25 19:27 | 2023-05-25 20:27 | 2023-05-26 20:27 | 24 | 2023-05-25 19:35 | 2023-05-25 22:58 | 203 | 406 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12017271 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY |  | FM008 |  | 2023-07-29 19:21 | 2023-07-29 20:21 | 2023-07-30 20:21 | 24 | 2023-07-29 19:30 | 2023-07-29 23:30 | 240 | 480 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12014171 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-07-25 20:45 | 2023-07-25 21:45 | 2023-07-26 21:45 | 24 | 2023-07-25 20:50 | 2023-07-25 23:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12349794 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | AHU TROUBLE LAMP IS NOT WORKING |  | FM008 |  | 2023-11-05 09:22 | 2023-11-05 10:22 | 2023-11-06 10:22 | 24 | 2023-11-05 09:30 | 2023-11-05 11:50 | 140 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2023-11469693 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | AHU-A1126-318 COOLING COIL DIRTY |  | FM008 |  | 2023-02-18 15:03 | 2023-02-18 16:03 | 2023-02-19 16:03 | 24 | 2023-02-18 15:10 | 2023-02-18 17:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12129837 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - C3-05-03 |  | FM008 |  | 2023-08-28 12:53 | 2023-08-28 13:53 | 2023-08-29 13:53 | 24 | 2023-08-28 13:00 | 2023-08-28 18:20 | 320 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95216 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12667101 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | AHU CABIN LAMP HOLDER FAULTY -C3-05-03 |  | FM008 |  | 2024-02-20 10:44 | 2024-02-20 11:44 | 2024-02-21 11:44 | 24 | 2024-02-20 10:50 | 2024-02-20 15:00 | 250 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 95217 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2024-12832760 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-318 – C3-05-03 |  | FM008 |  | 2024-04-20 19:42 | 2024-04-20 20:42 | 2024-04-21 20:42 | 24 | 2024-04-20 19:50 | 2024-04-20 22:10 | 140 | 280 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12277387 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-318 – C3-05-03 |  | FM008 |  | 2023-10-11 07:34 | 2023-10-11 08:34 | 2023-10-12 08:34 | 24 | 2023-10-11 07:40 | 2023-10-11 10:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10045150 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – C3-05-03 |  | FM008 |  | 2022-01-12 07:02 | 2022-01-12 08:02 | 2022-01-13 08:02 | 24 | 2022-01-12 07:10 | 2022-01-12 12:30 | 320 | 305 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10930506 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | CEILING AIR VENTS MISALIGNED NEAR C2-05-19 |  | FM008 |  | 2022-08-10 17:47 | 2022-08-10 18:47 | 2022-08-11 18:47 | 24 | 2022-08-10 17:55 | 2022-08-10 20:05 | 130 | 125 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 68485 | 55709 |  |  | 61252 | Gonzales, Mr. Edmundo Santos | N - - - |  | Voice Communication
| CM-2022-10956692 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | RETURNED DUCT INSULATION DAMAGED |  | FM008 |  | 2022-08-20 19:21 | 2022-08-20 20:21 | 2022-08-21 20:21 | 24 | 2022-08-20 19:30 | 2022-08-20 21:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10154586 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR AIR LEAKING -C3-05-03 |  | FM008 |  | 2022-02-21 21:00 | 2022-02-21 22:00 | 2022-02-22 22:00 | 24 | 2022-02-21 21:05 | 2022-02-21 22:55 | 110 | 330 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10703756 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED –C3-05-03 |  | FM008 |  | 2022-05-29 12:58 | 2022-05-29 13:58 | 2022-05-30 13:58 | 24 | 2022-05-29 13:00 | 2022-05-29 15:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10902539 | ASD-COC-TFL005-AHU144 | AIR HANDLING UNIT-05 | AHU-A1126-318- FILTER ALARM |  | FM008 |  | 2022-08-01 01:08 | 2022-08-01 02:08 | 2022-08-02 02:08 | 24 | 2022-08-01 01:15 | 2022-08-01 04:25 | 190 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95217 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10223375 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-05-01 |  | FM008 |  | 2022-03-06 16:15 | 2022-03-06 17:15 | 2022-03-07 17:15 | 24 | 2022-03-06 16:25 | 2022-03-06 18:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17333 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11425291 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU-A1126-319 – CABIN LAMP NOT WORKING – C3-05-01 |  | FM008 |  | 2023-01-31 01:23 | 2023-01-31 02:23 | 2023-02-01 02:23 | 24 | 2023-01-31 01:30 | 2023-01-31 03:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11421809 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - (AHU-A1126-319)-) -AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 005 |  | FM008 |  | 2023-01-31 09:25 | 2023-01-31 10:25 | 2023-02-01 10:25 | 24 | 2023-01-31 09:35 | 2023-01-31 11:03 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 132112 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11766086 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM, AHU-A1126-319 , C3-05-01 |  | FM008 |  | 2023-05-06 10:12 | 2023-05-06 11:12 | 2023-05-07 11:12 | 24 | 2023-05-06 10:20 | 2023-05-06 15:30 | 310 | 185 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-12484189 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-12-18 07:27 | 2023-12-18 08:27 | 2023-12-19 08:27 | 24 | 2023-12-18 07:30 | 2023-12-18 15:30 | 480 | 155 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11382057 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU-A1126-319 FILTER DIRTY-- |  | FM008 |  | 2023-01-17 19:20 | 2023-01-17 20:20 | 2023-01-18 20:20 | 24 | 2023-01-17 19:25 | 2023-01-17 21:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11465490 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU DUCT AIR LEAKAGE - AHU-A1126-319 – C3-05-03 |  | FM008 |  | 2023-02-15 19:09 | 2023-02-15 20:09 | 2023-02-16 20:09 | 24 | 2023-02-15 19:15 | 2023-02-15 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 87807 |  |  | FM1195 | Abdulla, Mr. Hasainar | N - - - |  | Voice Communication
| CM-2023-12014771 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | FILTER DIRTY - C3-05-03 |  | FM008 |  | 2023-07-27 19:12 | 2023-07-27 20:12 | 2023-07-28 20:12 | 24 | 2023-07-27 19:20 | 2023-07-27 21:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12014518 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2023-07-27 00:38 | 2023-07-27 01:38 | 2023-07-28 01:38 | 24 | 2023-07-27 00:45 | 2023-07-27 03:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 68060 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12232148 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-05-01 |  | FM008 |  | 2023-09-27 14:44 | 2023-09-27 15:44 | 2023-09-28 15:44 | 24 | 2023-09-27 14:50 | 2023-09-27 16:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12230721 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-319 – C3-05-01 |  | FM008 |  | 2023-09-28 22:24 | 2023-09-28 23:24 | 2023-09-29 23:24 | 24 | 2023-09-28 22:30 | 2023-09-29 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12347935 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - AHU-A1126-319 – T3-05-01 |  | FM008 |  | 2023-11-05 12:44 | 2023-11-05 13:44 | 2023-11-06 13:44 | 24 | 2023-11-05 12:50 | 2023-11-05 14:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 17053 |  |  | FM10039 | Perumalraja Kothandapani, Mr. | N - - - |  | Voice Communication
| CM-2024-12552746 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | FILTER DIRTY - AIR HANDLING UNIT 145 (TAG NO:AHU-A1126-319)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 005 |  | FM008 |  | 2024-01-10 08:36 | 2024-01-10 09:36 | 2024-01-11 09:36 | 24 | 2024-01-10 08:40 | 2024-01-10 12:30 | 230 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-11824515 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AIR HANDLING UNIT 145 (TAG NO:AHU-A1126-319 |  | FM008 |  | 2023-05-25 20:28 | 2023-05-25 21:28 | 2023-05-26 21:28 | 24 | 2023-05-25 20:35 | 2023-05-25 22:58 | 143 | 286 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2022-10098164 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT IS FADED - AHU-A1126-319 - C3-05-01 |  | FM008 |  | 2022-01-31 15:11 | 2022-01-31 16:11 | 2022-02-01 16:11 | 24 | 2022-01-31 15:21 | 2022-01-31 17:21 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10085273 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1126-319 – C3-05-01 |  | FM008 |  | 2022-01-29 20:51 | 2022-01-29 21:51 | 2022-01-30 21:51 | 24 | 2022-01-29 21:00 | 2022-01-29 23:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-11076951 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU-A1126-319 FILTER DIRTY |  | FM008 |  | 2022-10-05 10:11 | 2022-10-05 11:11 | 2022-10-06 11:11 | 24 | 2022-10-05 10:22 | 2022-10-05 12:00 | 98 | 196 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11091016 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | Chilled Water insulation damage on supply line resulting in condensation from valve and dropping on duct passing below - C3 05 01 |  | FM008 |  | 2022-10-12 07:11 | 2022-10-12 08:11 | 2022-10-13 08:11 | 24 | 2022-10-12 07:20 | 2022-10-12 10:30 | 190 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2022-11196477 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU-A1126-319 – DUCT INSULATION DAMAGED – C3-05-01 |  | FM008 |  | 2022-11-19 00:08 | 2022-11-19 01:08 | 2022-11-20 01:08 | 24 | 2022-11-19 00:10 | 2022-11-19 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11196467 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | AHU-A1126-319- FILTER DIRTY – C3-05-03 |  | FM008 |  | 2022-11-18 22:01 | 2022-11-18 23:01 | 2022-11-19 23:01 | 24 | 2022-11-18 22:05 | 2022-11-18 23:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-10888039 | ASD-COC-TFL005-AHU145 | AIR HANDLING UNIT-05 | FILTER DIRTY -C3-05-03 |  | FM008 |  | 2022-07-30 13:18 | 2022-07-30 14:18 | 2022-07-31 14:18 | 24 | 2022-07-30 13:25 | 2022-07-30 16:40 | 195 | 105 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11580322 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - ( FCU-A1126-320 ) - C3-03-03 |  | FM008 |  | 2023-03-22 20:04 | 2023-03-22 21:04 | 2023-03-23 21:04 | 24 | 2023-03-22 20:10 | 2023-03-22 23:00 | 170 | 680 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 132112 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12347846 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | AHU LIGHNTING FLEXIBLE CONNECTOR DAMAGE: -AIR HANDLING UNIT 146 (TAG NO:AHU-A1126-320)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 005 |  | FM008 |  | 2023-11-05 04:15 | 2023-11-05 05:15 | 2023-11-06 05:15 | 24 | 2023-11-05 04:20 | 2023-11-05 06:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 138627 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12399590 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | DUCT INFLATION DAMAGE - AIR HANDLING UNIT 146 (TAG NO:AHU-A1126-320)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 005 |  | FM008 |  | 2023-11-23 19:30 | 2023-11-23 20:30 | 2023-11-24 20:30 | 24 | 2023-11-23 19:40 | 2023-11-23 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11237663 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | AHU-A1126-320 C3-05-03 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-03 19:32 | 2022-12-03 20:32 | 2022-12-04 20:32 | 24 | 2022-12-03 19:40 | 2022-12-03 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2024-12587423 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINTS FADED C3-05-03 |  | FM008 |  | 2024-01-22 08:17 | 2024-01-22 09:17 | 2024-01-23 09:17 | 24 | 2024-01-22 08:25 | 2024-01-22 12:35 | 250 | 215 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 77406 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12612334 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-05-03 |  | FM008 |  | 2024-02-01 09:52 | 2024-02-01 10:52 | 2024-02-02 10:52 | 24 | 2024-02-01 09:55 | 2024-02-01 13:50 | 235 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2024-12667102 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | AHU CABIN LAMP HOLDER FAULTY -C3-05-03 |  | FM008 |  | 2024-02-20 10:45 | 2024-02-20 11:45 | 2024-02-21 11:45 | 24 | 2024-02-20 10:50 | 2024-02-20 13:00 | 130 | 260 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 17333 | 95217 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-12423125 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-11-27 19:43 | 2023-11-27 20:43 | 2023-11-28 20:43 | 24 | 2023-11-27 19:50 | 2023-11-27 22:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2024-12690236 | ASD-COC-TFL005-AHU146 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-05-03 |  | FM008 |  | 2024-03-01 19:19 | 2024-03-01 20:19 | 2024-03-02 20:19 | 24 | 2024-03-01 19:25 | 2024-03-01 22:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2022-10085184 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-29 16:37 | 2022-01-29 17:37 | 2022-01-30 17:37 | 24 | 2022-01-29 16:45 | 2022-01-29 18:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10208584 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-02 12:09 | 2022-03-02 13:09 | 2022-03-03 13:09 | 24 | 2022-03-02 12:15 | 2022-03-02 14:30 | 135 | 405 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 87807 |  |  | FM5803 | Tiwari, Mr. Sanjeed Kumar | N - - - |  | Voice Communication
| CM-2023-11970097 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | SUPPLY MOTOR CABLE FAULTY - (MCC-AHU-A1126-357) - |  | FM008 |  | 2023-07-10 09:59 | 2023-07-10 10:59 | 2023-07-11 10:59 | 24 | 2023-07-10 10:05 | 2023-07-10 18:35 | 510 | 590 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 132112 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12253038 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-357 – C3-06-01 |  | FM008 |  | 2023-10-02 14:53 | 2023-10-02 15:53 | 2023-10-03 15:53 | 24 | 2023-10-02 15:00 | 2023-10-02 17:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2024-12737523 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | AHU-A1126-357-DUCT INSULATION DAMAGE - C3-05-03 |  | FM008 |  | 2024-03-18 07:09 | 2024-03-18 08:09 | 2024-03-19 08:09 | 24 | 2024-03-18 07:15 | 2024-03-18 10:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2023-11372211 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGE – AHU-A1126-357 – C3-05-01 |  | FM008 |  | 2023-01-15 22:13 | 2023-01-15 23:13 | 2023-01-16 23:13 | 24 | 2023-01-15 22:20 | 2023-01-16 01:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11784723 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -HIRD FLOOR AREA 005 |  | FM008 |  | 2023-05-12 14:43 | 2023-05-12 15:43 | 2023-05-13 15:43 | 24 | 2023-05-12 14:50 | 2023-05-12 16:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2024-12612299 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2024-02-01 08:14 | 2024-02-01 09:14 | 2024-02-02 09:14 | 24 | 2024-02-01 08:15 | 2024-02-01 10:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68060 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-11253233 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-05-01 |  | FM008 |  | 2022-12-06 20:21 | 2022-12-06 21:21 | 2022-12-07 21:21 | 24 | 2022-12-06 20:30 | 2022-12-06 23:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11913271 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING – C3-05-01 |  | FM008 |  | 2023-06-22 19:52 | 2023-06-22 20:52 | 2023-06-23 20:52 | 24 | 2023-06-22 20:00 | 2023-06-23 01:45 | 345 | 235 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12363576 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-357,C3-05-01 |  | FM008 |  | 2023-11-07 19:33 | 2023-11-07 20:33 | 2023-11-08 20:33 | 24 | 2023-11-07 19:40 | 2023-11-07 22:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2024-12608738 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | AHU-A1126-357 DUCT INSULATION DAMAGED |  | FM008 |  | 2024-01-30 19:27 | 2024-01-30 20:27 | 2024-01-31 20:27 | 24 | 2024-01-30 19:35 | 2024-01-30 21:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10043909 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED;AHU-A1126-357 - C3-05-01 |  | FM008 |  | 2022-01-10 09:59 | 2022-01-10 10:59 | 2022-01-11 10:59 | 24 | 2022-01-10 10:07 | 2022-01-10 11:19 | 72 | 123 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10366417 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | FLEXIBLE HOSE CONNECTOR DAMAGED |  | FM008 |  | 2022-04-15 14:39 | 2022-04-15 15:39 | 2022-04-16 15:39 | 24 | 2022-04-15 15:20 | 2022-04-15 16:49 | 89 | 178 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106972 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11973701 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | AHU-A1126-357 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2023-07-14 19:11 | 2023-07-14 20:11 | 2023-07-15 20:11 | 24 | 2023-07-14 19:15 | 2023-07-14 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12256419 | ASD-COC-TFL005-AHU162 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C3-05-01 |  | FM008 |  | 2023-10-07 21:15 | 2023-10-07 22:15 | 2023-10-08 22:15 | 24 | 2023-10-07 21:20 | 2023-10-08 00:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10202328 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C3-05-03 |  | FM008 |  | 2022-02-28 14:05 | 2022-02-28 15:05 | 2022-03-01 15:05 | 24 | 2022-02-28 14:16 | 2022-02-28 16:25 | 129 | 387 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2022-11252974 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-358 – C3-05-03 – |  | FM008 |  | 2022-12-05 19:26 | 2022-12-05 20:26 | 2022-12-06 20:26 | 24 | 2022-12-05 19:35 | 2022-12-05 23:35 | 240 | 480 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17573 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12043188 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-05-04 |  | FM008 |  | 2023-08-03 22:35 | 2023-08-03 23:35 | 2023-08-04 23:35 | 24 | 2023-08-03 22:45 | 2023-08-04 01:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12200425 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-09-20 19:11 | 2023-09-20 20:11 | 2023-09-21 20:11 | 24 | 2023-09-20 19:15 | 2023-09-21 00:40 | 325 | 485 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12385835 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-17 19:32 | 2023-11-17 20:32 | 2023-11-18 20:32 | 24 | 2023-11-17 19:37 | 2023-11-18 01:15 | 338 | 545 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-11372213 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGE – AHU-A1126-358 – C3-05-03 |  | FM008 |  | 2023-01-15 22:14 | 2023-01-15 23:14 | 2023-01-16 23:14 | 24 | 2023-01-15 22:20 | 2023-01-16 01:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12187853 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-358 |  | FM008 |  | 2023-09-16 21:07 | 2023-09-16 22:07 | 2023-09-17 22:07 | 24 | 2023-09-16 21:10 | 2023-09-17 00:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2022-11189053 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | AHU-A1126-358- CHILLED WATER LINE PAINT FADED- C3-05-03 |  | FM008 |  | 2022-11-14 19:31 | 2022-11-14 20:31 | 2022-11-15 20:31 | 24 | 2022-11-14 19:35 | 2022-11-14 21:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2024-12629859 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | AHU-A1126-358 FILTER DIRTY |  | FM008 |  | 2024-02-08 08:24 | 2024-02-08 09:24 | 2024-02-09 09:24 | 24 | 2024-02-08 08:35 | 2024-02-08 10:55 | 140 | 280 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12741774 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | ELR FAULTY – (MCC-AHU-A1126-358) -C3 05 03 |  | FM008 |  | 2024-03-22 07:07 | 2024-03-22 08:07 | 2024-03-23 08:07 | 24 | 2024-03-22 07:15 | 2024-03-22 10:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12278887 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1126-358 – C3-05-03 |  | FM008 |  | 2023-10-11 13:09 | 2023-10-11 14:09 | 2023-10-12 14:09 | 24 | 2023-10-11 13:15 | 2023-10-11 16:30 | 195 | 545 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12597500 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2024-01-28 09:27 | 2024-01-28 10:27 | 2024-01-29 10:27 | 24 | 2024-01-28 09:35 | 2024-01-28 13:50 | 255 | 320 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12733513 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-358) C3 05 03 |  | FM008 |  | 2024-03-16 22:34 | 2024-03-16 23:34 | 2024-03-17 23:34 | 24 | 2024-03-16 22:40 | 2024-03-17 01:00 | 140 | 420 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12858240 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C3-05-03 |  | FM008 |  | 2024-04-28 19:15 | 2024-04-28 20:15 | 2024-04-29 20:15 | 24 | 2024-04-28 19:20 | 2024-04-28 22:20 | 180 | 275 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10780750 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | AHU-A1126-358- DP 1 FILTER ALARM – C3-05-03 |  | FM008 |  | 2022-06-26 08:23 | 2022-06-26 09:23 | 2022-06-27 09:23 | 24 | 2022-06-26 08:30 | 2022-06-26 14:45 | 375 | 215 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11971223 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -(TAG NO:AHU-A1126-358)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 005 |  | FM008 |  | 2023-07-10 10:00 | 2023-07-10 11:00 | 2023-07-11 11:00 | 24 | 2023-07-10 10:02 | 2023-07-10 13:02 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10309031 | ASD-COC-TFL005-AHU163 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR AIR LEAKAGE - AHU-A1126-358 - MECHANICAL ROOM C3-05-03 |  | FM008 |  | 2022-03-31 21:12 | 2022-03-31 22:12 | 2022-04-01 22:12 | 24 | 2022-03-31 21:20 | 2022-03-31 23:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 005 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17573 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10252782 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C3-01-01 |  | FM008 |  | 2022-03-16 08:32 | 2022-03-16 09:32 | 2022-03-17 09:32 | 24 | 2022-03-16 08:40 | 2022-03-16 11:20 | 160 | 320 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2022-10792820 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-301 – C3-01-01 |  | FM008 |  | 2022-06-30 07:03 | 2022-06-30 08:03 | 2022-07-01 08:03 | 24 | 2022-06-30 07:13 | 2022-06-30 10:14 | 181 | 269 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10917471 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-08-09 16:22 | 2022-08-09 17:22 | 2022-08-10 17:22 | 24 | 2022-08-09 16:25 | 2022-08-09 18:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 55709 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-11114481 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING - C3-01-01 |  | FM008 |  | 2022-10-19 03:47 | 2022-10-19 04:47 | 2022-10-20 04:47 | 24 | 2022-10-19 03:55 | 2022-10-19 05:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11193490 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED - C3-01-01 |  | FM008 |  | 2022-11-16 11:22 | 2022-11-16 12:22 | 2022-11-17 12:22 | 24 | 2022-11-16 11:30 | 2022-11-16 14:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 105233 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2022-11230257 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED - AHU-A1126-301 |  | FM008 |  | 2022-11-28 09:11 | 2022-11-28 10:11 | 2022-11-29 10:11 | 24 | 2022-11-28 09:20 | 2022-11-28 11:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11350496 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE -:AHU-A1126-301-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2023-01-06 19:28 | 2023-01-06 20:28 | 2023-01-07 20:28 | 24 | 2023-01-06 19:35 | 2023-01-06 21:30 | 115 | 230 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11523104 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301 CABIN LIGHT SWITCH FAULTY |  | FM008 |  | 2023-03-06 08:11 | 2023-03-06 09:11 | 2023-03-07 09:11 | 24 | 2023-03-06 08:15 | 2023-03-06 09:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11620419 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC TOO NOISY NEAR C2-01-36 CORRIDOOR |  | FM008 |  | 2023-04-03 12:46 | 2023-04-03 13:46 | 2023-04-04 13:46 | 24 | 2023-04-03 12:55 | 2023-04-03 13:55 | 60 | 180 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 17053 |  |  | 125847 | Saha, Mr. Somnath | N - - - |  | Voice Communication
| CM-2023-11621111 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-04-05 19:18 | 2023-04-05 20:18 | 2023-04-06 20:18 | 24 | 2023-04-05 19:25 | 2023-04-05 21:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11843455 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED - AHU-A1126-301- T3 01 01 |  | FM008 |  | 2023-06-02 16:03 | 2023-06-02 17:03 | 2023-06-03 17:03 | 24 | 2023-06-02 16:10 | 2023-06-02 18:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12451249 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC NOT WORKING - ROOM 3345(TAG NO: C2-01-05 (STAFF BRIEFING ROOM))-AIRSIDE-CONCOURSE C-SECOND FLOOR AREA 001 |  | FM008 |  | 2023-12-07 11:08 | 2023-12-07 12:08 | 2023-12-08 12:08 | 24 | 2023-12-07 11:18 | 2023-12-07 13:30 | 132 | 35 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 137948 | Ferrer, Mr. Lorrenz Icely De Villa | N - - - |  | Voice Communication
| CM-2022-11165899 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-11-08 19:29 | 2022-11-08 20:29 | 2022-11-09 20:29 | 24 | 2022-11-08 19:35 | 2022-11-08 21:30 | 115 | 230 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11630745 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301–DUCT INSULATION DAMAGED- - |  | FM008 |  | 2023-04-08 19:08 | 2023-04-08 20:08 | 2023-04-09 20:08 | 24 | 2023-04-08 19:15 | 2023-04-08 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11835180 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | NEAR C2-01-36 A/C IS TOO NOISY |  | FM008 |  | 2023-05-30 10:47 | 2023-05-30 11:47 | 2023-05-31 11:47 | 24 | 2023-05-30 10:50 | 2023-05-30 12:25 | 95 | 65 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOISY | MISALIGNMENT | RECTIFIED | 68060 | 87807 |  |  | 85054 | Sheikh, Mr. Sarjil | N - - - |  | Voice Communication
| CM-2023-12007438 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301-(DUST INSULATION DAMAGE) |  | FM008 |  | 2023-07-25 07:27 | 2023-07-25 08:27 | 2023-07-26 08:27 | 24 | 2023-07-25 07:35 | 2023-07-25 10:10 | 155 | 465 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12156777 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | RELEASE FAN FLEXIBLE CONNECTOR DAMAGED-AIR HANDLING UNIT 127 (TAG NO:AHU-A1126-301)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2023-09-05 16:08 | 2023-09-05 17:08 | 2023-09-06 17:08 | 24 | 2023-09-05 16:17 | 2023-09-05 18:47 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17336 | 87807 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2024-12533751 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC IS TOO COLD -ROOM 3329(TAG NO: C2-01-06 (STAFF DEPLOYMENT ROOM))-AIRSIDE-CONCOURSE C-SECOND FLOOR AREA 001 |  | FM008 |  | 2024-01-02 10:07 | 2024-01-02 11:07 | 2024-01-03 11:07 | 24 | 2024-01-02 10:10 | 2024-01-02 11:00 | 50 | 50 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 109375 | Etchu, Mr. Clarkson Agbor Eyong | N - - - |  | Voice Communication
| CM-2022-10913019 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER ALARM - (TAG NO:AHU-A1126-301) CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2022-08-03 07:57 | 2022-08-03 08:57 | 2022-08-04 08:57 | 24 | 2022-08-03 08:00 | 2022-08-03 13:30 | 330 | 185 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 55709 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-11668093 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | C1-01-15- AC IS TOO HOT – - |  | FM008 |  | 2023-04-15 22:26 | 2023-04-15 23:26 | 2023-04-16 23:26 | 24 | 2023-04-15 22:30 | 2023-04-16 01:00 | 150 | 50 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94953 | 17053 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2023-12085235 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC IS NOT WORKING -C1-01-15-UPGRADE ON DEPARTURE BEHIND SAMSUNG SHOP GATE C2 |  | FM008 |  | 2023-08-15 05:53 | 2023-08-15 06:53 | 2023-08-16 06:53 | 24 | 2023-08-15 06:00 | 2023-08-15 06:30 | 30 | 30 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2023-12363698 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC NOT WORKING |  | FM008 |  | 2023-11-07 07:02 | 2023-11-07 08:02 | 2023-11-08 08:02 | 24 | 2023-11-07 07:10 | 2023-11-07 08:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 137948 | Ferrer, Mr. Lorrenz Icely De Villa | N - - - |  | Voice Communication
| CM-2024-12846141 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301 DUCT INSULATION DAMAGE - AIR HANDLING UNIT 127 (TAG NO:AHU-A1126-301)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2024-04-23 22:02 | 2024-04-23 23:02 | 2024-04-24 23:02 | 24 | 2024-04-23 22:10 | 2024-04-24 01:00 | 170 | 510 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12363480 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC TOO COLD - C2-01-01 |  | FM008 |  | 2023-11-07 12:54 | 2023-11-07 13:54 | 2023-11-08 13:54 | 24 | 2023-11-07 13:00 | 2023-11-07 13:45 | 45 | 45 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 108333 | Jayakumar Jayasree, Mr. Jayasankar | N - - - |  | Voice Communication
| CM-2024-12701131 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY |  | FM008 |  | 2024-03-03 19:22 | 2024-03-03 20:22 | 2024-03-04 20:22 | 24 | 2024-03-03 19:30 | 2024-03-03 21:25 | 115 | 230 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12704677 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC TOO HOT – QATAR AIRWAYS UPGRADE DESK - BEHIND THE SAMSUNG STORE NEAR GATE C1 |  | FM008 |  | 2024-03-05 22:34 | 2024-03-05 23:34 | 2024-03-06 23:34 | 24 | 2024-03-05 22:40 | 2024-03-06 01:45 | 185 | 35 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 17053 |  |  | 118843 | Rodrigues, Ms. Carmel | N - - - |  | Voice Communication
| CM-2022-10146450 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2022-02-15 13:58 | 2022-02-15 14:58 | 2022-02-16 14:58 | 24 | 2022-02-15 14:05 | 2022-02-15 16:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10809875 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AC TOO HOT – C2-01-03 & C2-01-06 |  | FM008 |  | 2022-07-04 14:34 | 2022-07-04 15:34 | 2022-07-05 15:34 | 24 | 2022-07-04 14:35 | 2022-07-04 16:15 | 100 | 35 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 95217 |  |  | 108333 | Jayakumar Jayasree, Mr. Jayasankar | N - - - |  | Voice Communication
| CM-2022-11006212 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | C3 01 01 Mechanical Room in Concourse-C chilled Water leakage from DRV valve and strainer, insulation damage. |  | FM008 |  | 2022-09-11 09:08 | 2022-09-11 10:08 | 2022-09-12 10:08 | 24 | 2022-09-11 09:18 | 2022-09-11 13:35 | 257 | 75 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2022-11091010 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301 – FILTER ALARM-- |  | FM008 |  | 2022-10-12 07:01 | 2022-10-12 08:01 | 2022-10-13 08:01 | 24 | 2022-10-12 07:10 | 2022-10-12 11:45 | 275 | 145 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10032966 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301 SUPPLY DUCT ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-01-09 05:43 | 2022-01-09 06:43 | 2022-01-10 06:43 | 24 | 2022-01-09 05:48 | 2022-01-09 06:48 | 60 | 180 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10142787 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | AHU-A1126-301 - DUCT INSULATION DAMAGED – C3-01-01 |  | FM008 |  | 2022-02-17 16:37 | 2022-02-17 17:37 | 2022-02-18 17:37 | 24 | 2022-02-17 16:40 | 2022-02-17 18:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10777070 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | MESH BLOWER PAINT PEALED OFF IN MATAR SAFETY OFFICE -C2-01-03 |  | FM008 |  | 2022-06-23 21:20 | 2022-06-23 22:20 | 2022-06-24 22:20 | 24 | 2022-06-23 21:25 | 2022-06-23 23:15 | 110 | 90 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | FAN BLOWER IS DIRTY | CLEANED THE BLOWER | 106914 | 87807 |  |  | 107227 | Mohammed, Mr. Viquaruddin Ahmed | N - - - |  | E-mail
| CM-2022-10777072 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | Paint peel off from the ceiling mesh of blower -C2-01-06 |  | FM008 |  | 2022-06-23 21:29 | 2022-06-23 22:29 | 2022-06-24 22:29 | 24 | 2022-06-23 21:35 | 2022-06-23 23:55 | 140 | 80 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | FAN BLOWER IS DIRTY | CLEANED THE BLOWER | 106914 | 87807 |  |  | 107227 | Mohammed, Mr. Viquaruddin Ahmed | N - - - |  | E-mail
| CM-2023-12188541 | ASD-COC-TFL001-AHU127 | AIR HANDLING UNIT-05 | UNUSUAL NOISE COMING FROM CEILING - NEAR C2-01-36 (GATE C2 ARRIVAL LEVEL) |  | FM008 |  | 2023-09-16 01:57 | 2023-09-16 02:57 | 2023-09-17 02:57 | 24 | 2023-09-16 02:05 | 2023-09-16 03:15 | 70 | 70 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 95216 | 87807 |  |  | 17760 | Rafeeq, Mr. Mohammed | N - - - |  | Voice Communication
| CM-2022-10104542 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE -AHU-A1126-302 |  | FM008 |  | 2022-02-02 12:20 | 2022-02-02 13:20 | 2022-02-03 13:20 | 24 | 2022-02-02 12:30 | 2022-02-02 14:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10171190 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE -C3-01-03 |  | FM008 |  | 2022-02-24 00:10 | 2022-02-24 01:10 | 2022-02-25 01:10 | 24 | 2022-02-24 00:15 | 2022-02-24 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106914 | 55709 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10832029 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | SUPPLY AC GRILL DIRTY-C3-01-03 |  | FM008 |  | 2022-07-15 07:18 | 2022-07-15 08:18 | 2022-07-16 08:18 | 24 | 2022-07-15 07:25 | 2022-07-15 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106914 | 95217 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12007319 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C3-01-04 |  | FM008 |  | 2023-07-24 19:11 | 2023-07-24 20:11 | 2023-07-25 20:11 | 24 | 2023-07-24 19:15 | 2023-07-24 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12850079 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 DUCT INSULATION DAMAGED C3-01-03 |  | FM008 |  | 2024-04-25 07:39 | 2024-04-25 08:39 | 2024-04-26 08:39 | 24 | 2024-04-25 07:45 | 2024-04-25 10:00 | 135 | 175 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10903621 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 – DP3 FILTER DIRTY |  | FM008 |  | 2022-08-01 14:19 | 2022-08-01 15:19 | 2022-08-02 15:19 | 24 | 2022-08-01 14:20 | 2022-08-01 15:48 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 76858 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2022-11062831 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 AHU INSIDE LAMP NOT WORKING C3-01-03 |  | FM008 |  | 2022-09-29 03:30 | 2022-09-29 04:30 | 2022-09-30 04:30 | 24 | 2022-09-29 03:39 | 2022-09-29 05:07 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 87807 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11177335 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - C3-01-03 |  | FM008 |  | 2022-11-09 19:37 | 2022-11-09 20:37 | 2022-11-10 20:37 | 24 | 2022-11-09 19:45 | 2022-11-09 21:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17053 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11354187 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-302 – C3-01-03 |  | FM008 |  | 2023-01-06 21:22 | 2023-01-06 22:22 | 2023-01-07 22:22 | 24 | 2023-01-06 21:30 | 2023-01-06 23:50 | 140 | 365 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12044326 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-05 07:14 | 2023-08-05 08:14 | 2023-08-06 08:14 | 24 | 2023-08-05 07:20 | 2023-08-05 10:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12128134 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-29 17:44 | 2023-08-29 18:44 | 2023-08-30 18:44 | 24 | 2023-08-29 17:50 | 2023-08-29 18:50 | 60 | 180 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12366571 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-11 20:00 | 2023-11-11 21:00 | 2023-11-12 21:00 | 24 | 2023-11-11 20:10 | 2023-11-11 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12852265 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-302 – C1-01-03 |  | FM008 |  | 2024-04-28 07:18 | 2024-04-28 08:18 | 2024-04-29 08:18 | 24 | 2024-04-28 07:25 | 2024-04-28 10:35 | 190 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | BMS
| CM-2023-11971355 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2023-07-10 19:06 | 2023-07-10 20:06 | 2023-07-11 20:06 | 24 | 2023-07-10 19:10 | 2023-07-10 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12229990 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | DUCT IINSULATION DAMAGED – C3-01-03 |  | FM008 |  | 2023-09-26 22:34 | 2023-09-26 23:34 | 2023-09-27 23:34 | 24 | 2023-09-26 22:40 | 2023-09-27 01:40 | 180 | 320 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12231576 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH FAULTY - AIR HANDLING UNIT 128 (TAG NO:AHU-A1126-302)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2023-09-28 22:00 | 2023-09-28 23:00 | 2023-09-29 23:00 | 24 | 2023-09-28 22:08 | 2023-09-29 01:25 | 197 | 363 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 119320 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12504906 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C3-01-03 |  | FM008 |  | 2023-12-25 08:05 | 2023-12-25 09:05 | 2023-12-26 09:05 | 24 | 2023-12-25 08:10 | 2023-12-25 17:00 | 530 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12510569 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 RETURN AC GRILL DIRTY |  | FM008 |  | 2023-12-26 19:04 | 2023-12-26 20:04 | 2023-12-27 20:04 | 24 | 2023-12-26 19:10 | 2023-12-26 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10119423 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-02-07 12:00 | 2022-02-07 13:00 | 2022-02-08 13:00 | 24 | 2022-02-07 12:10 | 2022-02-07 14:15 | 125 | 375 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11175455 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | RETURN GRILL DIRTY - C2-01-32 |  | FM008 |  | 2022-11-08 09:28 | 2022-11-08 10:28 | 2022-11-09 10:28 | 24 | 2022-11-08 09:35 | 2022-11-08 13:35 | 240 | 195 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10820773 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-07-06 11:27 | 2022-07-06 12:27 | 2022-07-07 12:27 | 24 | 2022-07-06 11:30 | 2022-07-06 14:30 | 180 | 185 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10888784 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | C3 01 03 AHU Room in Concourse-C - AHU A1126-302 - Supply duct access door CAP-06 is having condensation, water dripping to the floor. Investigate and find the reason. Share beedback with Assurance and Delivery team |  | FM008 |  | 2022-07-31 08:07 | 2022-07-31 09:07 | 2022-08-01 09:07 | 24 | 2022-07-31 08:16 | 2022-07-31 11:05 | 169 | 65 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 87807 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2022-10888785 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | C3 01 03 AHU Room in Concourse-C - AHU A1126-302 - Chilled water supply line strainer is leaky. Investigate and resolve it. |  | FM008 |  | 2022-07-31 08:08 | 2022-07-31 09:08 | 2022-08-01 09:08 | 24 | 2022-07-31 08:15 | 2022-07-31 11:45 | 210 | 75 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 87807 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2023-12235041 | ASD-COC-TFL001-AHU128 | AIR HANDLING UNIT-05 | AHU-A1126-302 FILTER DIRTY C3-01-03 |  | FM008 |  | 2023-09-30 15:17 | 2023-09-30 16:17 | 2023-10-01 16:17 | 24 | 2023-09-30 15:25 | 2023-09-30 17:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 87807 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2022-10886338 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | FILTER ALARM -AHU-A1126-303)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2022-07-30 18:57 | 2022-07-30 19:57 | 2022-07-31 19:57 | 24 | 2022-07-30 19:00 | 2022-07-30 19:40 | 40 | 80 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11350497 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE-(AHU-A1126-303) CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2023-01-06 19:35 | 2023-01-06 20:35 | 2023-01-07 20:35 | 24 | 2023-01-06 19:45 | 2023-01-06 21:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11818252 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO HOT - UPGRADE COUNTER AREA IN GATE C2 NEAR C1-01-15 |  | FM008 |  | 2023-05-22 05:15 | 2023-05-22 06:15 | 2023-05-23 06:15 | 24 | 2023-05-22 05:20 | 2023-05-22 06:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 105233 | 17053 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2023-12217174 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED C3-01-01 |  | FM008 |  | 2023-09-24 11:45 | 2023-09-24 12:45 | 2023-09-25 12:45 | 24 | 2023-09-24 11:50 | 2023-09-24 14:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-11165900 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AHU-A1126-303 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-11-08 19:30 | 2022-11-08 20:30 | 2022-11-09 20:30 | 24 | 2022-11-08 19:35 | 2022-11-08 23:40 | 245 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11690747 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO HOT AREA C1-01-15 |  | FM008 |  | 2023-04-19 22:57 | 2023-04-19 23:57 | 2023-04-20 23:57 | 24 | 2023-04-19 23:05 | 2023-04-20 01:15 | 130 | 65 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 77406 | 87807 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2024-12668169 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC NOT WORKING -ACTIVITY NODE 3 |  | FM008 |  | 2024-02-19 09:54 | 2024-02-19 10:54 | 2024-02-20 10:54 | 24 | 2024-02-19 10:00 | 2024-02-19 15:05 | 305 | 65 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 87807 |  |  | FM11723 | Nakanwagi, Ms. Safinah | N - - - |  | Voice Communication
| CM-2024-12796128 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC NOT WORKING READING ROOM NEAR C1-02-03 |  | FM008 |  | 2024-04-04 23:01 | 2024-04-05 00:01 | 2024-04-06 00:01 | 24 | 2024-04-04 23:10 | 2024-04-05 00:45 | 95 | 65 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | FM11723 | Nakanwagi, Ms. Safinah | N - - - |  | Voice Communication
| CM-2022-11006213 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | C3 01 01 Mechanical Room in Concourse-C chilled Water leakage from DRV valve and insulation damage on the CHILLED water supply line. |  | FM008 |  | 2022-09-11 09:09 | 2022-09-11 10:09 | 2022-09-12 10:09 | 24 | 2022-09-11 09:19 | 2022-09-11 14:15 | 296 | 75 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2023-11694957 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | C1-01 -15,UOD COUNTER ( UPGRADING COUNTER AREA) NEAR GATE C2 – AC TOO COLD |  | FM008 |  | 2023-04-21 02:31 | 2023-04-21 03:31 | 2023-04-22 03:31 | 24 | 2023-04-21 02:35 | 2023-04-21 03:10 | 35 | 35 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2023-11972747 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-303 – C3 01 01 |  | FM008 |  | 2023-07-12 21:18 | 2023-07-12 22:18 | 2023-07-13 22:18 | 24 | 2023-07-12 21:25 | 2023-07-12 23:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12358209 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-303 – C3-01-01 |  | FM008 |  | 2023-11-05 19:59 | 2023-11-05 20:59 | 2023-11-06 20:59 | 24 | 2023-11-05 20:05 | 2023-11-05 23:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12328664 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO COLD – UOD COUNTER AREA NEAR C1-01-15 |  | FM008 |  | 2023-10-28 23:55 | 2023-10-29 00:55 | 2023-10-30 00:55 | 24 | 2023-10-29 00:05 | 2023-10-29 01:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 87807 |  |  | 105209 | Ghale, Ms. Poonam | N - - - |  | Voice Communication
| CM-2023-12346275 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY – C3-01-01 |  | FM008 |  | 2023-11-03 13:01 | 2023-11-03 14:01 | 2023-11-04 14:01 | 24 | 2023-11-03 13:10 | 2023-11-03 16:15 | 185 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 105233 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10142079 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C3-01-01 |  | FM008 |  | 2022-02-19 15:24 | 2022-02-19 16:24 | 2022-02-20 16:24 | 24 | 2022-02-19 15:30 | 2022-02-19 18:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10276135 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO HOT |  | FM008 |  | 2022-03-24 16:13 | 2022-03-24 17:13 | 2022-03-25 17:13 | 24 | 2022-03-24 16:20 | 2022-03-24 19:30 | 190 | 35 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 55709 |  |  | 82565 | Karimova, Ms. Ramziya | N - - - |  | Voice Communication
| CM-2022-11157776 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | WATER CONDENSATION FROM CEILING,NEAR,-C2-01-36. |  | FM008 |  | 2022-11-02 23:34 | 2022-11-03 00:34 | 2022-11-04 00:34 | 24 | 2022-11-02 23:40 | 2022-11-03 01:00 | 80 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 77406 | 87807 |  |  | 17537 | Agyapong, Mr. Abraham Sono Kwame | N - - - |  | Voice Communication
| CM-2022-11277675 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO COLD - UOD COUNTER BESIDE SAMSUNG SHOP NEAR C1-01-15 |  | FM008 |  | 2022-12-19 10:40 | 2022-12-19 11:40 | 2022-12-20 11:40 | 24 | 2022-12-19 10:45 | 2022-12-19 11:40 | 55 | 55 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 55709 |  |  | 105209 | Ghale, Ms. Poonam | N - - - |  | Voice Communication
| CM-2023-11660756 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO HOT IN UPGRADE ON DEPARTURE COUNTER , NEAR C1-01-15 |  | FM008 |  | 2023-04-14 05:36 | 2023-04-14 06:36 | 2023-04-15 06:36 | 24 | 2023-04-14 05:45 | 2023-04-14 06:15 | 30 | 30 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 87807 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2023-11684287 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | C1-01-15 QR COUNTERS - AC TOO HOT |  | FM008 |  | 2023-04-18 22:17 | 2023-04-18 23:17 | 2023-04-19 23:17 | 24 | 2023-04-18 22:25 | 2023-04-18 23:35 | 70 | 50 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | 100842 | Vincent, Ms. Beatrice | N - - - |  | Voice Communication
| CM-2022-10145894 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AHU-A1126-303 CHILLED WATER LINE PAINT FADED C3-01-01 |  | FM008 |  | 2022-02-15 16:07 | 2022-02-15 17:07 | 2022-02-16 17:07 | 24 | 2022-02-15 16:17 | 2022-02-15 18:25 | 128 | 384 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 89127 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10251923 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED - AHU-A1126-303 – C3-01-01 |  | FM008 |  | 2022-03-16 11:20 | 2022-03-16 12:20 | 2022-03-17 12:20 | 24 | 2022-03-16 11:30 | 2022-03-16 13:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10592436 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) – NEAR C1-01-15 - PASSENGERS ARE COMPLAINING |  | FM008 |  | 2022-04-25 13:41 | 2022-04-25 14:11 | 2022-04-25 18:11 | 4 | 2022-04-25 13:45 | 2022-04-25 15:30 | 105 | 65 | 1 | HVAC |  | Closed | Urgent | THIRD FLOOR AREA 001 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 17053 |  |  | 82565 | Karimova, Ms. Ramziya | N - - - |  | Voice Communication
| CM-2023-12252421 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-303 - MECHANICAL ROOM C3-01-01 |  | FM008 |  | 2023-10-03 15:36 | 2023-10-03 16:36 | 2023-10-04 16:36 | 24 | 2023-10-03 15:45 | 2023-10-03 17:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12779056 | ASD-COC-TFL001-AHU129 | AIR HANDLING UNIT-05 | AC TOO WARM - NEAR C1-01-15 OPEN AREA |  | FM008 |  | 2024-03-30 05:45 | 2024-03-30 06:45 | 2024-03-31 06:45 | 24 | 2024-03-30 05:50 | 2024-03-30 08:00 | 130 | 65 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 64691 | Fraylon, Mr. Jefferson Elnas | N - - - |  | Voice Communication
| CM-2022-10886002 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1126-304 – C3-01-03 |  | FM008 |  | 2022-07-29 15:18 | 2022-07-29 16:18 | 2022-07-30 16:18 | 24 | 2022-07-29 15:25 | 2022-07-29 18:00 | 155 | 115 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12090236 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-304 C3-01-03 |  | FM008 |  | 2023-08-16 22:29 | 2023-08-16 23:29 | 2023-08-17 23:29 | 24 | 2023-08-16 22:35 | 2023-08-17 00:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17573 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2023-12274102 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | AHU-A1126-304 FILTER DIRTY |  | FM008 |  | 2023-10-10 23:05 | 2023-10-11 00:05 | 2023-10-12 00:05 | 24 | 2023-10-10 23:10 | 2023-10-11 01:40 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11177336 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - C3-01-03 |  | FM008 |  | 2022-11-09 19:39 | 2022-11-09 20:39 | 2022-11-10 20:39 | 24 | 2022-11-09 19:45 | 2022-11-09 23:50 | 245 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17053 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11354189 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - AHU-A1126-304 – C3-01-03 |  | FM008 |  | 2023-01-06 21:26 | 2023-01-06 22:26 | 2023-01-07 22:26 | 24 | 2023-01-06 21:35 | 2023-01-06 23:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11763580 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED |  | FM008 |  | 2023-05-04 20:01 | 2023-05-04 21:01 | 2023-05-05 21:01 | 24 | 2023-05-04 20:05 | 2023-05-04 22:45 | 160 | 640 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12232068 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM THE AC VENT NEAR C1-01-016 - DUPLICATE WORK ORDER CM-2023-12230125 |  | FM008 |  | 2023-09-27 11:05 | 2023-09-27 12:05 | 2023-09-28 12:05 | 24 | 2023-09-27 11:10 | 2023-09-27 14:00 | 170 | 125 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17333 | 87807 |  |  | FM8120 | JAMAL | N - - - |  | Voice Communication
| CM-2024-12796373 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2024-04-05 10:48 | 2024-04-05 11:48 | 2024-04-06 11:48 | 24 | 2024-04-05 10:50 | 2024-04-05 12:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12484528 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | AHU-A1126-304)-FILTER DIRTY -C3-01-03) |  | FM008 |  | 2023-12-16 20:48 | 2023-12-16 21:48 | 2023-12-17 21:48 | 24 | 2023-12-16 20:55 | 2023-12-16 22:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2024-12850208 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-C3-01-03 |  | FM008 |  | 2024-04-25 20:25 | 2024-04-25 21:25 | 2024-04-26 21:25 | 24 | 2024-04-25 20:30 | 2024-04-25 23:15 | 165 | 330 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12511665 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | C3-01-03 AHU-A1126-304 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-28 08:51 | 2023-12-28 09:51 | 2023-12-29 09:51 | 24 | 2023-12-28 08:55 | 2023-12-28 14:00 | 305 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-10046925 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED AHU-A1126-304 |  | FM008 |  | 2022-01-13 00:03 | 2022-01-13 01:03 | 2022-01-14 01:03 | 24 | 2022-01-13 00:10 | 2022-01-13 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 68060 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | BMS
| CM-2022-10119424 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-02-07 12:01 | 2022-02-07 13:01 | 2022-02-08 13:01 | 24 | 2022-02-07 12:10 | 2022-02-07 14:30 | 140 | 280 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11038299 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | AHU-A1126-304 DP1 FILTER ALARM C3-01-03 |  | FM008 |  | 2022-09-19 07:03 | 2022-09-19 08:03 | 2022-09-20 08:03 | 24 | 2022-09-19 07:10 | 2022-09-19 11:44 | 274 | 183 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 89127 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11170806 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-07 12:33 | 2022-11-07 13:33 | 2022-11-08 13:33 | 24 | 2022-11-07 12:40 | 2022-11-07 16:45 | 245 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-11361354 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | FILTER DIRTY - C3-01-03 |  | FM008 |  | 2023-01-08 15:00 | 2023-01-08 16:00 | 2023-01-09 16:00 | 24 | 2023-01-08 15:05 | 2023-01-08 16:40 | 95 | 285 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2023-11668594 | ASD-COC-TFL001-AHU130 | AIR HANDLING UNIT-05 | AHU-A1126-304- HEATER SUPPLY CABLE FLEXIBLE CONNECTOR DAMAGED C3-01-03 |  | FM008 |  | 2023-04-15 20:06 | 2023-04-15 21:06 | 2023-04-16 21:06 | 24 | 2023-04-15 20:10 | 2023-04-15 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 87807 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10080391 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | CHILLED WATERLINE PAINT FADED C3-01-03 |  | FM008 |  | 2022-01-26 12:19 | 2022-01-26 13:19 | 2022-01-27 13:19 | 24 | 2022-01-26 12:29 | 2022-01-26 14:29 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 87807 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10202327 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -C3-01-03 |  | FM008 |  | 2022-02-28 14:03 | 2022-02-28 15:03 | 2022-03-01 15:03 | 24 | 2022-02-28 14:10 | 2022-02-28 16:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2022-10780826 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU-A1126-350 C3-01-03 DP1 FILTER DIRTY |  | FM008 |  | 2022-06-26 19:21 | 2022-06-26 20:21 | 2022-06-27 20:21 | 24 | 2022-06-26 19:30 | 2022-06-26 21:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 95217 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-12050622 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | C3-01-03-DUCT INSULATION DAMAGED-AHU-A1126-350)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 001 |  | FM008 |  | 2023-08-05 22:53 | 2023-08-05 23:53 | 2023-08-06 23:53 | 24 | 2023-08-05 23:00 | 2023-08-06 01:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2024-12850080 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU-A1126-350 DUCT INSULATION DAMAGED C3-01-03 |  | FM008 |  | 2024-04-25 07:40 | 2024-04-25 08:40 | 2024-04-26 08:40 | 24 | 2024-04-25 07:45 | 2024-04-25 10:05 | 140 | 185 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11062832 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU-A1126-350 AHU INSIDE LAMP NOT WORKING C3-01-03 |  | FM008 |  | 2022-09-29 03:31 | 2022-09-29 04:31 | 2022-09-30 04:31 | 24 | 2022-09-29 03:41 | 2022-09-29 06:40 | 179 | 188 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 87807 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12414011 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-350) |  | FM008 |  | 2023-11-26 13:12 | 2023-11-26 14:12 | 2023-11-27 14:12 | 24 | 2023-11-26 13:20 | 2023-11-26 14:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2024-12852266 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-350 – C3-01-03 |  | FM008 |  | 2024-04-28 07:19 | 2024-04-28 08:19 | 2024-04-29 08:19 | 24 | 2024-04-28 07:25 | 2024-04-28 08:25 | 60 | 120 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | BMS
| CM-2022-11176852 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU-A1126-350- CHILLER LINE PAINT FADED – C3-01-03- |  | FM008 |  | 2022-11-11 19:15 | 2022-11-11 20:15 | 2022-11-12 20:15 | 24 | 2022-11-11 19:20 | 2022-11-11 23:30 | 250 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11255733 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU-A1126-350 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-09 07:14 | 2022-12-09 08:14 | 2022-12-10 08:14 | 24 | 2022-12-09 07:20 | 2022-12-09 10:30 | 190 | 760 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12504907 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C3-01-03 |  | FM008 |  | 2023-12-25 08:06 | 2023-12-25 09:06 | 2023-12-26 09:06 | 24 | 2023-12-25 08:10 | 2023-12-25 14:30 | 380 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12398753 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-350 - MECHANICAL ROOM C3-01-03 |  | FM008 |  | 2023-11-20 07:32 | 2023-11-20 08:32 | 2023-11-21 08:32 | 24 | 2023-11-20 07:40 | 2023-11-20 11:00 | 200 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12229495 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY -C3-01-03 |  | FM008 |  | 2023-09-29 00:58 | 2023-09-29 01:58 | 2023-09-30 01:58 | 24 | 2023-09-29 01:10 | 2023-09-29 04:30 | 200 | 355 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 87807 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2024-12745635 | ASD-COC-TFL001-AHU155 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-01-03 |  | FM008 |  | 2024-03-20 07:01 | 2024-03-20 08:01 | 2024-03-21 08:01 | 24 | 2024-03-20 07:02 | 2024-03-20 10:02 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 001 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10135086 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | INSULATION DAMAGED |  | FM008 |  | 2022-02-13 10:56 | 2022-02-13 11:56 | 2022-02-14 11:56 | 24 | 2022-02-13 11:05 | 2022-02-13 13:35 | 150 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2023-12007320 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C3-03-02 |  | FM008 |  | 2023-07-24 19:12 | 2023-07-24 20:12 | 2023-07-25 20:12 | 24 | 2023-07-24 19:20 | 2023-07-24 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2023-12510432 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-305 -C3-02-01 |  | FM008 |  | 2023-12-26 12:30 | 2023-12-26 13:30 | 2023-12-27 13:30 | 24 | 2023-12-26 12:35 | 2023-12-26 13:35 | 60 | 180 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM12771 | Philip, Mr. Anthony Felix | N - - - |  | Voice Communication
| CM-2022-10903623 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | AHU-A1126-305- DP3 FILTER DIRTY-- |  | FM008 |  | 2022-08-01 14:20 | 2022-08-01 15:20 | 2022-08-02 15:20 | 24 | 2022-08-01 14:30 | 2022-08-01 17:19 | 169 | 162 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 76858 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2023-11842072 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | UCT INSULATION DAMAGED – AHU-A1126-305 – C3 02 01 |  | FM008 |  | 2023-06-03 14:58 | 2023-06-03 15:58 | 2023-06-04 15:58 | 24 | 2023-06-03 15:07 | 2023-06-03 17:30 | 143 | 429 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 89127 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12304856 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AIR HANDLING UNIT 131 (TAG NO:AHU-A1126-305)-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2023-10-22 08:24 | 2023-10-22 09:24 | 2023-10-23 09:24 | 24 | 2023-10-22 08:35 | 2023-10-22 11:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2022-11232407 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING - AHU-A1126-305 – C3-02-01 |  | FM008 |  | 2022-11-29 19:01 | 2022-11-29 20:01 | 2022-11-30 20:01 | 24 | 2022-11-29 19:10 | 2022-11-29 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11361582 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | AHU-A1126-305 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-09 07:29 | 2023-01-09 08:29 | 2023-01-10 08:29 | 24 | 2023-01-09 07:35 | 2023-01-09 11:30 | 235 | 500 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11932777 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | SUPPLY MOTOR FLEXIBLE CONNECTOR DAMAGED - AHU-A1126-305 – C3-02-01 |  | FM008 |  | 2023-06-28 16:00 | 2023-06-28 17:00 | 2023-06-29 17:00 | 24 | 2023-06-28 16:10 | 2023-06-28 22:00 | 350 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 133396 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-12363247 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-305 – C3-02-01 |  | FM008 |  | 2023-11-06 20:00 | 2023-11-06 21:00 | 2023-11-07 21:00 | 24 | 2023-11-06 20:05 | 2023-11-06 23:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10820775 | ASD-COC-TFL002-AHU131 | AIR HANDLING UNIT-05 | DP FILTER ALARM |  | FM008 |  | 2022-07-06 11:28 | 2022-07-06 12:28 | 2022-07-07 12:28 | 24 | 2022-07-06 11:38 | 2022-07-06 13:10 | 92 | 184 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10820366 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU-A1126-306 - DP3 FILTER ALARM |  | FM008 |  | 2022-07-07 07:36 | 2022-07-07 08:36 | 2022-07-08 08:36 | 24 | 2022-07-07 07:45 | 2022-07-07 11:35 | 230 | 290 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11178466 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU-A1126-306 – CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-11-10 19:21 | 2022-11-10 20:21 | 2022-11-11 20:21 | 24 | 2022-11-10 19:30 | 2022-11-10 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12511654 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU-A1126-306 -- AHU CABIN LIGHT NOT WORKING -- AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2023-12-28 08:20 | 2023-12-28 09:20 | 2023-12-29 09:20 | 24 | 2023-12-28 08:30 | 2023-12-28 13:20 | 290 | 335 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 138627 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-11348519 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED – C3-02-03 – AHU-A1126-306 |  | FM008 |  | 2023-01-07 00:07 | 2023-01-07 01:07 | 2023-01-08 01:07 | 24 | 2023-01-07 00:15 | 2023-01-07 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10951204 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | HEATER CONDUCTOR FAULTY - AHU-A1126-306 – C3-03-02 |  | FM008 |  | 2022-08-15 08:09 | 2022-08-15 09:09 | 2022-08-16 09:09 | 24 | 2022-08-15 08:18 | 2022-08-15 12:39 | 261 | 188 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 106973 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11361583 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU-A1126-306 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-09 07:30 | 2023-01-09 08:30 | 2023-01-10 08:30 | 24 | 2023-01-09 07:40 | 2023-01-09 12:45 | 305 | 485 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11938257 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH DAMAGED, AHU-A1126-3036, C3-03-02 |  | FM008 |  | 2023-07-01 16:04 | 2023-07-01 17:04 | 2023-07-02 17:04 | 24 | 2023-07-01 16:13 | 2023-07-01 18:41 | 148 | 296 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | DOOR HINGES LOOSE/DAMAGED | REPAIRED/REPLACED | 124475 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12378754 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE - AIR HANDLING UNIT 132 (TAG NO:AHU-A1126-306)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2023-11-13 07:47 | 2023-11-13 08:47 | 2023-11-14 08:47 | 24 | 2023-11-13 07:55 | 2023-11-13 10:55 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 119320 | 87807 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2024-12772539 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | FILTER DIRTY -AIR HANDLING UNIT 132 (TAG NO:AHU-A1126-306-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2024-03-28 08:00 | 2024-03-28 09:00 | 2024-03-29 09:00 | 24 | 2024-03-28 08:05 | 2024-03-28 11:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10132806 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE AHU-A1126-306 |  | FM008 |  | 2022-02-13 08:45 | 2022-02-13 09:45 | 2022-02-14 09:45 | 24 | 2022-02-13 08:50 | 2022-02-13 10:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10709039 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU-A1126-306 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-05-31 13:47 | 2022-05-31 14:47 | 2022-06-01 14:47 | 24 | 2022-05-31 13:57 | 2022-05-31 16:10 | 133 | 266 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11606085 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, AHU-A1126-306 ,C3-02-03 |  | FM008 |  | 2023-03-28 19:27 | 2023-03-28 20:27 | 2023-03-29 20:27 | 24 | 2023-03-28 19:35 | 2023-03-28 22:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12232848 | ASD-COC-TFL002-AHU132 | AIR HANDLING UNIT-05 | AHU-A1126-306 FILTER DIRTY C3-02-03 |  | FM008 |  | 2023-09-30 12:56 | 2023-09-30 13:56 | 2023-10-01 13:56 | 24 | 2023-09-30 13:05 | 2023-09-30 15:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10124853 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | AHU-A1126-307-DUCT INSULATION DAMAGED |  | FM008 |  | 2022-02-12 09:31 | 2022-02-12 10:31 | 2022-02-13 10:31 | 24 | 2022-02-12 09:40 | 2022-02-12 12:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-11232646 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | AHU-A1126-307- CABIN LIGHT IS NOT ILLUMINATING-- |  | FM008 |  | 2022-11-30 19:18 | 2022-11-30 20:18 | 2022-12-01 20:18 | 24 | 2022-11-30 19:30 | 2022-11-30 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 94953 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11396201 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-307 C3-02-01 |  | FM008 |  | 2023-01-22 19:05 | 2023-01-22 20:05 | 2023-01-23 20:05 | 24 | 2023-01-22 19:10 | 2023-01-22 22:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 133396 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11999985 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C3-02-01 |  | FM008 |  | 2023-07-23 07:09 | 2023-07-23 08:09 | 2023-07-24 08:09 | 24 | 2023-07-23 07:15 | 2023-07-23 09:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12090238 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-307 C3-02-01 |  | FM008 |  | 2023-08-16 22:33 | 2023-08-16 23:33 | 2023-08-17 23:33 | 24 | 2023-08-16 22:40 | 2023-08-17 00:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17573 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2023-12281934 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-307 – C3-02-01 |  | FM008 |  | 2023-10-13 20:06 | 2023-10-13 21:06 | 2023-10-14 21:06 | 24 | 2023-10-13 20:15 | 2023-10-13 23:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-10874352 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – C3-02-01 |  | FM008 |  | 2022-07-28 07:30 | 2022-07-28 08:30 | 2022-07-29 08:30 | 24 | 2022-07-28 07:35 | 2022-07-28 11:55 | 260 | 115 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11362677 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 133 (TAG NO:AHU-A1126-307)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 002 DUCT INSULATION DAMAGED C3-02-01 |  | FM008 |  | 2023-01-12 08:18 | 2023-01-12 09:18 | 2023-01-13 09:18 | 24 | 2023-01-12 08:29 | 2023-01-12 12:15 | 226 | 678 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 89127 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12273820 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH BROKEN - C3-02-01 |  | FM008 |  | 2023-10-09 16:21 | 2023-10-09 17:21 | 2023-10-10 17:21 | 24 | 2023-10-09 16:30 | 2023-10-09 18:35 | 125 | 250 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 87807 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2024-12714146 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-307 – C3-02-01 |  | FM008 |  | 2024-03-10 07:24 | 2024-03-10 08:24 | 2024-03-11 08:24 | 24 | 2024-03-10 07:30 | 2024-03-10 10:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12732123 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | AHU-A1126-307 DUCT INSULATION DAMAGED- C3-02-01 |  | FM008 |  | 2024-03-15 07:05 | 2024-03-15 08:05 | 2024-03-16 08:05 | 24 | 2024-03-15 07:10 | 2024-03-15 10:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 87807 |  |  | FM11109 | Jeyaraj Bensigar Franklin, Mr. | N - - - |  | Voice Communication
| CM-2023-12321940 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-10-25 20:58 | 2023-10-25 21:58 | 2023-10-26 21:58 | 24 | 2023-10-25 21:05 | 2023-10-26 01:30 | 265 | 269 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12508139 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-28 11:09 | 2023-12-28 12:09 | 2023-12-29 12:09 | 24 | 2023-12-28 11:10 | 2023-12-28 17:30 | 380 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-10044455 | ASD-COC-TFL002-AHU133 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE (TAG NO:AHU-A1126-307 |  | FM008 |  | 2022-01-12 20:26 | 2022-01-12 21:26 | 2022-01-13 21:26 | 24 | 2022-01-12 20:30 | 2022-01-12 22:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106972 | 55709 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10154782 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1126-308 – C3-02-03 |  | FM008 |  | 2022-02-23 00:46 | 2022-02-23 01:46 | 2022-02-24 01:46 | 24 | 2022-02-23 00:55 | 2022-02-23 02:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10709390 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-06-02 20:33 | 2022-06-02 21:33 | 2022-06-03 21:33 | 24 | 2022-06-02 20:40 | 2022-06-03 00:55 | 255 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10825947 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED AHU-A1126-308 |  | FM008 |  | 2022-07-09 13:00 | 2022-07-09 14:00 | 2022-07-10 14:00 | 24 | 2022-07-09 13:10 | 2022-07-09 15:40 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 95217 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10886005 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1126-308 – C3-03-02 |  | FM008 |  | 2022-07-29 15:21 | 2022-07-29 16:21 | 2022-07-30 16:21 | 24 | 2022-07-29 15:31 | 2022-07-29 16:15 | 44 | 88 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11178467 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308 – CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-11-10 19:22 | 2022-11-10 20:22 | 2022-11-11 20:22 | 24 | 2022-11-10 19:30 | 2022-11-10 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11611634 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-03-31 07:10 | 2023-03-31 08:10 | 2023-04-01 08:10 | 24 | 2023-03-31 07:15 | 2023-03-31 10:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-11402970 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-02-03 |  | FM008 |  | 2023-01-23 19:01 | 2023-01-23 20:01 | 2023-01-24 20:01 | 24 | 2023-01-23 19:05 | 2023-01-23 21:20 | 135 | 405 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11483815 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | SUPPLY BLOWER NOISY , AHU-A1126-308 |  | FM008 |  | 2023-02-24 08:42 | 2023-02-24 09:42 | 2023-02-25 09:42 | 24 | 2023-02-24 08:50 | 2023-02-24 18:05 | 555 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-12141933 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308 – DUCT INSULATION IS DAMAGED – C3-02-03 |  | FM008 |  | 2023-09-02 15:38 | 2023-09-02 16:38 | 2023-09-03 16:38 | 24 | 2023-09-02 15:45 | 2023-09-02 18:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12512940 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-12-27 21:13 | 2023-12-27 22:13 | 2023-12-28 22:13 | 24 | 2023-12-27 21:20 | 2023-12-28 00:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2022-11163876 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | FILTER DIRTY – C3-03-02 |  | FM008 |  | 2022-11-06 19:30 | 2022-11-06 20:30 | 2022-11-07 20:30 | 24 | 2022-11-06 19:35 | 2022-11-06 21:20 | 105 | 315 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11362678 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308- DUCT INSULATION DAMAGED - C3-02-03 |  | FM008 |  | 2023-01-12 08:20 | 2023-01-12 09:20 | 2023-01-13 09:20 | 24 | 2023-01-12 08:30 | 2023-01-12 12:10 | 220 | 660 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 89127 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12422513 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-28 22:47 | 2023-11-28 23:47 | 2023-11-29 23:47 | 24 | 2023-11-28 22:55 | 2023-11-29 00:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12633267 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-308 |  | FM008 |  | 2024-02-07 20:02 | 2024-02-07 21:02 | 2024-02-08 21:02 | 24 | 2024-02-07 20:05 | 2024-02-07 23:00 | 175 | 525 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-12321938 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | AHU-A1126-308 FILTER DIRTY -T3-02-03 |  | FM008 |  | 2023-10-25 20:56 | 2023-10-25 21:56 | 2023-10-26 21:56 | 24 | 2023-10-25 21:05 | 2023-10-25 22:30 | 85 | 255 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10031511 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-06 16:11 | 2022-01-06 17:11 | 2022-01-07 17:11 | 24 | 2022-01-06 16:20 | 2022-01-06 17:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 68485 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10279391 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | RETURN DUCT ACCESS DOOR AIR LEAKAGE AHU-A1126-308 C3-02-03 |  | FM008 |  | 2022-03-25 16:30 | 2022-03-25 17:30 | 2022-03-26 17:30 | 24 | 2022-03-25 16:35 | 2022-03-25 18:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 85125 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11354218 | ASD-COC-TFL002-AHU134 | AIR HANDLING UNIT-05 | ACESS DOOR AIR LEAKAGE – C3-02-03 - AHU-A1126-308 |  | FM008 |  | 2023-01-07 02:12 | 2023-01-07 03:12 | 2023-01-08 03:12 | 24 | 2023-01-07 02:20 | 2023-01-07 04:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94954 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-10831796 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AHU-A1126-351-DP1 FILTER ALARM |  | FM008 |  | 2022-07-14 06:59 | 2022-07-14 07:59 | 2022-07-15 07:59 | 24 | 2022-07-14 07:05 | 2022-07-14 09:30 | 145 | 275 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12035035 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED T3-02-01 |  | FM008 |  | 2023-07-30 22:01 | 2023-07-30 23:01 | 2023-07-31 23:01 | 24 | 2023-07-30 22:05 | 2023-07-31 01:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12510434 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AHU-A1126-351 FILTER DIRTY - AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2023-12-26 12:32 | 2023-12-26 13:32 | 2023-12-27 13:32 | 24 | 2023-12-26 12:40 | 2023-12-26 14:30 | 110 | 119 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 87807 |  |  | FM12771 | Philip, Mr. Anthony Felix | N - - - |  | Voice Communication
| CM-2024-12831563 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AC NOISY -GATE C2 -ARRIVAL |  | FM008 |  | 2024-04-18 15:06 | 2024-04-18 16:06 | 2024-04-19 16:06 | 24 | 2024-04-18 15:15 | 2024-04-18 17:45 | 150 | 65 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | T28771 | Shumail, Mr. Lubaib | N - - - |  | Voice Communication
| CM-2022-11248884 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -C3-02-01 |  | FM008 |  | 2022-12-05 06:58 | 2022-12-05 07:58 | 2022-12-06 07:58 | 24 | 2022-12-05 07:05 | 2022-12-05 08:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11342163 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING |  | FM008 |  | 2023-01-02 14:22 | 2023-01-02 15:22 | 2023-01-03 15:22 | 24 | 2023-01-02 14:25 | 2023-01-02 17:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95216 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12216559 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AHU-A1126-351 – C3-02-01 – AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-09-24 11:15 | 2023-09-24 12:15 | 2023-09-25 12:15 | 24 | 2023-09-24 11:25 | 2023-09-24 13:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94954 | 87807 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-12414009 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-351) |  | FM008 |  | 2023-11-26 13:10 | 2023-11-26 14:10 | 2023-11-27 14:10 | 24 | 2023-11-26 13:15 | 2023-11-26 14:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2022-11255735 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AHU-A1126-351 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-12-09 07:16 | 2022-12-09 08:16 | 2022-12-10 08:16 | 24 | 2022-12-09 07:20 | 2022-12-09 11:00 | 220 | 660 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12732124 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | AHU-A1126-351 DUCT INSULATION DAMAGED - AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2024-03-15 07:09 | 2024-03-15 08:09 | 2024-03-16 08:09 | 24 | 2024-03-15 07:10 | 2024-03-15 13:15 | 365 | 545 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 87807 |  |  | FM11109 | Jeyaraj Bensigar Franklin, Mr. | N - - - |  | E-mail
| CM-2023-12319727 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - AHU-A1126-351 – C3-02-01 |  | FM008 |  | 2023-10-24 07:07 | 2023-10-24 08:07 | 2023-10-25 08:07 | 24 | 2023-10-24 07:15 | 2023-10-24 18:40 | 685 | 305 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12591766 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-02-01 |  | FM008 |  | 2024-01-23 19:26 | 2024-01-23 20:26 | 2024-01-24 20:26 | 24 | 2024-01-23 19:30 | 2024-01-23 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 95217 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11447512 | ASD-COC-TFL002-AHU156 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED--AHU-A1126-351)--CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2023-02-11 21:02 | 2023-02-11 22:02 | 2023-02-12 22:02 | 24 | 2023-02-11 21:10 | 2023-02-12 00:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10080392 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | AHU-A1126-352 -C3-02-03 CHILLED WATERLINE PAINT FADED |  | FM008 |  | 2022-01-26 12:22 | 2022-01-26 13:22 | 2022-01-27 13:22 | 24 | 2022-01-26 12:30 | 2022-01-26 16:35 | 245 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 87807 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10792819 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-352 – C3-03-02 |  | FM008 |  | 2022-06-30 07:02 | 2022-06-30 08:02 | 2022-07-01 08:02 | 24 | 2022-06-30 07:11 | 2022-06-30 08:39 | 88 | 264 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11266431 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | FAHU SUPPLY AIR DUCT INSULATION DAMAGED, SUPPLY AIR LEAK FROM THE EDGES OF ACTUATOR - C3 06 01 MECHANICAL ROOM IN CONCOURSE-C |  | FM008 |  | 2022-12-11 15:08 | 2022-12-11 16:08 | 2022-12-12 16:08 | 24 | 2022-12-11 15:20 | 2022-12-11 18:35 | 195 | 65 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2023-11365472 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE AHU-A1126-352 C3-02-03 |  | FM008 |  | 2023-01-13 22:19 | 2023-01-13 23:19 | 2023-01-14 23:19 | 24 | 2023-01-13 22:30 | 2023-01-14 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 55709 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-12050623 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | C3-02-03-DUCT INSUALTION DAMAGED -AIR HANDLING UNIT 157 (TAG NO:AHU-A1126-352)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 002 |  | FM008 |  | 2023-08-05 22:56 | 2023-08-05 23:56 | 2023-08-06 23:56 | 24 | 2023-08-05 23:00 | 2023-08-06 01:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-11183102 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C3-02-03 |  | FM008 |  | 2022-11-12 19:27 | 2022-11-12 20:27 | 2022-11-13 20:27 | 24 | 2022-11-12 19:35 | 2022-11-12 23:45 | 250 | 245 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12111463 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-08-22 07:37 | 2023-08-22 08:37 | 2023-08-23 08:37 | 24 | 2023-08-22 07:45 | 2023-08-22 09:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11301680 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-12-25 08:21 | 2022-12-25 09:21 | 2022-12-26 09:21 | 24 | 2022-12-25 08:30 | 2022-12-25 11:35 | 185 | 555 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12088704 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.3FLRP4.CONC2032.AHU352.SYSALM.DP1 / -MECHANICAL ROOM C3-03-02 |  | FM008 |  | 2023-08-14 13:54 | 2023-08-14 14:54 | 2023-08-15 14:54 | 24 | 2023-08-14 13:55 | 2023-08-14 16:20 | 145 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12511623 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | AHU-A1126-352 AHU CABIN LIGHTING SWITCH FAULTY C3-02-03 |  | FM008 |  | 2023-12-28 07:38 | 2023-12-28 08:38 | 2023-12-29 08:38 | 24 | 2023-12-28 07:45 | 2023-12-28 10:30 | 165 | 330 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2024-12730812 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2024-03-14 12:07 | 2024-03-14 13:07 | 2024-03-15 13:07 | 24 | 2024-03-14 12:15 | 2024-03-14 18:20 | 365 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 87807 |  |  | FM12771 | Philip, Mr. Anthony Felix | N - - - |  | Voice Communication
| CM-2023-12159193 | ASD-COC-TFL002-AHU157 | AIR HANDLING UNIT-05 | AHU ACTUATOR FUALTY C3-02-03 |  | FM008 |  | 2023-09-08 18:59 | 2023-09-08 19:59 | 2023-09-09 19:59 | 24 | 2023-09-08 19:10 | 2023-09-09 | 290 | 343 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 002 | N | DAMAGED | ATUACTOR DAMAGE | REPLACED THE COIL | 106972 | 17053 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2022-10188425 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - C3-03-01 |  | FM008 |  | 2022-02-25 22:34 | 2022-02-25 23:34 | 2022-02-26 23:34 | 24 | 2022-02-25 22:40 | 2022-02-26 00:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-11156727 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING AHU-A1126-309 |  | FM008 |  | 2022-11-02 10:40 | 2022-11-02 11:40 | 2022-11-03 11:40 | 24 | 2022-11-02 10:45 | 2022-11-02 12:13 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11994170 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AHU-A1126-309)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 003 |  | FM008 |  | 2023-07-19 07:54 | 2023-07-19 08:54 | 2023-07-20 08:54 | 24 | 2023-07-19 08:00 | 2023-07-19 14:02 | 362 | 545 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12040927 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - |  | FM008 |  | 2023-08-02 11:25 | 2023-08-02 12:25 | 2023-08-03 12:25 | 24 | 2023-08-02 11:30 | 2023-08-02 13:59 | 149 | 298 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 17053 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-12041813 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -C3-03-01 |  | FM008 |  | 2023-08-03 19:11 | 2023-08-03 20:11 | 2023-08-04 20:11 | 24 | 2023-08-03 19:15 | 2023-08-03 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11008056 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | chilled Water leakage from isolation valve and insulation damage. C3 03 01 Mechanical Room in Concourse-C |  | FM008 |  | 2022-09-11 09:12 | 2022-09-11 10:12 | 2022-09-12 10:12 | 24 | 2022-09-11 09:20 | 2022-09-11 18:35 | 555 | 65 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 106972 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2023-12338945 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - C3-03-01 |  | FM008 |  | 2023-10-31 02:25 | 2023-10-31 03:25 | 2023-11-01 03:25 | 24 | 2023-10-31 02:30 | 2023-10-31 05:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 87807 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2022-10202528 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | INSULATION DAMAGE AHU-A1126-309 C3-05-01 |  | FM008 |  | 2022-03-01 14:29 | 2022-03-01 15:29 | 2022-03-02 15:29 | 24 | 2022-03-01 14:35 | 2022-03-01 17:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 87807 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10045667 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | AHU-A1126-309 – CHILLED WATER LINE PAINT FADED-- |  | FM008 |  | 2022-01-15 14:39 | 2022-01-15 15:39 | 2022-01-16 15:39 | 24 | 2022-01-15 14:45 | 2022-01-15 16:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 55709 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2022-10841798 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | AHU-A1126-309 – DUCT INSULATION DAMAGED- |  | FM008 |  | 2022-07-15 13:05 | 2022-07-15 14:05 | 2022-07-16 14:05 | 24 | 2022-07-15 13:10 | 2022-07-15 15:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 95217 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10902537 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | AHU-A1126-309-FILTER ALARM |  | FM008 |  | 2022-08-01 01:04 | 2022-08-01 02:04 | 2022-08-02 02:04 | 24 | 2022-08-01 01:05 | 2022-08-01 02:15 | 70 | 125 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95217 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11399326 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C3-03-01 |  | FM008 |  | 2023-01-23 21:25 | 2023-01-23 22:25 | 2023-01-24 22:25 | 24 | 2023-01-23 21:30 | 2023-01-23 23:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-11960380 | ASD-COC-TFL003-AHU135 | AIR HANDLING UNIT-05 | 02 ACCESS DOORS ON SUPPLY AIR DUCT NOT CLOSED PROPERLY AND CORNERS HAVING DUCT OPENINGS, DOOR TO BE CLEANED PROPERLY - FA-AHU-A1126-309 - C0-03-01 MECHANICAL |  | FM008 |  | 2023-07-09 08:29 | 2023-07-09 09:29 | 2023-07-10 09:29 | 24 | 2023-07-09 08:35 | 2023-07-09 10:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | 118925 | Datla, Mr. Anil Varma | N - - - |  | E-mail
| CM-2023-11998755 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 136 -DUCT INSULATION DAMAGE -C3-03-03 |  | FM008 |  | 2023-07-23 08:10 | 2023-07-23 09:10 | 2023-07-24 09:10 | 24 | 2023-07-23 08:15 | 2023-07-23 13:00 | 285 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12423597 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED,AHU-A1126-310,C3-03-03 |  | FM008 |  | 2023-11-30 07:25 | 2023-11-30 08:25 | 2023-12-01 08:25 | 24 | 2023-11-30 07:30 | 2023-11-30 17:00 | 570 | 545 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11160131 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING -AHU-A1126-310 - C3-03-03 |  | FM008 |  | 2022-11-03 14:15 | 2022-11-03 15:15 | 2022-11-04 15:15 | 24 | 2022-11-03 14:21 | 2022-11-03 16:49 | 148 | 181 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11176198 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-09 00:03 | 2022-11-09 01:03 | 2022-11-10 01:03 | 24 | 2022-11-09 00:10 | 2022-11-09 04:10 | 240 | 370 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11181358 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | AHU-A1126-310 -CHILLER LINE PAINT FADED – C3-03-03 |  | FM008 |  | 2022-11-12 00:06 | 2022-11-12 01:06 | 2022-11-13 01:06 | 24 | 2022-11-12 00:10 | 2022-11-12 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12252455 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | AHU-A1126-310 FILTER DIRTY |  | FM008 |  | 2023-10-03 19:13 | 2023-10-03 20:13 | 2023-10-04 20:13 | 24 | 2023-10-03 19:20 | 2023-10-03 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12730810 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2024-03-14 12:05 | 2024-03-14 13:05 | 2024-03-15 13:05 | 24 | 2024-03-14 12:10 | 2024-03-14 15:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 87807 |  |  | FM12771 | Philip, Mr. Anthony Felix | N - - - |  | Voice Communication
| CM-2023-12346646 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE ISSUE - AHU-A1126-310 - C0-03-03 |  | FM008 |  | 2023-11-03 08:43 | 2023-11-03 09:43 | 2023-11-04 09:43 | 24 | 2023-11-03 08:45 | 2023-11-03 11:30 | 165 | 330 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 133396 | 17053 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-10037052 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | AHU-A1126-310- CHILLED WATER LINE PAINT FADED – C3-03-03 |  | FM008 |  | 2022-01-09 14:36 | 2022-01-09 15:36 | 2022-01-10 15:36 | 24 | 2022-01-09 14:45 | 2022-01-09 17:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 17154 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10223554 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY -C3-03-03 |  | FM008 |  | 2022-03-07 09:45 | 2022-03-07 10:45 | 2022-03-08 10:45 | 24 | 2022-03-07 09:50 | 2022-03-07 11:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10902538 | ASD-COC-TFL003-AHU136 | AIR HANDLING UNIT-05 | AHU-A1126-310- FILTER ALARM |  | FM008 |  | 2022-08-01 01:05 | 2022-08-01 02:05 | 2022-08-02 02:05 | 24 | 2022-08-01 01:10 | 2022-08-01 03:20 | 130 | 125 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11101588 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | AHU-A1126-311 DP3 FILTER ALARM C3-03-01 |  | FM008 |  | 2022-10-14 08:40 | 2022-10-14 09:40 | 2022-10-15 09:40 | 24 | 2022-10-14 08:50 | 2022-10-14 10:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11345573 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED AHU-A1126-311 - C3-03-01 |  | FM008 |  | 2023-01-05 19:08 | 2023-01-05 20:08 | 2023-01-06 20:08 | 24 | 2023-01-05 19:15 | 2023-01-05 23:15 | 240 | 480 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11157768 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED - AHU-A1126-311 – C3-03-01 |  | FM008 |  | 2022-11-02 22:18 | 2022-11-02 23:18 | 2022-11-03 23:18 | 24 | 2022-11-02 22:25 | 2022-11-03 00:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11194608 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-03-01 |  | FM008 |  | 2022-11-18 00:08 | 2022-11-18 01:08 | 2022-11-19 01:08 | 24 | 2022-11-18 00:15 | 2022-11-18 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11216028 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | MARINA LIGHT NOT ILLUMINATING - AHU-A1126-311 – C3-03-01 |  | FM008 |  | 2022-11-26 19:10 | 2022-11-26 20:11 | 2022-11-27 20:11 | 24 | 2022-11-26 19:15 | 2022-11-26 21:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11008055 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | chilled Water leakage from DRV valve and insulation damage. C3 03 01 Mechanical Room in Concourse-C |  | FM008 |  | 2022-09-11 09:09 | 2022-09-11 10:09 | 2022-09-12 10:09 | 24 | 2022-09-11 09:19 | 2022-09-11 18:00 | 521 | 65 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 106972 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2023-11934534 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | AHU-A1126-311 AHU HEATER FLEXIBLE CONNECTOR DAMAGED C3-03-01 |  | FM008 |  | 2023-06-29 02:40 | 2023-06-29 03:40 | 2023-06-30 03:40 | 24 | 2023-06-29 02:45 | 2023-06-29 05:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 89127 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12321939 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | AHU-A1126-311 FILTER DIRTY C3-03-01 |  | FM008 |  | 2023-10-25 20:58 | 2023-10-25 21:58 | 2023-10-26 21:58 | 24 | 2023-10-25 21:05 | 2023-10-25 23:55 | 170 | 245 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10049539 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGE AHU-A1126-311 C3-03-01 |  | FM008 |  | 2022-01-15 19:10 | 2022-01-15 20:10 | 2022-01-16 20:10 | 24 | 2022-01-15 19:15 | 2022-01-15 21:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 85125 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10888038 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | FILTER DIRTY – C3-03-01 |  | FM008 |  | 2022-07-30 13:17 | 2022-07-30 14:17 | 2022-07-31 14:17 | 24 | 2022-07-30 13:25 | 2022-07-30 15:40 | 135 | 95 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11936850 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | PRE FILTER DIRTY-AIR HANDLING UNIT 137 (TAG NO:AHU-A1126-311)- |  | FM008 |  | 2023-07-02 08:38 | 2023-07-02 09:38 | 2023-07-03 09:38 | 24 | 2023-07-02 08:45 | 2023-07-02 15:00 | 375 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12166464 | ASD-COC-TFL003-AHU137 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1126-311 |  | FM008 |  | 2023-09-09 19:27 | 2023-09-09 20:27 | 2023-09-10 20:27 | 24 | 2023-09-09 19:35 | 2023-09-09 22:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106972 | 17053 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2022-10142530 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | AHU-A1126-312 INSULATION DAMAGED C3-03-03 |  | FM008 |  | 2022-02-16 08:27 | 2022-02-16 09:27 | 2022-02-17 09:27 | 24 | 2022-02-16 08:35 | 2022-02-16 16:30 | 475 | 305 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2023-11345574 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED AHU-A1126-312 C3-03-03 |  | FM008 |  | 2023-01-05 19:09 | 2023-01-05 20:09 | 2023-01-06 20:09 | 24 | 2023-01-05 19:15 | 2023-01-05 23:15 | 240 | 480 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-11767360 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | AHU-A1126-312– DUCT INSULATION DAMAGED- - |  | FM008 |  | 2023-05-07 10:11 | 2023-05-07 11:11 | 2023-05-08 11:11 | 24 | 2023-05-07 10:15 | 2023-05-07 13:10 | 175 | 350 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12383710 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | AHU-A1126-312DUCT INSULATION DAMAGED – C3-03-03 |  | FM008 |  | 2023-11-15 07:34 | 2023-11-15 08:34 | 2023-11-16 08:34 | 24 | 2023-11-15 07:40 | 2023-11-15 10:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 87807 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2024-12553646 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | WATER LEAKING FROM CEILING - OUTSIDE CORRIODR C2-03-18 |  | FM008 |  | 2024-01-10 15:25 | 2024-01-10 16:25 | 2024-01-11 16:25 | 24 | 2024-01-10 15:30 | 2024-01-10 16:15 | 45 | 90 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 119320 | 17053 |  |  | FM13090 | Kamau, Ms. Caroline Mugure | N - - - |  | E-mail
| CM-2022-11178101 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C3-03-03 |  | FM008 |  | 2022-11-12 19:26 | 2022-11-12 20:26 | 2022-11-13 20:26 | 24 | 2022-11-12 19:35 | 2022-11-12 21:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11385212 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-01-18 19:16 | 2023-01-18 20:16 | 2023-01-19 20:16 | 24 | 2023-01-18 19:20 | 2023-01-18 21:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM5430 | Subbiah, Mr. Lakshmanan | N - - - |  | Voice Communication
| CM-2023-11827449 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FAULTY -AIR HANDLING UNIT 138 (TAG NO:AHU-A1126-312) |  | FM008 |  | 2023-05-27 00:15 | 2023-05-27 01:15 | 2023-05-28 01:15 | 24 | 2023-05-27 00:20 | 2023-05-27 02:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12671811 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-312 c3-03-03 |  | FM008 |  | 2024-02-22 21:21 | 2024-02-22 22:21 | 2024-02-23 22:21 | 24 | 2024-02-22 21:25 | 2024-02-22 23:55 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2022-10282428 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | AHU-A1126-312 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-26 14:28 | 2022-03-26 15:28 | 2022-03-27 15:28 | 24 | 2022-03-26 14:35 | 2022-03-26 16:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10048840 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-01-15 21:26 | 2022-01-15 22:26 | 2022-01-16 22:26 | 24 | 2022-01-15 21:30 | 2022-01-15 23:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10044217 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | AHU-A1126-312 – CHILLER WATER LINE PAINT FADED – C3-03-03 |  | FM008 |  | 2022-01-11 12:26 | 2022-01-11 13:26 | 2022-01-12 13:26 | 24 | 2022-01-11 12:35 | 2022-01-11 15:40 | 185 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 105233 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10888041 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | FILTER DIRTY – C3-03-03 |  | FM008 |  | 2022-07-30 13:19 | 2022-07-30 14:19 | 2022-07-31 14:19 | 24 | 2022-07-30 13:25 | 2022-07-30 14:50 | 85 | 95 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12166466 | ASD-COC-TFL003-AHU138 | AIR HANDLING UNIT-05 | DUCT INSULATION DMAAGED AHU-A1126-312 |  | FM008 |  | 2023-09-09 19:29 | 2023-09-09 20:29 | 2023-09-10 20:29 | 24 | 2023-09-09 19:35 | 2023-09-09 22:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM11844 | Senthur Pandian, Mr. Selvaraj | N - - - |  | Voice Communication
| CM-2022-11226309 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | AHU-A1126-353 CABIN LIGHT NOT WORKING – C3-03-01 |  | FM008 |  | 2022-11-27 19:06 | 2022-11-27 20:06 | 2022-11-28 20:06 | 24 | 2022-11-27 19:15 | 2022-11-27 21:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11935595 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | BAG FILTER DIRTY-AIR HANDLING UNIT 158 (TAG NO:AHU-A1126-353) |  | FM008 |  | 2023-07-02 08:36 | 2023-07-02 09:36 | 2023-07-03 09:36 | 24 | 2023-07-02 08:40 | 2023-07-02 12:05 | 205 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 17053 |  |  | FM11905 | Virender Pal Singh, Mr. Ritish Jarial | N - - - |  | Voice Communication
| CM-2023-12040688 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | C3-03-01-AHU CABIN LAMP FAULTY-AIR HANDLING UNIT 158 (TAG NO:AHU-A1126-353)- |  | FM008 |  | 2023-08-01 15:27 | 2023-08-01 16:27 | 2023-08-02 16:27 | 24 | 2023-08-01 15:35 | 2023-08-01 18:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17336 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12016141 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE AHU-A1126-353 |  | FM008 |  | 2023-07-28 07:05 | 2023-07-28 08:05 | 2023-07-29 08:05 | 24 | 2023-07-28 07:10 | 2023-07-28 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | DOOR HINGES LOOSE/DAMAGED | REPAIRED/REPLACED | 106972 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2023-12040487 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | AHU-A1126-353 FILTER DIRTY |  | FM008 |  | 2023-07-31 19:38 | 2023-07-31 20:38 | 2023-08-01 20:38 | 24 | 2023-07-31 19:45 | 2023-07-31 22:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11008053 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | supply air duct access door damage, Supply air leak from the edges of door and creating condensation upon the door frame area C3 03 01 Mechanical Room in Concourse-C |  | FM008 |  | 2022-09-11 09:08 | 2022-09-11 10:08 | 2022-09-12 10:08 | 24 | 2022-09-11 09:18 | 2022-09-11 17:25 | 487 | 165 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 106972 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2023-11779307 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE – C3 01 01 |  | FM008 |  | 2023-05-09 08:31 | 2023-05-09 09:31 | 2023-05-10 09:31 | 24 | 2023-05-09 08:35 | 2023-05-09 14:45 | 370 | 455 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 106972 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12344241 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY- AREA 3 -ROOM 1 MECHANICAL ROOM -AIR HANDLING UNIT 158 (TAG NO:AHU-A1126-353) |  | FM008 |  | 2023-11-02 19:36 | 2023-11-02 20:36 | 2023-11-03 20:36 | 24 | 2023-11-02 19:42 | 2023-11-03 01:45 | 363 | 248 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17336 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-10202503 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | AHU INSULATION DAMAGED – C3-03-01 |  | FM008 |  | 2022-03-01 11:42 | 2022-03-01 12:42 | 2022-03-02 12:42 | 24 | 2022-03-01 11:50 | 2022-03-01 14:20 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106976 | 87807 |  |  | FM5803 | Tiwari, Mr. Sanjeed Kumar | N - - - |  | Voice Communication
| CM-2022-10045632 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | AHU-A1126-353 – CHILLED WATER LINE PAINT FADED - C3-03-01 |  | FM008 |  | 2022-01-15 12:28 | 2022-01-15 13:28 | 2022-01-16 13:28 | 24 | 2022-01-15 12:35 | 2022-01-15 14:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | UNIT IS RUSTED | CLEANED & REPAINT THE UNIT | 94953 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2024-12745636 | ASD-COC-TFL003-AHU158 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-03-01 |  | FM008 |  | 2024-03-20 07:03 | 2024-03-20 08:03 | 2024-03-21 08:03 | 24 | 2024-03-20 07:05 | 2024-03-20 13:05 | 360 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10141269 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | AHU-A1126-354 SUPPLY DUCT INSULATION DAMAGED C3-03-03 |  | FM008 |  | 2022-02-15 07:42 | 2022-02-15 08:42 | 2022-02-16 08:42 | 24 | 2022-02-15 07:50 | 2022-02-15 13:55 | 365 | 730 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM7717 | Gamini Rajaguru R W Herath Mudiyanselage Giddawa Gedara, | N - - - |  | Voice Communication
| CM-2023-11365473 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE AHU-A1126-354, C3-03-03 |  | FM008 |  | 2023-01-13 22:24 | 2023-01-13 23:24 | 2023-01-14 23:24 | 24 | 2023-01-13 22:30 | 2023-01-14 01:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 55709 |  |  | FM11739 | Ranjith Kumar Kalyanasundaram, Mr. | N - - - |  | Voice Communication
| CM-2023-12042324 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-354 – C3 03 03 |  | FM008 |  | 2023-08-03 11:36 | 2023-08-03 12:36 | 2023-08-04 12:36 | 24 | 2023-08-03 11:40 | 2023-08-03 13:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-12084415 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-03-03 |  | FM008 |  | 2023-08-14 00:51 | 2023-08-14 01:51 | 2023-08-15 01:51 | 24 | 2023-08-14 01:00 | 2023-08-14 03:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12342408 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGE: - AIR HANDLING UNIT 159 (TAG NO:AHU-A1126-354)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 003 |  | FM008 |  | 2023-11-01 16:18 | 2023-11-01 17:18 | 2023-11-02 17:18 | 24 | 2023-11-01 16:27 | 2023-11-01 18:25 | 118 | 236 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 138627 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-11759754 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT ILLUMINATING |  | FM008 |  | 2023-05-01 16:14 | 2023-05-01 17:14 | 2023-05-02 17:14 | 24 | 2023-05-01 16:23 | 2023-05-01 17:52 | 89 | 178 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 121959 | 17053 |  |  | FM7853 | Guilles, Mr. Ronel Balid | N - - - |  | Voice Communication
| CM-2023-12229099 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-09-27 09:31 | 2023-09-27 10:31 | 2023-09-28 10:31 | 24 | 2023-09-27 09:40 | 2023-09-27 12:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11179948 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED -C3-03-03 |  | FM008 |  | 2022-11-13 00:03 | 2022-11-13 01:03 | 2022-11-14 01:03 | 24 | 2022-11-13 00:10 | 2022-11-13 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-10223552 | ASD-COC-TFL003-AHU159 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY -C3-03-03 |  | FM008 |  | 2022-03-07 09:43 | 2022-03-07 10:43 | 2022-03-08 10:43 | 24 | 2022-03-07 09:50 | 2022-03-07 11:50 | 120 | 225 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 003 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-11060463 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS -C3-04-01 |  | FM008 |  | 2022-09-26 18:36 | 2022-09-26 19:36 | 2022-09-27 19:36 | 24 | 2022-09-26 18:45 | 2022-09-26 21:25 | 160 | 100 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | BMS
| CM-2022-11196434 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | AHU-A1126-313- DUCT INSULATION DAMAGED – C3-04-01 |  | FM008 |  | 2022-11-18 19:20 | 2022-11-18 20:20 | 2022-11-19 20:20 | 24 | 2022-11-18 19:30 | 2022-11-18 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12018236 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | LIGHTING SWITCH FAULTY |  | FM008 |  | 2023-07-29 19:29 | 2023-07-29 20:29 | 2023-07-30 20:29 | 24 | 2023-07-29 19:35 | 2023-07-30 01:10 | 335 | 365 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95216 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12141663 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1126-313, C3-04-01 |  | FM008 |  | 2023-09-02 09:21 | 2023-09-02 10:21 | 2023-09-03 10:21 | 24 | 2023-09-02 09:30 | 2023-09-02 17:30 | 480 | 250 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 87807 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12507466 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-12-25 19:34 | 2023-12-25 20:34 | 2023-12-26 20:34 | 24 | 2023-12-25 19:40 | 2023-12-25 22:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2024-12609281 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED ,AHU-A1126-313, C3-04-01 |  | FM008 |  | 2024-01-29 19:16 | 2024-01-29 20:16 | 2024-01-30 20:16 | 24 | 2024-01-29 19:25 | 2024-01-29 21:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10887263 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | AHU-A1126-313 – FILTER ALARM – C3-04-01- |  | FM008 |  | 2022-07-31 17:07 | 2022-07-31 18:07 | 2022-08-01 18:07 | 24 | 2022-07-31 17:10 | 2022-07-31 19:50 | 160 | 95 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11218942 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT ILLUMINATING - AHU-A1126-313 – C3-04-01 |  | FM008 |  | 2022-11-27 00:12 | 2022-11-27 01:12 | 2022-11-28 01:12 | 24 | 2022-11-27 00:20 | 2022-11-27 03:00 | 160 | 320 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12229619 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-29 09:44 | 2023-09-29 10:44 | 2023-09-30 10:44 | 24 | 2023-09-29 09:50 | 2023-09-29 12:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12346660 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY – T3-04-01 |  | FM008 |  | 2023-11-03 09:54 | 2023-11-03 10:54 | 2023-11-04 10:54 | 24 | 2023-11-03 10:04 | 2023-11-03 12:04 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12510604 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-12-26 23:37 | 2023-12-27 00:37 | 2023-12-28 00:37 | 24 | 2023-12-26 23:45 | 2023-12-27 02:00 | 135 | 540 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-10157830 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | AHU139 DUCT INSULATION DAMAGED – C3-04-01 |  | FM008 |  | 2022-02-22 12:16 | 2022-02-22 13:16 | 2022-02-23 13:16 | 24 | 2022-02-22 12:25 | 2022-02-22 14:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106976 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2022-10282653 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | AHU-A1126-313 ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-03-27 00:05 | 2022-03-27 01:05 | 2022-03-28 01:05 | 24 | 2022-03-27 00:10 | 2022-03-27 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-11091017 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | Chilled Water leakage from isolation valve and insulation damage. |  | FM008 |  | 2022-10-12 07:13 | 2022-10-12 08:13 | 2022-10-13 08:13 | 24 | 2022-10-12 07:20 | 2022-10-12 08:20 | 60 | 120 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95216 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2022-11091018 | ASD-COC-TFL004-AHU139 | AIR HANDLING UNIT-05 | Chilled Water leakage from DRV valve and insulation damage- C3 04 01 |  | FM008 |  | 2022-10-12 07:14 | 2022-10-12 08:14 | 2022-10-13 08:14 | 24 | 2022-10-12 07:20 | 2022-10-12 09:25 | 125 | 65 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 004 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95216 | 17053 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2022-10208585 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-02 12:10 | 2022-03-02 13:10 | 2022-03-03 13:10 | 24 | 2022-03-02 12:15 | 2022-03-02 14:30 | 135 | 405 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 87807 |  |  | FM5803 | Tiwari, Mr. Sanjeed Kumar | N - - - |  | Voice Communication
| CM-2022-11219144 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 147 -DUST INSTALLTION DAMAGE- C3-06-01. |  | FM008 |  | 2022-11-25 07:07 | 2022-11-25 08:07 | 2022-11-26 08:07 | 24 | 2022-11-25 07:15 | 2022-11-25 10:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11404256 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-27 20:33 | 2023-01-27 21:33 | 2023-01-28 21:33 | 24 | 2023-01-27 20:40 | 2023-01-27 23:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2023-12018232 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-07-29 19:23 | 2023-07-29 20:23 | 2023-07-30 20:23 | 24 | 2023-07-29 19:30 | 2023-07-29 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12484188 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-12-18 07:25 | 2023-12-18 08:25 | 2023-12-19 08:25 | 24 | 2023-12-18 07:30 | 2023-12-18 18:25 | 655 | 345 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11081362 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AHU-A1126-321 FILTER ALARM C3-06-01 |  | FM008 |  | 2022-10-07 19:04 | 2022-10-07 20:04 | 2022-10-08 20:04 | 24 | 2022-10-07 19:10 | 2022-10-07 20:10 | 60 | 90 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 76858 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11196619 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AHU-A1126- 321- DUCT INSULATION DAMAGED- C3-06-01 |  | FM008 |  | 2022-11-19 19:37 | 2022-11-19 20:37 | 2022-11-20 20:37 | 24 | 2022-11-19 19:45 | 2022-11-19 21:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17154 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11762026 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AHU-A1126-321 – AHU CABIN LAMP IS NOT ILLUMANATING |  | FM008 |  | 2023-05-01 14:34 | 2023-05-01 15:34 | 2023-05-02 15:34 | 24 | 2023-05-01 14:44 | 2023-05-01 16:12 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 17053 |  |  | FM7853 | Ronel Balid Guilles, | N - - - |  | Voice Communication
| CM-2022-10909742 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-321 |  | FM008 |  | 2022-08-03 08:04 | 2022-08-03 09:04 | 2022-08-04 09:04 | 24 | 2022-08-03 08:11 | 2022-08-03 16:05 | 474 | 184 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10969582 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED |  | FM008 |  | 2022-08-27 21:04 | 2022-08-27 22:04 | 2022-08-28 22:04 | 24 | 2022-08-27 21:10 | 2022-08-27 23:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-9966947 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1126-321 ( ASD-COC-TFL006-AHU147-FIL900 ) |  | FM008 |  | 2022-01-02 16:48 | 2022-01-02 17:48 | 2022-01-03 17:48 | 24 | 2022-01-02 16:57 | 2022-01-02 17:45 | 48 | 48 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 55709 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | E-mail
| CM-2022-10074380 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AHU-A1126-321 – CHILLED WATER LINE PAINT FADED- C3-06-03 |  | FM008 |  | 2022-01-23 09:43 | 2022-01-23 10:43 | 2022-01-24 10:43 | 24 | 2022-01-23 09:50 | 2022-01-23 12:30 | 160 | 256 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 55709 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-10368345 | ASD-COC-TFL006-AHU147 | AIR HANDLING UNIT-05 | AHU-A1126-321 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-04-15 10:21 | 2022-04-15 11:21 | 2022-04-16 11:21 | 24 | 2022-04-15 10:25 | 2022-04-15 13:00 | 155 | 310 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10820365 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AHU-A1126-322 - DP1 & DP3 FILTER ALARM |  | FM008 |  | 2022-07-07 07:35 | 2022-07-07 08:35 | 2022-07-08 08:35 | 24 | 2022-07-07 07:40 | 2022-07-07 09:55 | 135 | 405 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11193316 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | CHILLER LINE PAINT FADED – C3-06-02 |  | FM008 |  | 2022-11-15 19:30 | 2022-11-15 20:30 | 2022-11-16 20:30 | 24 | 2022-11-15 19:35 | 2022-11-15 21:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11935255 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-06-30 13:24 | 2023-06-30 14:24 | 2023-07-01 14:24 | 24 | 2023-06-30 13:30 | 2023-06-30 18:05 | 275 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12014994 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | RELEAF FAN MOTOR CONECTOR DAMAGED -C3-06-02 |  | FM008 |  | 2023-07-29 02:26 | 2023-07-29 03:26 | 2023-07-30 03:26 | 24 | 2023-07-29 02:35 | 2023-07-29 05:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12067172 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2023-08-13 07:42 | 2023-08-13 08:42 | 2023-08-14 08:42 | 24 | 2023-08-13 07:50 | 2023-08-13 13:50 | 360 | 545 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12095768 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AC TOO HOT C11 ARRIVAL AREA NEAR C2-06-18 |  | FM008 |  | 2023-08-16 11:32 | 2023-08-16 12:32 | 2023-08-17 12:32 | 24 | 2023-08-16 11:40 | 2023-08-16 12:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 17053 |  |  | R11940 | Alam, Mr. Zarif | N - - - |  | E-mail
| CM-2023-12098550 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY,AHU-A1126-322,C3-06-02 |  | FM008 |  | 2023-08-18 07:15 | 2023-08-18 08:15 | 2023-08-19 08:15 | 24 | 2023-08-18 07:20 | 2023-08-18 09:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2023-12366979 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-322) – C3 06 02 |  | FM008 |  | 2023-11-10 23:20 | 2023-11-11 00:20 | 2023-11-12 00:20 | 24 | 2023-11-10 23:20 | 2023-11-11 01:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11218262 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED - AHU-A1126-322 - C3-06-02 |  | FM008 |  | 2022-11-24 07:26 | 2022-11-24 08:26 | 2022-11-25 08:26 | 24 | 2022-11-24 07:30 | 2022-11-24 15:50 | 500 | 305 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | E-mail
| CM-2023-12097595 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY, AHU-A1126-322, C3-06-02 |  | FM008 |  | 2023-08-17 08:52 | 2023-08-17 09:52 | 2023-08-18 09:52 | 24 | 2023-08-17 08:55 | 2023-08-17 12:45 | 230 | 305 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12117732 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.3FLRP12.CONC6022.AHU322.SYSALM.DP3 / / - CONCOURSE C-THIRD FLOOR AREA 006 |  | FM008 |  | 2023-08-27 00:29 | 2023-08-27 01:29 | 2023-08-28 01:29 | 24 | 2023-08-27 00:35 | 2023-08-27 02:10 | 95 | 125 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | Y - - - |  | BMS
| CM-2024-12850007 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AHU-A1126-322 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-04-24 22:30 | 2024-04-24 23:30 | 2024-04-25 23:30 | 24 | 2024-04-24 22:35 | 2024-04-25 01:20 | 165 | 495 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-10889003 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AHU-A1126-322 – FILTER DIRTY – C3-06-02 |  | FM008 |  | 2022-07-31 14:09 | 2022-07-31 15:09 | 2022-08-01 15:09 | 24 | 2022-07-31 14:15 | 2022-07-31 17:40 | 205 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2023-11610219 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-04-01 19:38 | 2023-04-01 20:38 | 2023-04-02 20:38 | 24 | 2023-04-01 19:45 | 2023-04-01 22:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 121959 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2023-12223719 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AHU-A1126-322 AHU DUCT INSULATION DAMAGED C3-06-02 |  | FM008 |  | 2023-09-24 22:18 | 2023-09-24 23:18 | 2023-09-25 23:18 | 24 | 2023-09-24 22:25 | 2023-09-25 01:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 87807 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12322266 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1126-322)- |  | FM008 |  | 2023-10-26 22:31 | 2023-10-26 23:31 | 2023-10-27 23:31 | 24 | 2023-10-26 22:40 | 2023-10-27 00:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2024-12666833 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-06-02 |  | FM008 |  | 2024-02-19 11:39 | 2024-02-19 12:39 | 2024-02-20 12:39 | 24 | 2024-02-19 11:45 | 2024-02-19 17:40 | 355 | 305 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10042295 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | AHU-A1126-322 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-12 12:38 | 2022-01-12 13:38 | 2022-01-13 13:38 | 24 | 2022-01-12 12:40 | 2022-01-12 15:00 | 140 | 280 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68485 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10194375 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C3-06-02 |  | FM008 |  | 2022-02-27 07:37 | 2022-02-27 08:37 | 2022-02-28 08:37 | 24 | 2022-02-27 07:45 | 2022-02-27 10:40 | 175 | 350 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10103785 | ASD-COC-TFL006-AHU148 | AIR HANDLING UNIT-05 | INLET INSULATION DAMAGED – T3-06-03 |  | FM008 |  | 2022-02-03 07:36 | 2022-02-03 08:36 | 2022-02-04 08:36 | 24 | 2022-02-03 07:40 | 2022-02-03 11:15 | 215 | 645 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM5803 | SANJEED KUMAR TIWARI, | N - - - |  | Voice Communication
| CM-2022-11196644 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | AHU-A1126-323 C3-03-01- DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-19 21:46 | 2022-11-19 22:46 | 2022-11-20 22:46 | 24 | 2022-11-19 21:55 | 2022-11-19 23:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17154 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-11301118 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM-AHU-A1126-323)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 006 |  | FM008 |  | 2022-12-23 06:49 | 2022-12-23 07:49 | 2022-12-24 07:49 | 24 | 2022-12-23 06:58 | 2022-12-23 09:00 | 122 | 244 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11303229 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1126-323 |  | FM008 |  | 2022-12-24 08:50 | 2022-12-24 09:50 | 2022-12-25 09:50 | 24 | 2022-12-24 09:00 | 2022-12-24 12:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2023-12232502 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-323 – C3-06-01 |  | FM008 |  | 2023-09-28 22:24 | 2023-09-28 23:24 | 2023-09-29 23:24 | 24 | 2023-09-28 22:30 | 2023-09-29 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106973 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-12483770 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1126-323,C3-06-01 |  | FM008 |  | 2023-12-16 10:33 | 2023-12-16 11:33 | 2023-12-17 11:33 | 24 | 2023-12-16 10:40 | 2023-12-16 13:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10886340 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | FILTER ALARM -AHU-A1126-323)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 006 |  | FM008 |  | 2022-07-30 19:01 | 2022-07-30 20:01 | 2022-07-31 20:01 | 24 | 2022-07-30 19:05 | 2022-07-30 21:05 | 120 | 81 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11361352 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | filter dirty - C3-06-11 |  | FM008 |  | 2023-01-08 14:58 | 2023-01-08 15:58 | 2023-01-09 15:58 | 24 | 2023-01-08 15:05 | 2023-01-08 16:40 | 95 | 285 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2023-11951093 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-323 – T3-06-01 |  | FM008 |  | 2023-07-08 07:20 | 2023-07-08 08:20 | 2023-07-09 08:20 | 24 | 2023-07-08 07:30 | 2023-07-08 10:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10368346 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | AHU-A1126-323 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-04-15 10:25 | 2022-04-15 11:25 | 2022-04-16 11:25 | 24 | 2022-04-15 10:30 | 2022-04-15 12:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11590184 | ASD-COC-TFL006-AHU149 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED AHU-A1126-323 - C3-06-01 |  | FM008 |  | 2023-03-25 15:41 | 2023-03-25 16:41 | 2023-03-26 16:41 | 24 | 2023-03-25 15:50 | 2023-03-25 17:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 94954 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2022-10841840 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-07-15 21:33 | 2022-07-15 22:33 | 2022-07-16 22:33 | 24 | 2022-07-15 21:40 | 2022-07-15 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | BMS
| CM-2022-11193318 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | CHILLER LINE PAINT FADED – C3-06-02 |  | FM008 |  | 2022-11-15 19:31 | 2022-11-15 20:31 | 2022-11-16 20:31 | 24 | 2022-11-15 19:35 | 2022-11-15 21:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12041392 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | OVERLOAD RELAY FAULTY - AHU-A1126-324 – C3-06-02 |  | FM008 |  | 2023-08-02 15:00 | 2023-08-02 16:00 | 2023-08-03 16:00 | 24 | 2023-08-02 15:10 | 2023-08-02 18:09 | 179 | 358 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | CIRCUIT TRIP DUE TO OVERLOAD | RESET THE BREAKER | 106973 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12049552 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-05 19:39 | 2023-08-05 20:39 | 2023-08-06 20:39 | 24 | 2023-08-05 19:45 | 2023-08-05 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12188449 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-09-15 19:06 | 2023-09-15 20:06 | 2023-09-16 20:06 | 24 | 2023-09-15 19:10 | 2023-09-15 21:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-11273353 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | DP1 AND DP 3 FILTER ALARM |  | FM008 |  | 2022-12-16 06:56 | 2022-12-16 07:56 | 2022-12-17 07:56 | 24 | 2022-12-16 07:05 | 2022-12-16 09:30 | 145 | 435 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12632287 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - MECHANICAL ROOM C3-06-02 |  | FM008 |  | 2024-02-07 20:29 | 2024-02-07 21:29 | 2024-02-08 21:29 | 24 | 2024-02-07 20:38 | 2024-02-08 01:10 | 272 | 333 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17053 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-11215893 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | AHU-A1126-324 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-25 21:39 | 2022-11-25 22:39 | 2022-11-26 22:39 | 24 | 2022-11-25 21:45 | 2022-11-25 23:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12364374 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1126-324 )– C3 08 02 |  | FM008 |  | 2023-11-09 19:24 | 2023-11-09 20:24 | 2023-11-10 20:24 | 24 | 2023-11-09 19:30 | 2023-11-09 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12576538 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | WATER LEAKING FROM THE CEILING -GATE C11 |  | FM008 |  | 2024-01-19 11:24 | 2024-01-19 12:24 | 2024-01-20 12:24 | 24 | 2024-01-19 11:30 | 2024-01-19 15:20 | 230 | 105 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 17053 |  |  | C07170 | KHAMISI | N - - - |  | Voice Communication
| CM-2022-10045272 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – C3-06-03 |  | FM008 |  | 2022-01-12 09:55 | 2022-01-12 10:55 | 2022-01-13 10:55 | 24 | 2022-01-12 10:05 | 2022-01-12 12:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 105233 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10888106 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – MEC ROOM ,C3-06-02 |  | FM008 |  | 2022-07-31 08:36 | 2022-07-31 09:36 | 2022-08-01 09:36 | 24 | 2022-07-31 08:40 | 2022-07-31 18:35 | 595 | 185 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2023-11362926 | ASD-COC-TFL006-AHU150 | AIR HANDLING UNIT-05 | AHU-A1126-324)-DUCT INSULATION DAMAGE-CONCOURSE C-THIRD FLOOR AREA 006 |  | FM008 |  | 2023-01-13 07:03 | 2023-01-13 08:03 | 2023-01-14 08:03 | 24 | 2023-01-13 07:10 | 2023-01-13 10:30 | 200 | 600 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 77406 | 55709 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10079629 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | AHU-A1126-359-LIGHTING FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2022-01-26 10:32 | 2022-01-26 11:32 | 2022-01-27 11:32 | 24 | 2022-01-26 10:40 | 2022-01-26 12:09 | 89 | 178 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 95217 | 55709 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10793250 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-359 -MECHANICAL ROOM C3-06-01 |  | FM008 |  | 2022-07-03 13:07 | 2022-07-03 14:07 | 2022-07-04 14:07 | 24 | 2022-07-03 13:15 | 2022-07-03 16:20 | 185 | 290 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 95217 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-11230202 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | AHU-A1126-359- FILTER ALARM |  | FM008 |  | 2022-11-28 07:06 | 2022-11-28 08:06 | 2022-11-29 08:06 | 24 | 2022-11-28 07:15 | 2022-11-28 09:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11999052 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | AHU-A1126-359 CABIN LAMP SWICTH FAUTY C3-06-01 |  | FM008 |  | 2023-07-23 00:44 | 2023-07-23 01:44 | 2023-07-24 01:44 | 24 | 2023-07-23 00:50 | 2023-07-23 05:30 | 280 | 295 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 106972 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11117225 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | AHU-A1126-359 AHU CABIN LAMP NOT WORKING C3-06-01 |  | FM008 |  | 2022-10-21 10:12 | 2022-10-21 11:12 | 2022-10-22 11:12 | 24 | 2022-10-21 10:20 | 2022-10-21 15:40 | 320 | 183 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11801956 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | AHU-A1126-359)- - DUCT INSULATION DAMAGED-- |  | FM008 |  | 2023-05-18 20:02 | 2023-05-18 21:02 | 2023-05-19 21:02 | 24 | 2023-05-18 20:08 | 2023-05-18 23:08 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 94953 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12041297 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE -c0-06-01 |  | FM008 |  | 2023-08-02 08:08 | 2023-08-02 09:08 | 2023-08-03 09:08 | 24 | 2023-08-02 08:15 | 2023-08-02 11:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-11177237 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT ACCESS DOOR DAMAGE, SUPPLY AIR LEAK FROM THE EDGES OF DOOR AND CREATING CONDENSATION UPON THE DOOR FRAME AREA - C3-06-01 FA1-AHU-A1126-359 |  | FM008 |  | 2022-11-09 10:04 | 2022-11-09 11:04 | 2022-11-10 11:04 | 24 | 2022-11-09 10:15 | 2022-11-09 11:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94954 | 87807 |  |  | 90948 | Quazi, Mr. Maudud Hassan | N - - - |  | E-mail
| CM-2024-12872512 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-359 – C3-06-01 |  | FM008 |  | 2024-04-30 20:00 | 2024-04-30 21:00 | 2024-05-01 21:00 | 24 | 2024-04-30 20:05 | 2024-04-30 22:25 | 140 | 420 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12278889 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1126-359 -C3-06-07 |  | FM008 |  | 2023-10-11 13:10 | 2023-10-11 14:10 | 2023-10-12 14:10 | 24 | 2023-10-11 13:15 | 2023-10-11 18:35 | 320 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12733171 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | AHU-A1126-359 C3-06-01 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-03-16 07:07 | 2024-03-16 08:07 | 2024-03-17 08:07 | 24 | 2024-03-16 07:10 | 2024-03-16 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2022-10073122 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1126-359 C3-06-01 |  | FM008 |  | 2022-01-23 11:07 | 2022-01-23 12:07 | 2022-01-24 12:07 | 24 | 2022-01-23 11:10 | 2022-01-23 14:35 | 205 | 245 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 89127 | 55709 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-10366010 | ASD-COC-TFL006-AHU164 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -C3-06-01 |  | FM008 |  | 2022-04-17 08:12 | 2022-04-17 09:12 | 2022-04-18 09:12 | 24 | 2022-04-17 08:17 | 2022-04-17 10:17 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10188246 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | DUCT INSULATIONN IS DAMAGED - AHU-A1126-360 – C3-06-02 |  | FM008 |  | 2022-02-25 09:33 | 2022-02-25 10:33 | 2022-02-26 10:33 | 24 | 2022-02-25 09:37 | 2022-02-25 11:37 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10231341 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -C3-06-02 |  | FM008 |  | 2022-03-10 19:06 | 2022-03-10 20:06 | 2022-03-11 20:06 | 24 | 2022-03-10 19:10 | 2022-03-10 21:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2022-10793252 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1126-363 -MECHANICAL ROOM C3-06-02 |  | FM008 |  | 2022-07-03 13:10 | 2022-07-03 14:10 | 2022-07-04 14:10 | 24 | 2022-07-03 13:15 | 2022-07-03 14:40 | 85 | 255 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 95217 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11999944 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | AHU-A1126-360 AHU CABIN LAMP NOT WOKRING C3-06-02 |  | FM008 |  | 2023-07-23 00:31 | 2023-07-23 01:31 | 2023-07-24 01:31 | 24 | 2023-07-23 00:40 | 2023-07-23 03:00 | 140 | 280 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106972 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12200426 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-09-20 19:13 | 2023-09-20 20:13 | 2023-09-21 20:13 | 24 | 2023-09-20 19:15 | 2023-09-21 00:40 | 325 | 565 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2022-11190011 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | AHU-A1126-360 – CHILLER LINE PAINT FADED- |  | FM008 |  | 2022-11-15 21:43 | 2022-11-15 22:43 | 2022-11-16 22:43 | 24 | 2022-11-15 21:50 | 2022-11-15 23:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12098475 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | A1126-360-DUCT INSULATION DAMAGE- |  | FM008 |  | 2023-08-17 22:14 | 2023-08-17 23:14 | 2023-08-18 23:14 | 24 | 2023-08-17 22:20 | 2023-08-18 00:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12101022 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-08-20 19:28 | 2023-08-20 20:28 | 2023-08-21 20:28 | 24 | 2023-08-20 19:35 | 2023-08-21 01:35 | 360 | 545 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12872513 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-360 – C3-06-02 |  | FM008 |  | 2024-04-30 20:02 | 2024-04-30 21:02 | 2024-05-01 21:02 | 24 | 2024-04-30 20:10 | 2024-05-01 00:55 | 285 | 440 | 4 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2023-12274773 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.3FLRP12.CONC6022.AHU360.SYSALM.DP1 / / - MECHANICAL ROOM C3-06-02 |  | FM008 |  | 2023-10-09 09:43 | 2023-10-09 10:43 | 2023-10-10 10:43 | 24 | 2023-10-09 09:50 | 2023-10-09 11:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2024-12648241 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | AHU-A1126-360 SUPPLY DUCT INSULATION DAMAGE C3-06-02 |  | FM008 |  | 2024-02-14 19:47 | 2024-02-14 20:47 | 2024-02-15 20:47 | 24 | 2024-02-14 19:55 | 2024-02-14 21:45 | 110 | 220 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 87807 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2024-12733172 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | AHU-1126-360 C3-06-02 DUCT INSULATION DAMAGE |  | FM008 |  | 2024-03-16 07:09 | 2024-03-16 08:09 | 2024-03-17 08:09 | 24 | 2024-03-16 07:10 | 2024-03-16 10:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 17053 |  |  | FM12771 | ANTHONY FELIX PHILIP, Mr. | N - - - |  | Voice Communication
| CM-2022-10256977 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-03-18 11:57 | 2022-03-18 12:57 | 2022-03-19 12:57 | 24 | 2022-03-18 12:05 | 2022-03-18 14:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | BMS
| CM-2022-11076952 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | AHU-A1126-360 FILTER DIRTY |  | FM008 |  | 2022-10-05 10:13 | 2022-10-05 11:13 | 2022-10-06 11:13 | 24 | 2022-10-05 10:20 | 2022-10-05 16:20 | 360 | 195 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10679404 | ASD-COC-TFL006-AHU165 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1126-360 – C3-06-02 |  | FM008 |  | 2022-05-21 00:02 | 2022-05-21 01:02 | 2022-05-22 01:02 | 24 | 2022-05-21 00:50 | 2022-05-21 01:50 | 60 | 120 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 006 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11289200 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING – C3-08-01 |  | FM008 |  | 2022-12-19 15:01 | 2022-12-19 16:01 | 2022-12-20 16:01 | 24 | 2022-12-19 15:08 | 2022-12-19 18:03 | 175 | 243 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11909708 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | RELIEF MOTOR FLEXIBLE CONNECTOR DAMAGED - AHU-A1126-325 - C3-08-01 |  | FM008 |  | 2023-06-21 15:33 | 2023-06-21 16:33 | 2023-06-22 16:33 | 24 | 2023-06-21 15:42 | 2023-06-21 17:10 | 88 | 176 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 133396 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | BMS
| CM-2023-11913337 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | AHU HEATER FLEXIBLE CONNECTOR DAMAGED - AHU-A1126-325 – C3-08-01 |  | FM008 |  | 2023-06-23 04:06 | 2023-06-23 05:06 | 2023-06-24 05:06 | 24 | 2023-06-23 04:10 | 2023-06-23 06:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17573 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12097375 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | AHU-A1126-325 EXIT DOOR AIR LEAKAGE -T3 -08-01 |  | FM008 |  | 2023-08-19 16:34 | 2023-08-19 17:34 | 2023-08-20 17:34 | 24 | 2023-08-19 16:40 | 2023-08-19 18:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | DARIN AIR FLOW | RECTIFIED | 106914 | 17053 |  |  | FM12472 | Senthilkumar, Mr. Arumuga Nainar | N - - - |  | Voice Communication
| CM-2023-12484295 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-12-16 07:17 | 2023-12-16 08:17 | 2023-12-17 08:17 | 24 | 2023-12-16 07:20 | 2023-12-16 10:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12490200 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - C3-08-01 |  | FM008 |  | 2023-12-21 15:14 | 2023-12-21 16:14 | 2023-12-22 16:14 | 24 | 2023-12-21 15:20 | 2023-12-21 17:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2022-10889001 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | AHU-A1126-325 – FILTER DIRTY – C3-08-01 |  | FM008 |  | 2022-07-31 14:06 | 2022-07-31 15:06 | 2022-08-01 15:06 | 24 | 2022-07-31 14:15 | 2022-07-31 15:30 | 75 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM5678 | MUHAMED YAHYA ALUMKOOTTATHIL MUHAMEDKWAJA, | N - - - |  | Voice Communication
| CM-2022-11176165 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | AHU-A1126-325 - RETURN DUCT INSULATION DAMAGED - C3-08-01 |  | FM008 |  | 2022-11-08 19:34 | 2022-11-08 20:34 | 2022-11-09 20:34 | 24 | 2022-11-08 19:40 | 2022-11-08 23:45 | 245 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-12254973 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-325 - MECHANICAL ROOM C3-08-01 |  | FM008 |  | 2023-10-04 19:10 | 2023-10-04 20:10 | 2023-10-05 20:10 | 24 | 2023-10-04 19:15 | 2023-10-04 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM5557 | Mr. Rajesh Kumar Singh, | N - - - |  | Voice Communication
| CM-2023-11362924 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | (AHU-A1126-325)-DUCT INSULATION DAMAGE -CONCOURSE C-THIRD FLOOR AREA 008 |  | FM008 |  | 2023-01-13 07:00 | 2023-01-13 08:00 | 2023-01-14 08:00 | 24 | 2023-01-13 07:10 | 2023-01-13 10:30 | 200 | 600 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 77406 | 55709 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10128651 | ASD-COC-TFL008-AHU151 | AIR HANDLING UNIT-05 | DUCT ACCESS DOOR AIR LEAKAGE - AHU-A1126-325 – C3-08-01 |  | FM008 |  | 2022-02-11 07:27 | 2022-02-11 08:27 | 2022-02-12 08:27 | 24 | 2022-02-11 07:35 | 2022-02-11 09:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10224568 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2022-03-09 07:50 | 2022-03-09 08:50 | 2022-03-10 08:50 | 24 | 2022-03-09 08:00 | 2022-03-09 11:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM7717 | R W Herath Mudiyanselage Giddawa Gedara, Mr. Gamini Rajaguru | N - - - |  | Voice Communication
| CM-2022-10674518 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - C3-08-02 |  | FM008 |  | 2022-05-19 00:02 | 2022-05-19 01:02 | 2022-05-20 01:02 | 24 | 2022-05-19 00:05 | 2022-05-19 01:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-11277552 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | MERINE LIGHT NOT ILLUMINATING - AHU-A1126-326 – C3-08-02 |  | FM008 |  | 2022-12-18 14:34 | 2022-12-18 15:34 | 2022-12-19 15:34 | 24 | 2022-12-18 14:44 | 2022-12-18 16:44 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12049553 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-08-05 19:40 | 2023-08-05 20:40 | 2023-08-06 20:40 | 24 | 2023-08-05 19:45 | 2023-08-05 22:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11196275 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | AHU-A1126-326 CHILLER WATER LINE PAINT FADED C3-08-02 |  | FM008 |  | 2022-11-17 20:52 | 2022-11-17 21:52 | 2022-11-18 21:52 | 24 | 2022-11-17 21:00 | 2022-11-17 23:30 | 150 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 87807 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-11216880 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -C3-08-02 |  | FM008 |  | 2022-11-25 12:48 | 2022-11-25 13:48 | 2022-11-26 13:48 | 24 | 2022-11-25 12:58 | 2022-11-25 16:00 | 182 | 546 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17333 | 87807 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-11355913 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | AHU-A1126-326 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-10 07:43 | 2023-01-10 08:43 | 2023-01-11 08:43 | 24 | 2023-01-10 07:50 | 2023-01-10 18:00 | 610 | 465 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2023-12366275 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | AHU-A1126-324 -DUCT INSULATION DAMAGED – C3-08-02 |  | FM008 |  | 2023-11-10 19:23 | 2023-11-10 20:23 | 2023-11-11 20:23 | 24 | 2023-11-10 19:25 | 2023-11-10 22:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM10910 | Sivaganesan Alwar, Mr. | N - - - |  | Voice Communication
| CM-2024-12732846 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AHU-A1126-326 C3-08-02 |  | FM008 |  | 2024-03-16 19:39 | 2024-03-16 20:39 | 2024-03-17 20:39 | 24 | 2024-03-16 19:45 | 2024-03-16 22:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10888527 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – MEC ROOM, C3-08-02 |  | FM008 |  | 2022-07-31 08:37 | 2022-07-31 09:37 | 2022-08-01 09:37 | 24 | 2022-07-31 08:45 | 2022-07-31 15:30 | 405 | 140 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | E-mail
| CM-2022-10952950 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED –C3-08-02 |  | FM008 |  | 2022-08-17 07:10 | 2022-08-17 08:10 | 2022-08-18 08:10 | 24 | 2022-08-17 07:19 | 2022-08-17 09:05 | 106 | 318 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11581558 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | AHU-A1126-326 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-03-20 19:27 | 2023-03-20 20:27 | 2023-03-21 20:27 | 24 | 2023-03-20 19:30 | 2023-03-20 22:15 | 165 | 495 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM11739 | Kalyanasundaram, Mr. Ranjith Kumar | N - - - |  | Voice Communication
| CM-2022-10830339 | ASD-COC-TFL008-AHU152 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED AHU-A1126-326 |  | FM008 |  | 2022-07-12 22:02 | 2022-07-12 23:02 | 2022-07-13 23:02 | 24 | 2022-07-12 22:05 | 2022-07-13 00:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11200292 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – C3-08-01 |  | FM008 |  | 2022-11-20 00:08 | 2022-11-20 01:08 | 2022-11-21 01:08 | 24 | 2022-11-20 00:15 | 2022-11-20 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2023-11866199 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | AHU-A1126-327 – HEATER FLEXIBLE CABLE DAMAGED |  | FM008 |  | 2023-06-11 03:27 | 2023-06-11 04:27 | 2023-06-12 04:27 | 24 | 2023-06-11 03:30 | 2023-06-11 06:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 94953 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12494688 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1126-327,C3-08-01 |  | FM008 |  | 2023-12-24 08:18 | 2023-12-24 09:18 | 2023-12-25 09:18 | 24 | 2023-12-24 08:25 | 2023-12-24 14:30 | 365 | 305 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-12346344 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | AHU-A1126-327 DUCT INSULATION DAMAGED C3-08-01 |  | FM008 |  | 2023-11-03 19:19 | 2023-11-03 20:19 | 2023-11-04 20:19 | 24 | 2023-11-03 19:25 | 2023-11-03 22:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12712235 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | DUCT ACCESS DOOR AIR LEAKAGE-AIR HANDLING UNIT 153 (TAG NO:AHU-A1126-327)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 008 |  | FM008 |  | 2024-03-06 11:58 | 2024-03-06 12:58 | 2024-03-07 12:58 | 24 | 2024-03-06 12:00 | 2024-03-06 15:00 | 180 | 540 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 17053 |  |  | FM12771 | Philip, Mr. Anthony Felix | N - - - |  | Voice Communication
| CM-2023-11916790 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-327 – C3 08 01 |  | FM008 |  | 2023-06-24 09:01 | 2023-06-24 10:01 | 2023-06-25 10:01 | 24 | 2023-06-24 09:05 | 2023-06-24 11:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12132255 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS MECHANICAL ROOM C3-08-01 |  | FM008 |  | 2023-08-30 12:53 | 2023-08-30 13:53 | 2023-08-31 13:53 | 24 | 2023-08-30 13:00 | 2023-08-30 14:30 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106972 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12273877 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-10-09 20:04 | 2023-10-09 21:04 | 2023-10-10 21:04 | 24 | 2023-10-09 20:10 | 2023-10-09 21:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12794352 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-327 - C3-08-01 |  | FM008 |  | 2024-04-03 07:07 | 2024-04-03 08:07 | 2024-04-04 08:07 | 24 | 2024-04-03 07:15 | 2024-04-03 10:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM11844 | Selvaraj Senthur Pandian, Mr. | N - - - |  | Voice Communication
| CM-2023-12364177 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY AHU-A1126-327 |  | FM008 |  | 2023-11-09 07:40 | 2023-11-09 08:40 | 2023-11-10 08:40 | 24 | 2023-11-09 07:45 | 2023-11-09 10:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2022-10235657 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | AHU-A1126-327- DP1 FILTER DIRTY- |  | FM008 |  | 2022-03-13 14:39 | 2022-03-13 15:39 | 2022-03-14 15:39 | 24 | 2022-03-13 14:49 | 2022-03-13 16:49 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-10128652 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | DUCT ACCESS DOOR AIR LEAKAGE - AHU-A1126-327 - C3-08-01 |  | FM008 |  | 2022-02-11 07:28 | 2022-02-11 08:28 | 2022-02-12 08:28 | 24 | 2022-02-11 07:35 | 2022-02-11 09:40 | 125 | 250 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10888040 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | FILTER DIRTY – C3-08-01 |  | FM008 |  | 2022-07-30 13:18 | 2022-07-30 14:18 | 2022-07-31 14:18 | 24 | 2022-07-30 13:25 | 2022-07-30 15:45 | 140 | 95 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2023-11643831 | ASD-COC-TFL008-AHU153 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - AHU-A1126-327 – C3-08-01 |  | FM008 |  | 2023-04-10 15:31 | 2023-04-10 16:31 | 2023-04-11 16:31 | 24 | 2023-04-10 15:40 | 2023-04-10 17:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 94954 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10672574 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 DUCT INSULATION DAMAGED C3-08-02 |  | FM008 |  | 2022-05-16 22:12 | 2022-05-16 23:12 | 2022-05-17 23:12 | 24 | 2022-05-16 22:20 | 2022-05-16 23:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM3432 | Rao, Mr. Ankana Srinivasa | N - - - |  | Voice Communication
| CM-2022-10801772 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 – RETURN DUCT INSULATION DAMAGED –C3-08-02 |  | FM008 |  | 2022-07-03 17:05 | 2022-07-03 18:05 | 2022-07-04 18:05 | 24 | 2022-07-03 17:10 | 2022-07-03 18:45 | 95 | 285 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 95217 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10873496 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 FILTER ALARM CONCOURSE C-THIRD FLOOR AREA 008 |  | FM008 |  | 2022-07-29 03:10 | 2022-07-29 04:10 | 2022-07-30 04:10 | 24 | 2022-07-29 03:19 | 2022-07-29 05:20 | 121 | 130 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11040596 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-09-20 20:43 | 2022-09-20 21:43 | 2022-09-21 21:43 | 24 | 2022-09-20 20:50 | 2022-09-20 23:20 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-12187409 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 DUCT INSULATION DAMAGED – C3-08-02 |  | FM008 |  | 2023-09-14 19:03 | 2023-09-14 20:03 | 2023-09-15 20:03 | 24 | 2023-09-14 19:05 | 2023-09-14 21:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 17053 |  |  | FM5557 | Singh, Mr. Rajesh Kumar | N - - - |  | Voice Communication
| CM-2022-11194607 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED - C3-08-02 |  | FM008 |  | 2022-11-18 00:07 | 2022-11-18 01:07 | 2022-11-19 01:07 | 24 | 2022-11-18 00:15 | 2022-11-18 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 121959 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11355914 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-01-10 07:44 | 2023-01-10 08:44 | 2023-01-11 08:44 | 24 | 2023-01-10 07:50 | 2023-01-10 12:45 | 295 | 485 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM10657 | RAJAKUMAR RAJAYAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11176851 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 – AHU FILTER DIRTY – C3-08-02 |  | FM008 |  | 2022-11-11 19:13 | 2022-11-11 20:13 | 2022-11-12 20:13 | 24 | 2022-11-11 19:20 | 2022-11-11 21:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2023-11916791 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1126-328– C3 08 01 |  | FM008 |  | 2023-06-24 09:02 | 2023-06-24 10:02 | 2023-06-25 10:02 | 24 | 2023-06-24 09:10 | 2023-06-24 11:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM10657 | Rajayah, Mr. Rajakumar | N - - - |  | Voice Communication
| CM-2023-12322589 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AIR HANDLING UNIT 154 (TAG NO:AHU-A1126-328)-AIRSIDE-CONCOURSE C-THIRD FLOOR AREA 008 |  | FM008 |  | 2023-10-28 07:09 | 2023-10-28 08:09 | 2023-10-29 08:09 | 24 | 2023-10-28 07:15 | 2023-10-28 09:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 119320 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-10202352 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED -C3-05-03 |  | FM008 |  | 2022-02-28 16:23 | 2022-02-28 17:23 | 2022-03-01 17:23 | 24 | 2022-02-28 16:30 | 2022-02-28 18:35 | 125 | 375 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10256978 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-03-18 12:00 | 2022-03-18 13:00 | 2022-03-19 13:00 | 24 | 2022-03-18 12:10 | 2022-03-18 16:15 | 245 | 365 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 87807 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10714767 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | RETUNE DUCT INSULATION IS DAMAGED - AHU-A1126-328 - MECHANICAL ROOM C3-08-02 |  | FM008 |  | 2022-06-04 22:33 | 2022-06-04 23:33 | 2022-06-05 23:33 | 24 | 2022-06-04 22:40 | 2022-06-04 23:55 | 75 | 150 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11291724 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 – CABIN LAMP NOT WORKING -* C3-08-02 |  | FM008 |  | 2022-12-21 00:12 | 2022-12-21 01:12 | 2022-12-22 01:12 | 24 | 2022-12-21 00:20 | 2022-12-21 03:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11969479 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-07-11 18:59 | 2023-07-11 19:59 | 2023-07-12 19:59 | 24 | 2023-07-11 19:05 | 2023-07-11 22:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10096620 | ASD-COC-TFL008-AHU154 | AIR HANDLING UNIT-05 | AHU-A1126-328 – CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-01-31 10:13 | 2022-01-31 11:13 | 2022-02-01 11:13 | 24 | 2022-01-31 10:20 | 2022-01-31 12:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 55709 |  |  | FM5430 | LAKSHMANAN SUBBIAH, Mr. | N - - - |  | Voice Communication
| CM-2022-11291788 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | MARINE LAMP NOT ILLUMINATING - AHU-A1126-361 – C3-08-01 |  | FM008 |  | 2022-12-21 10:26 | 2022-12-21 11:26 | 2022-12-22 11:26 | 24 | 2022-12-21 10:31 | 2022-12-21 12:02 | 91 | 182 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12253039 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-361 – C3-08-01 |  | FM008 |  | 2023-10-02 14:54 | 2023-10-02 15:54 | 2023-10-03 15:54 | 24 | 2023-10-02 15:00 | 2023-10-02 17:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 87807 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2022-10954200 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | supply duct insulation damaged |  | FM008 |  | 2022-08-18 07:09 | 2022-08-18 08:09 | 2022-08-19 08:09 | 24 | 2022-08-18 07:15 | 2022-08-18 09:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 55709 |  |  | FM1526 | Tasawoor Kadir, Mr. Malim | N - - - |  | Voice Communication
| CM-2023-11866855 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ASD-COC-TFL008-AHU166(AHU-A1126-361) MECHANICAL ROOM C3-08-01 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.3FLRP13.CONC8012.AHU361.SYSALM.DP1 / Jun/08/2023 2:48:22 PM |  | FM008 |  | 2023-06-08 15:27 | 2023-06-08 16:27 | 2023-06-09 16:27 | 24 | 2023-06-08 15:35 | 2023-06-08 18:00 | 145 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11930915 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | AHU LIGHTING FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2023-06-26 17:07 | 2023-06-26 18:07 | 2023-06-27 18:07 | 24 | 2023-06-26 17:16 | 2023-06-26 18:45 | 89 | 178 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 121959 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-12487295 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-12-18 13:21 | 2023-12-18 14:21 | 2023-12-19 14:21 | 24 | 2023-12-18 13:30 | 2023-12-18 16:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12708501 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-AIR HANDLING UNIT 166 (TAG NO:AHU-A1126-361)-CONCOURSE C-THIRD FLOOR AREA 008 |  | FM008 |  | 2024-03-06 11:55 | 2024-03-06 12:55 | 2024-03-07 12:55 | 24 | 2024-03-06 11:55 | 2024-03-06 17:35 | 340 | 455 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM12771 | Philip, Mr. Anthony Felix | N - - - |  | Voice Communication
| CM-2024-12822596 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1126-361 – C3-08-01 |  | FM008 |  | 2024-04-13 07:25 | 2024-04-13 08:25 | 2024-04-14 08:25 | 24 | 2024-04-13 07:30 | 2024-04-13 10:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-11037273 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | FAS SIGNAL ALARM - AHU-A1126-361 - LEVEL 3 CON C PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1126.3FLRP13.CONC8012.AHU361.GLBSGN.FAS1 / |  | FM008 |  | 2022-09-19 02:45 | 2022-09-19 03:45 | 2022-09-20 03:45 | 24 | 2022-09-19 02:55 | 2022-09-19 03:55 | 60 | 120 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106973 | 87807 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | BMS
| CM-2023-12095737 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEKAGE - C3-08-01 |  | FM008 |  | 2023-08-16 08:42 | 2023-08-16 09:42 | 2023-08-17 09:42 | 24 | 2023-08-16 08:50 | 2023-08-16 17:30 | 520 | 455 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2024-12629860 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | AHU-A1126-361 FILTER DIRTY |  | FM008 |  | 2024-02-08 08:27 | 2024-02-08 09:27 | 2024-02-09 09:27 | 24 | 2024-02-08 08:35 | 2024-02-08 10:55 | 140 | 420 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2024-12734948 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | AHU-A1126-361 DUCT INSULATION DAMAGED |  | FM008 |  | 2024-03-16 11:05 | 2024-03-16 12:05 | 2024-03-17 12:05 | 24 | 2024-03-16 11:05 | 2024-03-16 14:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12595160 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-AIR HANDLING UNIT 166 (TAG NO:AHU-A1126-361)- |  | FM008 |  | 2024-01-26 08:38 | 2024-01-26 09:38 | 2024-01-27 09:38 | 24 | 2024-01-26 08:45 | 2024-01-26 12:45 | 240 | 235 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM11905 | Ritish Jarial, Mr. | N - - - |  | Voice Communication
| CM-2023-11972528 | ASD-COC-TFL008-AHU166 | AIR HANDLING UNIT-05 | ACCESS DOOR AIR LEAKAGE - AHU-A1126-361 |  | FM008 |  | 2023-07-11 22:02 | 2023-07-11 23:02 | 2023-07-12 23:02 | 24 | 2023-07-11 22:10 | 2023-07-12 00:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NOT WORKING | LEAKAGE OF LIQUID OR GAS DUE TO DAMAGED PIPE | REPLACED THE DAMAGED PIPE | 106973 | 87807 |  |  | FM10910 | Alwar, Mr. Sivaganesan | N - - - |  | Voice Communication
| CM-2022-10075425 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | AHU-A1126-362; CHILL WATER LINE PAINT FADED – C3-08-02 |  | FM008 |  | 2022-01-24 10:38 | 2022-01-24 11:38 | 2022-01-25 11:38 | 24 | 2022-01-24 10:45 | 2022-01-24 12:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 55709 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2023-11908732 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED - AHU-A1126-362 – C3-08-02 |  | FM008 |  | 2023-06-21 12:21 | 2023-06-21 13:21 | 2023-06-22 13:21 | 24 | 2023-06-21 12:31 | 2023-06-21 14:30 | 119 | 238 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 133396 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | BMS
| CM-2022-11196274 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | AHU-A1126-362 CHILLER WATER LINE PAINT FADED C3-08-02 |  | FM008 |  | 2022-11-17 20:50 | 2022-11-17 21:50 | 2022-11-18 21:50 | 24 | 2022-11-17 20:55 | 2022-11-17 23:30 | 155 | 125 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106972 | 87807 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-11289637 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | MARINE LAMP IS NOT WORKING |  | FM008 |  | 2022-12-21 15:52 | 2022-12-21 16:52 | 2022-12-22 16:52 | 24 | 2022-12-21 15:56 | 2022-12-21 16:34 | 38 | 76 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 68060 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12202300 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY -C3-08-02 |  | FM008 |  | 2023-09-19 13:20 | 2023-09-19 14:20 | 2023-09-20 14:20 | 24 | 2023-09-19 13:25 | 2023-09-19 16:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2024-12734946 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | AHU-A1126-362 DUCT INSULATION DAMAGED |  | FM008 |  | 2024-03-16 11:03 | 2024-03-16 12:03 | 2024-03-17 12:03 | 24 | 2024-03-16 11:05 | 2024-03-16 14:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2024-12655279 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2024-02-18 07:26 | 2024-02-18 08:26 | 2024-02-19 08:26 | 24 | 2024-02-18 07:30 | 2024-02-18 10:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM1955 | KUMAR | N - - - |  | Voice Communication
| CM-2022-10142823 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | AHU-A1126-362 – DUCT ACCESS DOOR AIR LEAKAGE- |  | FM008 |  | 2022-02-17 22:12 | 2022-02-17 23:12 | 2022-02-18 23:12 | 24 | 2022-02-17 22:20 | 2022-02-18 00:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 55709 |  |  | FM1955 | Amma Sreedharan Pillai Sreekumar, Mr. Lekshmikutty | N - - - |  | Voice Communication
| CM-2022-10226322 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | AHU167 DUCT INSULATION DAMAGED – T3-08-03 |  | FM008 |  | 2022-03-09 13:56 | 2022-03-09 14:56 | 2022-03-10 14:56 | 24 | 2022-03-09 14:05 | 2022-03-09 16:05 | 120 | 285 | 3 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106976 | 17053 |  |  | FM2849 | Aneeshkumar, Mr. Mannoosseril Narayanakutty | N - - - |  | Voice Communication
| CM-2022-10676660 | ASD-COC-TFL008-AHU167 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED -C3-08-02 |  | FM008 |  | 2022-05-20 19:12 | 2022-05-20 20:12 | 2022-05-21 20:12 | 24 | 2022-05-20 19:15 | 2022-05-20 20:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | THIRD FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM1448 | Kalleri Veettil, Mr. Vinod Kumar | N - - - |  | Voice Communication
| CM-2022-10818204 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | FILTER DIRTY-AHU-A1154-A402)-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) |  | FM008 |  | 2022-07-04 13:04 | 2022-07-04 14:04 | 2022-07-05 14:04 | 24 | 2022-07-04 13:14 | 2022-07-04 14:50 | 96 | 192 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 95217 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12095375 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | WATER DRIPING FROM CEILING NEAR FOUNTAIN AREA |  | FM008 |  | 2023-08-16 10:43 | 2023-08-16 11:43 | 2023-08-17 11:43 | 24 | 2023-08-16 10:50 | 2023-08-16 16:30 | 340 | 125 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 77406 | 17053 |  |  | FM6922 | Murerwa, Ms. Silvia Gatwiri | N - - - |  | Voice Communication
| CM-2024-12704869 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | SUPPLY DUCT ACCESS DOOR LEAK - T4-24-01 |  | FM008 |  | 2024-03-06 15:25 | 2024-03-06 16:25 | 2024-03-07 16:25 | 24 | 2024-03-06 15:30 | 2024-03-06 17:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2023-11606502 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | AHU-A1154-A402- AHU INSIDE LIGHT NOT WORKING |  | FM008 |  | 2023-03-30 19:09 | 2023-03-30 20:09 | 2023-03-31 20:09 | 24 | 2023-03-30 19:15 | 2023-03-30 22:14 | 179 | 358 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 87807 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12198711 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | DP1 FILTER STATUS (AHU-A1154-A402) - T4 S12 - CM-2023-01-1542 |  | FM008 |  | 2023-09-17 22:36 | 2023-09-17 23:36 | 2023-09-18 23:36 | 24 | 2023-09-17 22:45 | 2023-09-17 23:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM11814 | Ayyappan Arunachalam | - - -
| CM-2023-11655144 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | SUPPLY FAN BELT IS DAMAGED |  | FM008 |  | 2023-04-14 01:37 | 2023-04-14 02:37 | 2023-04-15 02:37 | 24 | 2023-04-14 01:45 | 2023-04-14 04:35 | 170 | 245 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11673195 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | BLOWER BEARING FAULTY - AHU-A1154-A402 - QA1 LOUNGE |  | FM008 |  | 2023-04-17 07:27 | 2023-04-17 08:27 | 2023-04-18 08:27 | 24 | 2023-04-17 07:35 | 2023-04-17 11:35 | 240 | 480 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12555499 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | WATER LEAKING FROM THE CEILING NEAR T3-QA1-111 |  | FM008 |  | 2024-01-11 20:48 | 2024-01-11 21:18 | 2024-01-12 01:18 | 4 | 2024-01-11 20:55 | 2024-01-11 23:00 | 125 | 68 | 2 | HVAC |  | Closed | Urgent | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17333 | 17053 |  |  | FM11292 | Muturi, Ms. Grace Nyambura | N - - - |  | Voice Communication
| CM-2022-10261389 | ASD-LOU-QA1-AHU002 | AIR HANDLING UNIT-04 | AC VENT DIRTY -QA1 MAIN KITCHEN TU-A402-195 |  | FM008 |  | 2022-03-18 19:03 | 2022-03-18 20:03 | 2022-03-19 20:03 | 24 | 2022-03-18 19:10 | 2022-03-18 21:40 | 150 | 300 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11824847 | ASD-LOU-QA1-AHU003 | AIR HANDLING UNIT-04 | AHU HEATER FLEXIBLE CONNECTOR DAMAGED – T4 07A |  | FM008 |  | 2023-05-27 04:14 | 2023-05-27 05:14 | 2023-05-28 05:14 | 24 | 2023-05-27 04:20 | 2023-05-27 06:45 | 145 | 290 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 132112 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12704870 | ASD-LOU-QA1-AHU003 | AIR HANDLING UNIT-04 | DUCT INSULATION DAMAGED -T4-24-01 |  | FM008 |  | 2024-03-06 15:26 | 2024-03-06 16:26 | 2024-03-07 16:26 | 24 | 2024-03-06 15:35 | 2024-03-06 17:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2023-12198712 | ASD-LOU-QA1-AHU003 | AIR HANDLING UNIT-04 | DP1 FILTER STATUS (AHU-A1154-A421) - T4 S12 - CM-2023-01-1543 |  | FM008 |  | 2023-09-17 22:36 | 2023-09-17 23:36 | 2023-09-18 23:36 | 24 | 2023-09-17 22:45 | 2023-09-17 23:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17053 | 87807 |  |  | FM11814 | Ayyappan Arunachalam | - - -
| CM-2023-11624919 | ASD-LOU-QA1-AHU003 | AIR HANDLING UNIT-04 | LIGHTING FLEXIBLE CONNECTOR DAMAGED --AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) |  | FM008 |  | 2023-04-07 23:00 | 2023-04-08 | 2023-04-09 | 24 | 2023-04-07 23:05 | 2023-04-08 00:25 | 80 | 160 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-FIRST CLASS LOUNGE (QA1) | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106914 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10155100 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2-DELI DINING-AC TOO HOT |  | FM008 |  | 2022-02-19 17:39 | 2022-02-19 18:39 | 2022-02-20 18:39 | 24 | 2022-02-19 17:45 | 2022-02-19 18:30 | 45 | 45 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95217 | 55709 |  |  | 82123 | Sharma, Mr. Bobby Mukesh | N - - - |  | Voice Communication
| CM-2022-10710972 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM - DELI DINING AREA |  | FM008 |  | 2022-05-31 23:11 | 2022-06-01 00:11 | 2022-06-02 00:11 | 24 | 2022-05-31 23:15 | 2022-06-01 00:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 82123 | Sharma, Mr. Bobby Mukesh | N - - - |  | Voice Communication
| CM-2022-10722502 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD -QA2 DINING AREA |  | FM008 |  | 2022-06-06 05:08 | 2022-06-06 06:08 | 2022-06-07 06:08 | 24 | 2022-06-06 05:15 | 2022-06-06 08:15 | 180 | 60 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 61871 | Kaluarachchige Don, Ms. Nuradha | N - - - |  | Voice Communication
| CM-2022-10737839 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2- DELI DINING AND COMMON AREA – AC TOO HOT |  | FM008 |  | 2022-06-12 17:51 | 2022-06-12 18:51 | 2022-06-13 18:51 | 24 | 2022-06-12 18:00 | 2022-06-12 20:00 | 120 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 87807 |  |  | FM8258 | Mateo, Ms. Helen Arcenio | N - - - |  | Voice Communication
| CM-2022-10747918 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | A/C IS TOO WARM T4-QA2-01 (DINING) |  | FM008 |  | 2022-06-13 16:32 | 2022-06-13 17:32 | 2022-06-14 17:32 | 24 | 2022-06-13 16:40 | 2022-06-13 17:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 87807 |  |  | 29674 | Tangilan, Ms. Mary Jane Ignacio | N - - - |  | Voice Communication
| CM-2022-10748846 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | Qa2-DELI DINING – AC TOO HOT |  | FM008 |  | 2022-06-14 19:21 | 2022-06-14 20:21 | 2022-06-15 20:21 | 24 | 2022-06-14 19:25 | 2022-06-14 21:30 | 125 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17154 | 87807 |  |  | 28329 | Gutierrez, Mr. Ronnie Natac | N - - - |  | Voice Communication
| CM-2022-10775193 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC NOT COOLING – DELI DINING & FAMILY AREA OF QA2 LOUNGE (PASSENGERS COMPLAINING) |  | FM008 |  | 2022-06-20 15:54 | 2022-06-20 16:24 | 2022-06-20 20:24 | 4 | 2022-06-20 16:00 | 2022-06-20 17:30 | 90 | 60 | 1 | HVAC |  | Closed | Urgent | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2022-10778509 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI AREA DINING AC TOO HOT |  | FM008 |  | 2022-06-24 15:14 | 2022-06-24 16:14 | 2022-06-25 16:14 | 24 | 2022-06-24 15:20 | 2022-06-24 18:20 | 180 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | 109304 | Mahajani, Mr. Amit Ravindra | N - - - |  | Voice Communication
| CM-2022-10828660 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DINING AREA AC IS TOO HOT - (URGENT) |  | FM008 |  | 2022-07-08 07:23 | 2022-07-08 08:23 | 2022-07-09 08:23 | 24 | 2022-07-08 07:30 | 2022-07-08 16:10 | 520 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94953 | 95217 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-10826508 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI DINING – AC TOO HOT |  | FM008 |  | 2022-07-12 13:29 | 2022-07-12 14:29 | 2022-07-13 14:29 | 24 | 2022-07-12 13:35 | 2022-07-12 17:40 | 245 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 95217 |  |  | 28329 | Gutierrez, Mr. Ronnie Natac | N - - - |  | Voice Communication
| CM-2022-10840706 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT - QA2 DELI DINING |  | FM008 |  | 2022-07-15 15:14 | 2022-07-15 16:14 | 2022-07-16 16:14 | 24 | 2022-07-15 15:20 | 2022-07-15 16:15 | 55 | 55 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 95217 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-10842668 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | A/C IS TO WARM AT DELI DINING |  | FM008 |  | 2022-07-17 03:19 | 2022-07-17 04:19 | 2022-07-18 04:19 | 24 | 2022-07-17 03:25 | 2022-07-17 06:00 | 155 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 95217 |  |  | 83158 | Naeem, Mr. Mohammed | N - - - |  | Voice Communication
| CM-2022-10910354 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC IS TOO COLD-HIGH WIND FLOW FROM AC- T4-QA2-01 (DINING) |  | FM008 |  | 2022-08-06 17:22 | 2022-08-06 18:22 | 2022-08-07 18:22 | 24 | 2022-08-06 17:30 | 2022-08-06 18:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 55709 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2022-10928639 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM - DELI DINING AREA |  | FM008 |  | 2022-08-10 23:54 | 2022-08-11 00:54 | 2022-08-12 00:54 | 24 | 2022-08-11 | 2022-08-11 01:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 55709 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2022-10931755 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT IN DAILY DINING AREA BUSINESS LOUNGE FOURTH FLOOR MEZZANINE QA2 |  | FM008 |  | 2022-08-11 13:42 | 2022-08-11 14:42 | 2022-08-12 14:42 | 24 | 2022-08-11 13:50 | 2022-08-11 14:25 | 35 | 35 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 55709 |  |  | 65957 | Rocamora, Mr. Owens Tabilog | N - - - |  | Voice Communication
| CM-2023-11346197 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD DELI DINING AREA |  | FM008 |  | 2023-01-03 21:52 | 2023-01-03 22:52 | 2023-01-04 22:52 | 24 | 2023-01-03 22:00 | 2023-01-03 23:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-11350334 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD, DELI DINING AREA QA 2 LOUNGE |  | FM008 |  | 2023-01-05 23:44 | 2023-01-06 00:44 | 2023-01-07 00:44 | 24 | 2023-01-05 23:50 | 2023-01-06 04:00 | 250 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 133396 | 17053 |  |  | 85558 | Ogunbor, Mr. Osariemen Noel | N - - - |  | Voice Communication
| CM-2023-11878407 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI DINING AC TOO HOT |  | FM008 |  | 2023-06-12 19:08 | 2023-06-12 20:08 | 2023-06-13 20:08 | 24 | 2023-06-12 19:15 | 2023-06-12 23:30 | 255 | 30 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-11960252 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT - QA2 DELI DINING AREA |  | FM008 |  | 2023-07-08 18:55 | 2023-07-08 19:55 | 2023-07-09 19:55 | 24 | 2023-07-08 19:05 | 2023-07-08 21:00 | 115 | 60 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 87807 |  |  | 124352 | Navarro, Ms. Patricia Carretero | N - - - |  | Voice Communication
| CM-2023-11999023 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TEMP WARM-DAILY DINING AREA -QA2 |  | FM008 |  | 2023-07-22 17:51 | 2023-07-22 18:51 | 2023-07-23 18:51 | 24 | 2023-07-22 17:55 | 2023-07-22 18:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 17053 |  |  | 134565 | Mayanja, Mr. Elvis Manga | N - - - |  | Voice Communication
| CM-2023-12035046 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT DELI DINING AREA QA2 |  | FM008 |  | 2023-07-30 22:35 | 2023-07-30 23:35 | 2023-07-31 23:35 | 24 | 2023-07-30 22:40 | 2023-07-30 23:58 | 78 | 58 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-12058719 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | DP1 FINAL FILTER STATUS - QA2 - MECHANICAL ROOM ABOVE ROOM T3-QA2-29 (AHU-A1154-A404) PROJECT4.LOGICALVIEW:LOGICAL.BAC7.A1153QA.MECHRM.QA2011.AHUA404.SYSALM.DP1 / |  | FM008 |  | 2023-08-07 13:36 | 2023-08-07 14:36 | 2023-08-08 14:36 | 24 | 2023-08-07 13:45 | 2023-08-07 20:30 | 405 | 260 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12065368 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC NOT WORKING (TOO HOT) - QA2 DELI DINING AREA |  | FM008 |  | 2023-08-11 19:22 | 2023-08-11 20:22 | 2023-08-12 20:22 | 24 | 2023-08-11 19:30 | 2023-08-11 23:30 | 240 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-12428584 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD -QA2 DINING AREA |  | FM008 |  | 2023-12-01 13:47 | 2023-12-01 14:47 | 2023-12-02 14:47 | 24 | 2023-12-01 13:50 | 2023-12-01 14:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | DAMAGED | ATUACTOR DAMAGE | REPLACED THE COIL | 132112 | 87807 |  |  | 30842 | Anwari, Mr. Tanveer Iqbal | N - - - |  | Voice Communication
| CM-2023-11836623 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | A/C IS TOO HOT |  | FM008 |  | 2023-05-30 15:25 | 2023-05-30 16:25 | 2023-05-31 16:25 | 24 | 2023-05-30 15:30 | 2023-05-30 16:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 123901 | Shaik, Mr. Mohammed Samiulla | N - - - |  | Voice Communication
| CM-2023-11932816 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TEMP-TOO WARM-QA2 DAILY DINING AREA |  | FM008 |  | 2023-06-28 17:49 | 2023-06-28 18:49 | 2023-06-29 18:49 | 24 | 2023-06-28 17:55 | 2023-06-28 23:00 | 305 | 60 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 17053 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-11978757 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT – DELI DINING AREA |  | FM008 |  | 2023-07-16 17:55 | 2023-07-16 18:55 | 2023-07-17 18:55 | 24 | 2023-07-16 18:00 | 2023-07-16 20:00 | 120 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | Voice Communication
| CM-2023-12013030 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT QA2 DELI DINING AREA |  | FM008 |  | 2023-07-28 17:17 | 2023-07-28 18:17 | 2023-07-29 18:17 | 24 | 2023-07-28 17:25 | 2023-07-28 22:35 | 310 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 68485 | 17053 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | Voice Communication
| CM-2023-12043198 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC NOT WORKING -QA2 DELI DINING |  | FM008 |  | 2023-08-03 23:19 | 2023-08-04 00:19 | 2023-08-05 00:19 | 24 | 2023-08-03 23:25 | 2023-08-03 23:58 | 33 | 33 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17333 | 17053 |  |  | 20960 | Limpaiboon, Ms. Sukanya | N - - - |  | Voice Communication
| CM-2023-12058428 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD MAIN DINING AREA QA2 |  | FM008 |  | 2023-08-07 18:35 | 2023-08-07 19:35 | 2023-08-08 19:35 | 24 | 2023-08-07 18:45 | 2023-08-07 23:30 | 285 | 40 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | 134565 | Mayanja, Mr. Elvis Manga | N - - - |  | Voice Communication
| CM-2023-12063376 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM - DELI OPEN AREA |  | FM008 |  | 2023-08-11 13:36 | 2023-08-11 14:36 | 2023-08-12 14:36 | 24 | 2023-08-11 13:45 | 2023-08-11 15:35 | 110 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 87807 |  |  | 134565 | Mayanja, Mr. Elvis Manga | N - - - |  | Voice Communication
| CM-2023-12429468 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD -QA2 DELI DINING AREA |  | FM008 |  | 2023-11-30 17:38 | 2023-11-30 18:38 | 2023-12-01 18:38 | 24 | 2023-11-30 17:45 | 2023-11-30 18:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 124475 | 87807 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2024-12709323 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD QA3 DELI DINING AREA |  | FM008 |  | 2024-03-09 16:40 | 2024-03-09 17:40 | 2024-03-10 17:40 | 24 | 2024-03-09 16:45 | 2024-03-09 17:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 63360 | Rattanaponmeta, Mr. Paul | N - - - |  | Voice Communication
| CM-2023-11342464 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO COLD - QA2 DELI DINING AREA |  | FM008 |  | 2023-01-03 23:42 | 2023-01-04 00:42 | 2023-01-05 00:42 | 24 | 2023-01-03 23:45 | 2023-01-04 00:30 | 45 | 45 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 83164 | Nalog, Mr. Marco Paulo Lumacad | N - - - |  | Voice Communication
| CM-2023-11819083 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AHU FILTER BLOCKED |  | FM008 |  | 2023-05-24 23:05 | 2023-05-25 00:05 | 2023-05-26 00:05 | 24 | 2023-05-24 23:10 | 2023-05-25 01:00 | 110 | 165 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11932675 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM - QA2 DELI DINING AREA |  | FM008 |  | 2023-06-28 10:07 | 2023-06-28 11:07 | 2023-06-29 11:07 | 24 | 2023-06-28 10:20 | 2023-06-28 14:30 | 250 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-11994789 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM - QA2 SEATING AREA |  | FM008 |  | 2023-07-18 00:13 | 2023-07-18 01:13 | 2023-07-19 01:13 | 24 | 2023-07-18 00:20 | 2023-07-18 01:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 87807 |  |  | 83027 | A K R Kurup, Mr. Sambhu | N - - - |  | Voice Communication
| CM-2023-11998081 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM -DELI DINING AREA |  | FM008 |  | 2023-07-21 23:37 | 2023-07-22 00:37 | 2023-07-23 00:37 | 24 | 2023-07-21 23:45 | 2023-07-22 00:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 95216 | 17053 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2023-12089693 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT – QA2 DELI DINING |  | FM008 |  | 2023-08-15 06:40 | 2023-08-15 07:40 | 2023-08-16 07:40 | 24 | 2023-08-15 06:45 | 2023-08-15 08:00 | 75 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 134565 | Mayanja, Mr. Elvis Manga | N - - - |  | Voice Communication
| CM-2023-12138461 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT MEZZANINE DINING AREA QA2 |  | FM008 |  | 2023-09-01 00:49 | 2023-09-01 01:49 | 2023-09-02 01:49 | 24 | 2023-09-01 00:55 | 2023-09-01 06:00 | 305 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17573 |  |  | 29674 | Tangilan, Ms. Mary Jane Ignacio | N - - - |  | Voice Communication
| CM-2023-12489097 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | ABNORMAL SOUND COMING FROM THE AHU - AHU-A1153-A404 – QA2 THIRD FLOOR |  | FM008 |  | 2023-12-22 08:39 | 2023-12-22 09:39 | 2023-12-23 09:39 | 24 | 2023-12-22 08:45 | 2023-12-22 15:00 | 375 | 825 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 133396 | 87807 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2022-10690171 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM DELI DINING AREA |  | FM008 |  | 2022-05-23 18:35 | 2022-05-23 19:35 | 2022-05-24 19:35 | 24 | 2022-05-23 18:44 | 2022-05-23 20:00 | 76 | 66 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 55709 |  |  | 109304 | Mahajani, Mr. Amit Ravindra | N - - - |  | Voice Communication
| CM-2022-10710317 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC IS HOT - QA2,DELI DINING AREA |  | FM008 |  | 2022-06-01 16:46 | 2022-06-01 17:46 | 2022-06-02 17:46 | 24 | 2022-06-01 16:51 | 2022-06-01 18:30 | 99 | 64 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 39356 | Alde, Ms. Katrina Cuasay | N - - - |  | Voice Communication
| CM-2022-10723282 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2- DELI DINING -AC IS TOO HOT |  | FM008 |  | 2022-06-05 17:00 | 2022-06-05 18:00 | 2022-06-06 18:00 | 24 | 2022-06-05 17:05 | 2022-06-05 18:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 87807 | 17053 |  |  | 65957 | Rocamora, Mr. Owens Tabilog | N - - - |  | Voice Communication
| CM-2022-10747079 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT - DELI DINING AREA LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) |  | FM008 |  | 2022-06-15 12:34 | 2022-06-15 13:34 | 2022-06-16 13:34 | 24 | 2022-06-15 12:44 | 2022-06-15 15:20 | 156 | 64 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2022-10778409 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TEMPERATURE TOO WARM-DELI DINING AREA |  | FM008 |  | 2022-06-23 22:48 | 2022-06-23 23:48 | 2022-06-24 23:48 | 24 | 2022-06-23 22:55 | 2022-06-23 23:30 | 35 | 35 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 82123 | Sharma, Mr. Bobby Mukesh | N - - - |  | Voice Communication
| CM-2022-10818264 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI DINING AC TOO HOT |  | FM008 |  | 2022-07-05 02:34 | 2022-07-05 03:34 | 2022-07-06 03:34 | 24 | 2022-07-05 02:40 | 2022-07-05 04:00 | 80 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 95217 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-10817191 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | A/C IS TOO HOT T4-QA2-01 (DINING) |  | FM008 |  | 2022-07-07 23:28 | 2022-07-08 00:28 | 2022-07-09 00:28 | 24 | 2022-07-07 23:35 | 2022-07-08 01:00 | 85 | 60 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 95217 |  |  | 28329 | Gutierrez, Mr. Ronnie Natac | N - - - |  | Voice Communication
| CM-2022-10861979 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 LOUNGE, DELI DINING – AC TEMPERATURE IS TOO HOT |  | FM008 |  | 2022-07-20 14:32 | 2022-07-20 15:32 | 2022-07-21 15:32 | 24 | 2022-07-20 14:40 | 2022-07-20 16:25 | 105 | 70 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94954 | 95217 |  |  | 83164 | Nalog, Mr. Marco Paulo Lumacad | N - - - |  | Voice Communication
| CM-2022-10863821 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI DINING AREA – AC TOO HOT |  | FM008 |  | 2022-07-22 22:22 | 2022-07-22 23:22 | 2022-07-23 23:22 | 24 | 2022-07-22 22:30 | 2022-07-23 01:00 | 150 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 95217 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2022-10911598 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO WARM - DELI DINING AREA (OTHER AREA TOO) |  | FM008 |  | 2022-08-03 01:19 | 2022-08-03 02:19 | 2022-08-04 02:19 | 24 | 2022-08-03 01:20 | 2022-08-03 04:30 | 190 | 70 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 76858 |  |  | 83022 | Terse, Ms. Vaishali Subhash | N - - - |  | Voice Communication
| CM-2022-10957822 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI DINING AREA – AC IS TOO HOT- - |  | FM008 |  | 2022-08-19 00:32 | 2022-08-19 01:32 | 2022-08-20 01:32 | 24 | 2022-08-19 00:40 | 2022-08-19 01:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94953 | 55709 |  |  | 20960 | Limpaiboon, Ms. Sukanya | N - - - |  | Voice Communication
| CM-2022-11180103 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AHU-A1153-A404 – FILTER IS DIRTY – QA2 LOUNGE, ABOVE T3-QA2-29 |  | FM008 |  | 2022-11-11 01:27 | 2022-11-11 02:27 | 2022-11-12 02:27 | 24 | 2022-11-11 01:35 | 2022-11-11 04:30 | 175 | 175 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11328060 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TO BE REDUCED IN DAILY DINING AREA - AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) |  | FM008 |  | 2022-12-30 11:11 | 2022-12-30 12:11 | 2022-12-31 12:11 | 24 | 2022-12-30 11:20 | 2022-12-30 14:10 | 170 | 53 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 17053 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-10728359 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC NOT WORKING DELI DINING AREA QA2 |  | FM008 |  | 2022-06-08 16:58 | 2022-06-08 17:58 | 2022-06-09 17:58 | 24 | 2022-06-08 17:05 | 2022-06-08 18:45 | 100 | 30 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMPERATURE GAUGE FAULTY | RECTIFIED/REPLACED | 106972 | 87807 |  |  | 52772 | Oudadda, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10774674 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT QA2, DELI DINING AREA |  | FM008 |  | 2022-06-19 18:47 | 2022-06-19 19:47 | 2022-06-20 19:47 | 24 | 2022-06-19 19:00 | 2022-06-19 20:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 87807 |  |  | 109304 | Mahajani, Mr. Amit Ravindra | N - - - |  | Voice Communication
| CM-2022-10796279 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT - QA2 DELI DINING |  | FM008 |  | 2022-06-30 16:24 | 2022-06-30 17:24 | 2022-07-01 17:24 | 24 | 2022-06-30 16:30 | 2022-06-30 20:00 | 210 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 85125 | 95217 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-10817188 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC NOT WORKING -QA2 DELI DINING |  | FM008 |  | 2022-07-07 22:24 | 2022-07-07 23:24 | 2022-07-08 23:24 | 24 | 2022-07-07 22:30 | 2022-07-08 01:00 | 150 | 60 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 95217 |  |  | 63988 | Chua, Ms. Ma. Lilet Angelique Magno | N - - - |  | Voice Communication
| CM-2022-10855130 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | AC TOO HOT IN THE DINING AREA NEAR THE BUSINESS CENTER |  | FM008 |  | 2022-07-19 00:24 | 2022-07-19 01:24 | 2022-07-20 01:24 | 24 | 2022-07-19 00:30 | 2022-07-19 03:10 | 160 | 70 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 95217 |  |  | 116188 | Akram, Ms. Mehnaz | N - - - |  | Voice Communication
| CM-2022-10861799 | ASD-LOU-QA2-AHU001 | AIR HANDLING UNIT-04 | QA2 DELI DINING AC TOO HOT |  | FM008 |  | 2022-07-19 19:02 | 2022-07-19 20:02 | 2022-07-20 20:02 | 24 | 2022-07-19 19:10 | 2022-07-19 23:55 | 285 | 40 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-BUSINESS LOUNGE THIRD FLOOR (QA2) | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 95217 |  |  | 121539 | Panday, Mr. Saurabh Kumar | N - - - |  | Voice Communication
| CM-2022-10694980 | ASD-LOU-VL2-AHU004 | AIR HANDLING UNIT-04 | DP1 FILTER ALARM -AIRSIDE-LOUNGE-VIP LOUNGE GROUND FLOOR (VL1) |  | FM008 |  | 2022-05-28 14:13 | 2022-05-28 15:13 | 2022-05-29 15:13 | 24 | 2022-05-28 14:20 | 2022-05-28 16:00 | 100 | 300 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-VIP LOUNGE GROUND FLOOR (VL1) | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12344300 | ASD-LOU-VL2-AHU004 | AIR HANDLING UNIT-04 | AHU CABIN LAMP FAULTY -T4-09-04 |  | FM008 |  | 2023-11-03 01:50 | 2023-11-03 02:50 | 2023-11-04 02:50 | 24 | 2023-11-03 01:55 | 2023-11-03 03:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-VIP LOUNGE GROUND FLOOR (VL1) | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-11103059 | ASD-LOU-VL2-AHU004 | AIR HANDLING UNIT-04 | TEMPERATURE AND HUMIDITY SENSOR VALUE MISMATCH,AHU-A1157-A407 - T4-24-01 |  | FM008 |  | 2022-10-15 16:18 | 2022-10-15 17:18 | 2022-10-16 17:18 | 24 | 2022-10-15 16:25 | 2022-10-15 17:54 | 89 | 178 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-VIP LOUNGE GROUND FLOOR (VL1) | N | WARNING | THERMOSTAT VALUE MISMATCH | RECTIFIED | 105233 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10046896 | ASD-LOU-VL2-AHU004 | AIR HANDLING UNIT-04 | SUPPLY AIR DUCT INSULATION DAMAGE AHU-A1157-A407 T4-24-0 |  | FM008 |  | 2022-01-12 17:30 | 2022-01-12 18:30 | 2022-01-13 18:30 | 24 | 2022-01-12 17:35 | 2022-01-12 18:50 | 75 | 150 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-LOUNGE-VIP LOUNGE GROUND FLOOR (VL1) | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-10066253 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 – AIR LEAKAGE FROM SUPPLY ACCESS DOOR – T4-08-04 |  | FM008 |  | 2022-01-19 20:33 | 2022-01-19 21:33 | 2022-01-20 21:33 | 24 | 2022-01-19 20:40 | 2022-01-19 22:20 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10612954 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 FILTER DIRTY |  | FM008 |  | 2022-04-30 19:39 | 2022-04-30 20:39 | 2022-05-01 20:39 | 24 | 2022-04-30 19:49 | 2022-04-30 21:30 | 101 | 202 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11041312 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-09-23 00:07 | 2022-09-23 01:07 | 2022-09-24 01:07 | 24 | 2022-09-23 00:16 | 2022-09-23 01:30 | 74 | 222 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11247834 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -T4-08-04 |  | FM008 |  | 2022-12-05 10:01 | 2022-12-05 11:01 | 2022-12-06 11:01 | 24 | 2022-12-05 10:10 | 2022-12-05 17:00 | 410 | 485 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 17053 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2023-12007999 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | EXHAUST GRILL DIRTY - A1110-401 – T2 GL1 07, T2 GL1 10 AND T2 CL1 12 |  | FM008 |  | 2023-07-27 14:37 | 2023-07-27 15:37 | 2023-07-28 15:37 | 24 | 2023-07-27 14:45 | 2023-07-27 18:00 | 195 | 585 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12127749 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | EXHAUST GRILL DIRTY – EX-A1110-401 – ROOM 156,157 AND 158 ALSO 159 |  | FM008 |  | 2023-08-28 14:44 | 2023-08-28 15:44 | 2023-08-29 15:44 | 24 | 2023-08-28 14:50 | 2023-08-28 17:05 | 135 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12463346 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT BEARING NOISY |  | FM008 |  | 2023-12-11 08:40 | 2023-12-11 09:40 | 2023-12-12 09:40 | 24 | 2023-12-11 08:45 | 2023-12-11 12:00 | 195 | 585 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11188859 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1110-401 – T4-08-04 |  | FM008 |  | 2022-11-14 03:07 | 2022-11-14 04:07 | 2022-11-15 04:07 | 24 | 2022-11-14 03:10 | 2022-11-14 05:50 | 160 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-11650557 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-401 – T4-08-04 |  | FM008 |  | 2023-04-11 11:21 | 2023-04-11 12:21 | 2023-04-12 12:21 | 24 | 2023-04-11 11:30 | 2023-04-11 14:45 | 195 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 133396 | 94954 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11842327 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | MOTOR CABLE CONNECTOR DAMAGED -MCC-AHU-A1110-401 |  | FM008 |  | 2023-06-01 14:53 | 2023-06-01 15:53 | 2023-06-02 15:53 | 24 | 2023-06-01 15:00 | 2023-06-01 17:48 | 168 | 241 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 132112 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | E-mail
| CM-2023-11878033 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-401 - T4-08-04 |  | FM008 |  | 2023-06-15 00:04 | 2023-06-15 01:04 | 2023-06-16 01:04 | 24 | 2023-06-15 00:10 | 2023-06-15 03:45 | 215 | 217 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | BMS
| CM-2023-12114281 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1110-401,T4-08-04 |  | FM008 |  | 2023-08-26 08:29 | 2023-08-26 09:29 | 2023-08-27 09:29 | 24 | 2023-08-26 08:35 | 2023-08-26 10:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12685826 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-FILTER DIRTY -T4-08-04 |  | FM008 |  | 2024-02-27 09:41 | 2024-02-27 10:41 | 2024-02-28 10:41 | 24 | 2024-02-27 09:45 | 2024-02-27 15:40 | 355 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-11233428 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 AHU CABIN LAMP NOT WORKING T4-08-04 |  | FM008 |  | 2022-12-02 00:12 | 2022-12-02 01:12 | 2022-12-03 01:12 | 24 | 2022-12-02 00:20 | 2022-12-02 02:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 87807 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11834939 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 030 (TAG NO:AHU-A1110-417)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-05-29 14:08 | 2023-05-29 15:08 | 2023-05-30 15:08 | 24 | 2023-05-29 14:15 | 2023-05-29 16:15 | 120 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 132112 | 87807 |  |  | 10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12365793 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | EXHAUST GRILL DIRTY – ROOM 161 162 AND 163 |  | FM008 |  | 2023-11-08 16:22 | 2023-11-08 17:22 | 2023-11-09 17:22 | 24 | 2023-11-08 16:25 | 2023-11-08 17:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | FAN BLOWER IS DIRTY | CLEANED THE BLOWER | 132112 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12277259 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED |  | FM008 |  | 2023-10-10 18:56 | 2023-10-10 19:56 | 2023-10-11 19:56 | 24 | 2023-10-10 19:00 | 2023-10-10 22:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12287914 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED –(AHU-A1110-401) – T4 08 04 |  | FM008 |  | 2023-10-16 20:11 | 2023-10-16 21:11 | 2023-10-17 21:11 | 24 | 2023-10-16 20:20 | 2023-10-16 23:40 | 200 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12287915 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED – (AHU-A1110-401) – T4 08 04 |  | FM008 |  | 2023-10-16 20:12 | 2023-10-16 21:12 | 2023-10-17 21:12 | 24 | 2023-10-16 20:20 | 2023-10-16 23:50 | 210 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12287916 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1110-401) - T4 08 04 |  | FM008 |  | 2023-10-16 20:14 | 2023-10-16 21:14 | 2023-10-17 21:14 | 24 | 2023-10-16 20:20 | 2023-10-16 22:35 | 135 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12325059 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1110-401 – T4-09-04 |  | FM008 |  | 2023-10-26 07:34 | 2023-10-26 08:34 | 2023-10-27 08:34 | 24 | 2023-10-26 07:40 | 2023-10-26 10:40 | 180 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2024-12614571 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - MEC ROOM T4-08-04 |  | FM008 |  | 2024-02-02 19:32 | 2024-02-02 20:32 | 2024-02-03 20:32 | 24 | 2024-02-02 19:42 | 2024-02-03 00:55 | 313 | 335 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 105233 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-10255433 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401- FILTER DIRTY – T4-08-04 |  | FM008 |  | 2022-03-14 11:06 | 2022-03-14 12:06 | 2022-03-15 12:06 | 24 | 2022-03-14 11:16 | 2022-03-14 14:30 | 194 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10063185 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 – FILTER IS DIRTY – T4-08-04 |  | FM008 |  | 2022-01-18 23:59 | 2022-01-19 00:59 | 2022-01-20 00:59 | 24 | 2022-01-19 00:05 | 2022-01-19 01:15 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10627425 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 – FILTER DIRTY-- |  | FM008 |  | 2022-05-08 09:41 | 2022-05-08 10:41 | 2022-05-09 10:41 | 24 | 2022-05-08 09:50 | 2022-05-08 12:00 | 130 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10877175 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-07-27 02:04 | 2022-07-27 03:04 | 2022-07-28 03:04 | 24 | 2022-07-27 02:05 | 2022-07-27 04:15 | 130 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95216 | 87807 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2022-11024227 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 – DP3 FILTER ALARM – T4-08-04 |  | FM008 |  | 2022-09-16 00:20 | 2022-09-16 01:20 | 2022-09-17 01:20 | 24 | 2022-09-16 00:30 | 2022-09-16 02:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11078508 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1110-401) |  | FM008 |  | 2022-10-05 13:34 | 2022-10-05 14:34 | 2022-10-06 14:34 | 24 | 2022-10-05 13:40 | 2022-10-05 18:20 | 280 | 285 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10085011 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AIR LEAKING FROM ACCESS DOOR -AIR HANDLING UNIT 014 (TAG NO:AHU-A1110-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-01-29 11:19 | 2022-01-29 12:19 | 2022-01-30 12:19 | 24 | 2022-01-29 11:29 | 2022-01-29 12:30 | 61 | 183 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 55709 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2022-10121300 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | AHU-A1110-401 DP3 FILTER ALARM |  | FM008 |  | 2022-02-09 19:08 | 2022-02-09 20:08 | 2022-02-10 20:08 | 24 | 2022-02-09 19:15 | 2022-02-09 21:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 68485 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10153112 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED -T4-08-04 |  | FM008 |  | 2022-02-18 09:19 | 2022-02-18 10:19 | 2022-02-19 10:19 | 24 | 2022-02-18 09:25 | 2022-02-18 11:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2022-10772208 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | CHILL WATERLINE PAINT FADED AHU-A1110-401- T4-08-04 |  | FM008 |  | 2022-06-22 10:19 | 2022-06-22 11:19 | 2022-06-23 11:19 | 24 | 2022-06-22 10:25 | 2022-06-22 12:30 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 87807 | 87807 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2022-10781979 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AIR HANDLING UNIT 014 (TAG NO:AHU-A1110-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 - |  | FM008 |  | 2022-06-28 02:02 | 2022-06-28 03:02 | 2022-06-29 03:02 | 24 | 2022-06-28 02:10 | 2022-06-28 03:45 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11430334 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY-(AHU-A1110-401)IRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-02-08 07:24 | 2023-02-08 08:24 | 2023-02-09 08:24 | 24 | 2023-02-08 07:34 | 2023-02-08 10:15 | 161 | 201 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12282157 | ASD-MTB-FOF008-AHU014 | AIR HANDLING UNIT-05 | RELEIFE MOTOR ABNORMAL NOISY - AIR HANDLING UNIT 014 (TAG NO:AHU-A1110-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-10-15 00:20 | 2023-10-15 01:20 | 2023-10-16 01:20 | 24 | 2023-10-15 00:25 | 2023-10-15 03:10 | 165 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 119320 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10117971 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM T4-08-04 |  | FM008 |  | 2022-02-07 07:26 | 2022-02-07 08:26 | 2022-02-08 08:26 | 24 | 2022-02-07 07:30 | 2022-02-07 08:30 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 106972 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10364352 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403 DP3 FILTER ALARM |  | FM008 |  | 2022-04-15 12:02 | 2022-04-15 13:02 | 2022-04-16 13:02 | 24 | 2022-04-15 12:10 | 2022-04-15 15:20 | 190 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10573759 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN INFORMATION COUNTER DEPARTURE |  | FM008 |  | 2022-04-18 21:56 | 2022-04-18 22:56 | 2022-04-19 22:56 | 24 | 2022-04-18 22:05 | 2022-04-18 23:55 | 110 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 68543 | Shaikh, Mr. Zillur Rahman Mujeeb Ur Rahman | N - - - |  | Voice Communication
| CM-2022-10621298 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | CORRIDOR AC NOT WORKING FROM ROOM 155 TO 200 |  | FM008 |  | 2022-05-06 11:20 | 2022-05-06 12:20 | 2022-05-07 12:20 | 24 | 2022-05-06 11:26 | 2022-05-06 12:20 | 54 | 54 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | 115535 | Hossain, Mr. Md Parveg | N - - - |  | Voice Communication
| CM-2022-10623501 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AC NOT WORKING IN THE CORRIDOR FROM ROOM NO 180-200-CONTACT THE AC NOT WORKING IN THE CORRIDOR FROM ROOM NO 180-200-CONTACT THE REQUESTOR WHILE PROCEEDING FOR REPAIR |  | FM008 |  | 2022-05-06 22:01 | 2022-05-06 23:01 | 2022-05-07 23:01 | 24 | 2022-05-06 22:10 | 2022-05-06 23:55 | 105 | 25 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 95836 | Dabas, Mr. Rohit | N - - - |  | Voice Communication
| CM-2022-10620102 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – T4-08-04 |  | FM008 |  | 2022-05-08 06:54 | 2022-05-08 07:54 | 2022-05-09 07:54 | 24 | 2022-05-08 07:00 | 2022-05-08 08:00 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11060505 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED -T4-08-04 |  | FM008 |  | 2022-09-27 03:33 | 2022-09-27 04:33 | 2022-09-28 04:33 | 24 | 2022-09-27 03:40 | 2022-09-27 05:10 | 90 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM9671 | Karunagoda Mudalige, Mr. Kasun Lakmal | N - - - |  | Voice Communication
| CM-2022-11179192 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AC NOT WORKING 149 CORRIDOR AREA |  | FM008 |  | 2022-11-10 01:39 | 2022-11-10 02:39 | 2022-11-11 02:39 | 24 | 2022-11-10 01:45 | 2022-11-10 03:20 | 95 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | 102074 | Ahmmed, Mr. Rasel | N - - - |  | Voice Communication
| CM-2023-11364345 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403-DP3-FILTER DIRTY - :MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-01-12 11:32 | 2023-01-12 12:32 | 2023-01-13 12:32 | 24 | 2023-01-12 11:40 | 2023-01-12 13:40 | 120 | 75 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 55709 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11364346 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | (AHU-A1110-403)-BELT DAMAGE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-01-12 11:38 | 2023-01-12 12:38 | 2023-01-13 12:38 | 24 | 2023-01-12 11:45 | 2023-01-12 13:05 | 80 | 85 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11383289 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | BURNING SMELL - CORRIDOR AREA NEAR ROOM 195 |  | FM008 |  | 2023-01-18 10:29 | 2023-01-18 11:29 | 2023-01-19 11:29 | 24 | 2023-01-18 10:35 | 2023-01-18 15:30 | 295 | 305 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 121959 | 17053 |  |  | C07165 | JOSEPH | N - - - |  | Voice Communication
| CM-2023-11550957 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | BELT DAMAGED – T4-08-04 |  | FM008 |  | 2023-03-12 01:50 | 2023-03-12 02:50 | 2023-03-13 02:50 | 24 | 2023-03-12 02:00 | 2023-03-12 03:30 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11648729 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | SUPPLY BELT IS DAMAGED |  | FM008 |  | 2023-04-11 11:24 | 2023-04-11 12:24 | 2023-04-12 12:24 | 24 | 2023-04-11 11:30 | 2023-04-11 12:45 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | BMS
| CM-2023-11901762 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-08-04 |  | FM008 |  | 2023-06-21 21:01 | 2023-06-21 22:01 | 2023-06-22 22:01 | 24 | 2023-06-21 21:10 | 2023-06-21 23:10 | 120 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11930932 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-403- T4 08 04 |  | FM008 |  | 2023-06-26 18:58 | 2023-06-26 19:58 | 2023-06-27 19:58 | 24 | 2023-06-26 19:05 | 2023-06-26 20:05 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12035125 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AC VENT DIRTY - T3-08-07 |  | FM008 |  | 2023-07-31 10:31 | 2023-07-31 11:31 | 2023-08-01 11:31 | 24 | 2023-07-31 10:40 | 2023-07-31 13:10 | 150 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2023-12186726 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403 FILTER DIRTY T4-08-04 |  | FM008 |  | 2023-09-16 00:07 | 2023-09-16 01:07 | 2023-09-17 01:07 | 24 | 2023-09-16 00:15 | 2023-09-16 05:20 | 305 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11007590 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403- SUPPLY FLOW LOW ALARM- T4-08-04 |  | FM008 |  | 2022-09-09 07:00 | 2022-09-09 08:00 | 2022-09-10 08:00 | 24 | 2022-09-09 07:08 | 2022-09-09 09:55 | 167 | 127 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11517114 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | V-BELT DAMAGED-T4-08-04-:AHU-A1110-403-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-03-06 07:10 | 2023-03-06 08:10 | 2023-03-07 08:10 | 24 | 2023-03-06 07:20 | 2023-03-06 10:45 | 205 | 145 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 87807 |  |  | FM5381 | Thomas, Mr. Joseph | N - - - |  | Voice Communication
| CM-2023-11557719 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-03-13 00:25 | 2023-03-13 01:25 | 2023-03-14 01:25 | 24 | 2023-03-13 00:30 | 2023-03-13 02:05 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11895940 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | SUPPPLY BELT DAMAGED -AIR HANDLING UNIT 016 (TAG NO:AHU-A1110-403)- |  | FM008 |  | 2023-06-19 01:04 | 2023-06-19 02:04 | 2023-06-20 02:04 | 24 | 2023-06-19 01:10 | 2023-06-19 04:15 | 185 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12063922 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403-FILTER DIRTY |  | FM008 |  | 2023-08-08 11:35 | 2023-08-08 12:35 | 2023-08-09 12:35 | 24 | 2023-08-08 11:40 | 2023-08-08 12:40 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12111517 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AC VENT DIRTY AHU-A1110-403 T3-06-34 HOTEL CORRIDOR WEST SIDE |  | FM008 |  | 2023-08-22 11:19 | 2023-08-22 12:19 | 2023-08-23 12:19 | 24 | 2023-08-22 11:25 | 2023-08-22 15:30 | 245 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12276962 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1110-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-10-09 19:00 | 2023-10-09 20:00 | 2023-10-10 20:00 | 24 | 2023-10-09 19:05 | 2023-10-09 20:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12275529 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED -AIR HANDLING UNIT 016 (TAG NO:AHU-A1110-403) |  | FM008 |  | 2023-10-09 19:01 | 2023-10-09 20:01 | 2023-10-10 20:01 | 24 | 2023-10-09 19:06 | 2023-10-09 22:40 | 214 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12652441 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-403 – T4-08-04 |  | FM008 |  | 2024-02-15 14:56 | 2024-02-15 15:56 | 2024-02-16 15:56 | 24 | 2024-02-15 15:00 | 2024-02-15 22:00 | 420 | 361 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11039935 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-09-23 01:53 | 2022-09-23 02:53 | 2022-09-24 02:53 | 24 | 2022-09-23 02:00 | 2022-09-23 03:15 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11067380 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-08-04 |  | FM008 |  | 2022-10-01 11:46 | 2022-10-01 12:46 | 2022-10-02 12:46 | 24 | 2022-10-01 11:50 | 2022-10-01 15:30 | 220 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11196106 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | CORRIDOR AREA AC NOT WORKING NEAR HOTEL ROOM 189 |  | FM008 |  | 2022-11-17 08:19 | 2022-11-17 09:19 | 2022-11-18 09:19 | 24 | 2022-11-17 08:25 | 2022-11-17 09:10 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 87807 |  |  | 129378 | Mohan, Mr. Shamal | N - - - |  | Voice Communication
| CM-2022-11216995 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AC NOT WORKING IN THE HOTEL ROOM CORRIDOR - ROOM NO 149 TO ROOM NO 200 |  | FM008 |  | 2022-11-26 07:01 | 2022-11-26 08:01 | 2022-11-27 08:01 | 24 | 2022-11-26 07:10 | 2022-11-26 08:00 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 87807 |  |  | 122305 | Shankar, Mr. Sai | N - - - |  | Voice Communication
| CM-2022-11232693 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-12-01 00:09 | 2022-12-01 01:09 | 2022-12-02 01:09 | 24 | 2022-12-01 00:15 | 2022-12-01 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11971343 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2023-07-10 18:53 | 2023-07-10 19:53 | 2023-07-11 19:53 | 24 | 2023-07-10 19:00 | 2023-07-10 20:00 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11971344 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU BELT IS DAMAGED |  | FM008 |  | 2023-07-10 18:54 | 2023-07-10 19:54 | 2023-07-11 19:54 | 24 | 2023-07-10 19:02 | 2023-07-10 21:35 | 153 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12159419 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403 SUPPLY V-BELT DAMAGED T4-08-04 |  | FM008 |  | 2023-09-10 00:03 | 2023-09-10 01:03 | 2023-09-11 01:03 | 24 | 2023-09-10 00:05 | 2023-09-10 03:40 | 215 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12849876 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 016 (TAG NO:AHU-A1110-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2024-04-24 14:14 | 2024-04-24 15:14 | 2024-04-25 15:14 | 24 | 2024-04-24 14:20 | 2024-04-24 21:02 | 402 | 126 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12233364 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH FAULTY |  | FM008 |  | 2023-10-01 02:32 | 2023-10-01 03:32 | 2023-10-02 03:32 | 24 | 2023-10-01 02:40 | 2023-10-01 05:30 | 170 | 340 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95216 | 87807 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2024-12713325 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | CHILLED WATER VALVE LEAKING V1-AHU-A1110-403 IN THE MECHANICAL AREA |  | FM008 |  | 2024-03-09 21:53 | 2024-03-09 22:53 | 2024-03-10 22:53 | 24 | 2024-03-09 22:03 | 2024-03-09 23:03 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | WATER LEAKAGE | REPLACED/REPAIRED | 106914 | 17053 |  |  | ALNASIR3884 | BRIAN | N - - - |  | Voice Communication
| CM-2022-10120841 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED AHU-A1110-403 |  | FM008 |  | 2022-02-08 16:36 | 2022-02-08 17:36 | 2022-02-09 17:36 | 24 | 2022-02-08 16:45 | 2022-02-08 18:14 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10063186 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403 – FILTER IS DIRTY – T4-08-04 |  | FM008 |  | 2022-01-19 00:01 | 2022-01-19 01:01 | 2022-01-20 01:01 | 24 | 2022-01-19 00:10 | 2022-01-19 02:20 | 130 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10665293 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403 - V BELT DAMAGED |  | FM008 |  | 2022-05-15 10:47 | 2022-05-15 11:47 | 2022-05-16 11:47 | 24 | 2022-05-15 10:55 | 2022-05-15 14:40 | 225 | 145 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17053 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10674872 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-21 08:55 | 2022-05-21 09:55 | 2022-05-22 09:55 | 24 | 2022-05-21 09:05 | 2022-05-21 11:35 | 150 | 155 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10710928 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS |  | FM008 |  | 2022-05-31 17:45 | 2022-05-31 18:45 | 2022-06-01 18:45 | 24 | 2022-05-31 17:50 | 2022-05-31 20:00 | 130 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10734862 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - AHU-A1110-403 - T4-08-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB407.AHU403.SYSALM.DP3 / |  | FM008 |  | 2022-06-11 14:15 | 2022-06-11 15:15 | 2022-06-12 15:15 | 24 | 2022-06-11 14:25 | 2022-06-11 16:35 | 130 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - |  | BMS
| CM-2022-10128585 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403 FILTER DIRTY |  | FM008 |  | 2022-02-10 21:33 | 2022-02-10 22:33 | 2022-02-11 22:33 | 24 | 2022-02-10 21:40 | 2022-02-10 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10153113 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED - T4-08-04 |  | FM008 |  | 2022-02-18 09:20 | 2022-02-18 10:20 | 2022-02-19 10:20 | 24 | 2022-02-18 09:30 | 2022-02-18 10:45 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2022-10617033 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AC NOT WORKING IN WEST WING CORRIDOR – ROOM NO 149 TO ROOM NO 200 |  | FM008 |  | 2022-05-05 22:05 | 2022-05-05 23:05 | 2022-05-06 23:05 | 24 | 2022-05-05 22:14 | 2022-05-05 23:55 | 101 | 61 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 17053 |  |  | 95836 | Dabas, Mr. Rohit | N - - - |  | Voice Communication
| CM-2022-10790831 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-30 00:09 | 2022-06-30 01:09 | 2022-07-01 01:09 | 24 | 2022-06-30 00:15 | 2022-06-30 01:35 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-11549976 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | ROOM 155 – 200 CORRIDOR AC IS TOO HOT / NOT FUNCTIONING- - |  | FM008 |  | 2023-03-12 10:07 | 2023-03-12 11:07 | 2023-03-13 11:07 | 24 | 2023-03-12 10:15 | 2023-03-12 11:50 | 95 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94953 | 87807 |  |  | 115535 | Hossain, Mr. Md Parveg | N - - - |  | Voice Communication
| CM-2023-11632566 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | AHU-A1110-403-CABIN LAMP NOT WORKING-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-04-09 12:23 | 2023-04-09 13:23 | 2023-04-10 13:23 | 24 | 2023-04-09 12:32 | 2023-04-09 14:02 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 77406 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12257485 | ASD-MTB-FOF008-AHU016 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-403 – T4-08-04 |  | FM008 |  | 2023-10-08 00:25 | 2023-10-08 01:25 | 2023-10-09 01:25 | 24 | 2023-10-08 00:30 | 2023-10-08 05:15 | 285 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10125211 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 – DP1 FILTER ALARM – T4-08-04 |  | FM008 |  | 2022-02-13 00:14 | 2022-02-13 01:14 | 2022-02-14 01:14 | 24 | 2022-02-13 00:20 | 2022-02-13 02:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94954 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10262523 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | FILTER DIRTY- T4-08-04 |  | FM008 |  | 2022-03-19 19:01 | 2022-03-19 20:01 | 2022-03-20 20:01 | 24 | 2022-03-19 19:10 | 2022-03-19 20:30 | 80 | 240 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2022-10750236 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-405 – T4-08-04 |  | FM008 |  | 2022-06-19 07:06 | 2022-06-19 08:06 | 2022-06-20 08:06 | 24 | 2022-06-19 07:10 | 2022-06-19 09:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10793220 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405-DP 2 FILTER ALARM – T4-08-04 |  | FM008 |  | 2022-07-03 10:44 | 2022-07-03 11:44 | 2022-07-04 11:44 | 24 | 2022-07-03 10:50 | 2022-07-03 16:30 | 340 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11059927 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED -T4-08-04 |  | FM008 |  | 2022-09-27 00:05 | 2022-09-27 01:05 | 2022-09-28 01:05 | 24 | 2022-09-27 00:10 | 2022-09-27 01:45 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2022-11270533 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED (AHU-439, AHU-435 & AHU-419) - AHU-A1110-405 – T4-08-04 |  | FM008 |  | 2022-12-13 12:58 | 2022-12-13 13:58 | 2022-12-14 13:58 | 24 | 2022-12-13 13:05 | 2022-12-13 16:00 | 175 | 660 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11654644 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-405 -T4-08-04 |  | FM008 |  | 2023-04-12 08:34 | 2023-04-12 09:34 | 2023-04-13 09:34 | 24 | 2023-04-12 08:40 | 2023-04-12 10:45 | 125 | 305 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12067946 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM -FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-08-13 04:34 | 2023-08-13 05:34 | 2023-08-14 05:34 | 24 | 2023-08-13 04:40 | 2023-08-13 05:50 | 70 | 210 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12115739 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | CABLE LAMP FAULTY - AHU-A1110-405 – T4-08-04 |  | FM008 |  | 2023-08-25 19:09 | 2023-08-25 20:09 | 2023-08-26 20:09 | 24 | 2023-08-25 19:15 | 2023-08-26 01:55 | 400 | 345 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 133396 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-12278770 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 SUPPLY FAN BELT DAMAGED |  | FM008 |  | 2023-10-11 00:03 | 2023-10-11 01:03 | 2023-10-12 01:03 | 24 | 2023-10-11 00:10 | 2023-10-11 03:35 | 205 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12278771 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 RELIEF BELT DAMAGED |  | FM008 |  | 2023-10-11 00:04 | 2023-10-11 01:04 | 2023-10-12 01:04 | 24 | 2023-10-11 00:10 | 2023-10-11 05:10 | 300 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12278772 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 FILTER DIRTY |  | FM008 |  | 2023-10-11 00:04 | 2023-10-11 01:04 | 2023-10-12 01:04 | 24 | 2023-10-11 00:10 | 2023-10-11 04:10 | 240 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12326088 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | SUPPLY MOTOR AND BLOWER BASE SPRING IS RUSTED |  | FM008 |  | 2023-10-29 00:03 | 2023-10-29 01:03 | 2023-10-30 01:03 | 24 | 2023-10-29 00:10 | 2023-10-29 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | RETURN FAN MOTOR BURNT | REPLACED THE MOTOR | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12485206 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | FILTER DIRTY - AIR HANDLING UNIT 018 (TAG NO:AHU-A1110-405)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-12-19 00:01 | 2023-12-19 01:01 | 2023-12-20 01:01 | 24 | 2023-12-19 00:10 | 2023-12-19 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11090534 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405- COOLING COIL DIRTY – T4-08-04- |  | FM008 |  | 2022-10-09 22:18 | 2022-10-09 23:18 | 2022-10-10 23:18 | 24 | 2022-10-09 22:25 | 2022-10-10 01:00 | 155 | 310 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 95217 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11101518 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU INSIDE LAMP NOT WORKING AHU-A1110-405 |  | FM008 |  | 2022-10-13 16:46 | 2022-10-13 17:46 | 2022-10-14 17:46 | 24 | 2022-10-13 16:55 | 2022-10-13 18:24 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11022226 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 FILTER ALARM T4-08-04 |  | FM008 |  | 2022-09-14 00:13 | 2022-09-14 01:13 | 2022-09-15 01:13 | 24 | 2022-09-14 00:23 | 2022-09-14 01:53 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11101296 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | BELT MOTOR IS NOISY |  | FM008 |  | 2022-10-12 19:04 | 2022-10-12 20:04 | 2022-10-13 20:04 | 24 | 2022-10-12 19:10 | 2022-10-12 23:55 | 285 | 855 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11273376 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 DP1,DP2,DP3 FILTER DIRTY |  | FM008 |  | 2022-12-16 08:21 | 2022-12-16 09:21 | 2022-12-17 09:21 | 24 | 2022-12-16 08:30 | 2022-12-16 11:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11822322 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 FILTER IS DIRTY |  | FM008 |  | 2023-05-22 10:48 | 2023-05-22 11:48 | 2023-05-23 11:48 | 24 | 2023-05-22 10:52 | 2023-05-22 12:42 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12278505 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | RELIEF MOTOR BASE PLATE DAMAGED - AHU-A1110-405 – T4-08-04 |  | FM008 |  | 2023-10-12 08:46 | 2023-10-12 09:46 | 2023-10-13 09:46 | 24 | 2023-10-12 08:55 | 2023-10-12 13:00 | 245 | 335 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106973 | 87807 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2024-12632165 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AC TOO HOT, ARRIVAL IMMIGRATION ALL COUNTER AREA |  | FM008 |  | 2024-02-09 16:48 | 2024-02-09 17:48 | 2024-02-10 17:48 | 24 | 2024-02-09 16:55 | 2024-02-09 18:35 | 100 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 124475 | 17053 |  |  | MOI | ABDULLA | N - - - |  | Voice Communication
| CM-2024-12613965 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-405 – T4-08-04 |  | FM008 |  | 2024-02-01 14:35 | 2024-02-01 15:35 | 2024-02-02 15:35 | 24 | 2024-02-01 14:45 | 2024-02-01 17:40 | 175 | 230 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106973 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2023-12275556 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY FOR AHU-A1110-405 -T4-08-04 |  | FM008 |  | 2023-10-10 01:36 | 2023-10-10 02:36 | 2023-10-11 02:36 | 24 | 2023-10-10 01:40 | 2023-10-10 04:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 87807 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2023-12347254 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | BLOWER PAINT FADED - AIR HANDLING UNIT 018 (TAG NO:AHU-A1110-405)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 - TG-08-04 |  | FM008 |  | 2023-11-05 07:18 | 2023-11-05 08:18 | 2023-11-06 08:18 | 24 | 2023-11-05 07:25 | 2023-11-05 09:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 119320 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2024-12781121 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ASD-MTB-FOF008-AHU018 AHU-A1110-405 AIR HANDLING UNIT 018 (TAG NO:AHU-A1110-405)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB405.AHU4 |  | FM008 |  | 2024-03-31 14:12 | 2024-03-31 15:12 | 2024-04-01 15:12 | 24 | 2024-03-31 14:20 | 2024-03-31 18:30 | 250 | 350 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10044440 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-01-12 18:34 | 2022-01-12 19:34 | 2022-01-13 19:34 | 24 | 2022-01-12 18:44 | 2022-01-12 20:00 | 76 | 186 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10071274 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405-FILTER DIRTY |  | FM008 |  | 2022-01-22 00:28 | 2022-01-22 01:28 | 2022-01-23 01:28 | 24 | 2022-01-22 00:35 | 2022-01-22 02:05 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10125176 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT LOOSE -AHU-A1110-405)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-02-12 22:38 | 2022-02-12 23:38 | 2022-02-13 23:38 | 24 | 2022-02-12 22:45 | 2022-02-12 23:55 | 70 | 210 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 55709 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-9950897 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AC IS TOO HOT ARRIVAL IMMIGRATION |  | FM008 |  | 2022-01-01 23:11 | 2022-01-02 00:11 | 2022-01-03 00:11 | 24 | 2022-01-01 23:20 | 2022-01-01 23:50 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | MOI | ABDUL AZIZ | N - - - |  | Voice Communication
| CM-2022-10147478 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 DRAIN LINE BLOCKED |  | FM008 |  | 2022-02-19 05:33 | 2022-02-19 06:33 | 2022-02-20 06:33 | 24 | 2022-02-19 05:36 | 2022-02-19 06:30 | 54 | 108 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 55709 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10567870 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-405 T4-08-04 |  | FM008 |  | 2022-04-21 19:12 | 2022-04-21 20:12 | 2022-04-22 20:12 | 24 | 2022-04-21 19:21 | 2022-04-21 22:05 | 164 | 229 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11024228 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 – RELIEF FAN BELT IS DAMAGED – T4-08-04 |  | FM008 |  | 2022-09-16 00:22 | 2022-09-16 01:22 | 2022-09-17 01:22 | 24 | 2022-09-16 00:31 | 2022-09-16 03:40 | 189 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11043293 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405- DP1 FILTER DIRTY - T4-08-04 |  | FM008 |  | 2022-09-25 00:24 | 2022-09-25 01:24 | 2022-09-26 01:24 | 24 | 2022-09-25 00:30 | 2022-09-25 02:25 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11297178 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-405 – T4-08-04 |  | FM008 |  | 2022-12-20 07:12 | 2022-12-20 08:12 | 2022-12-21 08:12 | 24 | 2022-12-20 07:20 | 2022-12-20 09:30 | 130 | 260 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11656457 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | HR WHEEL MOTOR FELIBLE CONNECTOR IS DAMAGED |  | FM008 |  | 2023-04-12 14:11 | 2023-04-12 15:11 | 2023-04-13 15:11 | 24 | 2023-04-12 14:20 | 2023-04-12 17:23 | 183 | 181 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11973741 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405-FILTER DIRTY T4-08-04 |  | FM008 |  | 2023-07-15 00:07 | 2023-07-15 01:07 | 2023-07-16 01:07 | 24 | 2023-07-15 00:14 | 2023-07-15 04:20 | 246 | 247 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10364613 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AC TOO COLD -ARIVAL IMMIGRATIONS IN CUSTOMS ALL AREA |  | FM008 |  | 2022-04-17 04:01 | 2022-04-17 05:01 | 2022-04-18 05:01 | 24 | 2022-04-17 04:10 | 2022-04-17 05:00 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | CT13756 | JAMES | N - - - |  | Voice Communication
| CM-2023-11430333 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - (AHU-A1110-405) - -AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-02-08 07:23 | 2023-02-08 08:23 | 2023-02-09 08:23 | 24 | 2023-02-08 07:30 | 2023-02-08 09:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12165566 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED |  | FM008 |  | 2023-09-09 00:02 | 2023-09-09 01:02 | 2023-09-10 01:02 | 24 | 2023-09-09 00:06 | 2023-09-09 01:36 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12280225 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | ABNORMAL NOISE FROM UNIT-AIR HANDLING UNIT 018 (TAG NO:AHU-A1110-405)-T4-08-04 |  | FM008 |  | 2023-10-14 08:44 | 2023-10-14 09:44 | 2023-10-15 09:44 | 24 | 2023-10-14 08:50 | 2023-10-14 12:45 | 235 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2024-12777236 | ASD-MTB-FOF008-AHU018 | AIR HANDLING UNIT-05 | AHU-A1110-405 SUPPLY BELT DAMAGED -T4-08-04 |  | FM008 |  | 2024-03-30 10:47 | 2024-03-30 11:47 | 2024-03-31 11:47 | 24 | 2024-03-30 10:55 | 2024-03-30 12:30 | 95 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2022-10125217 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU-A1110-407 – DP1 FILTER ALARM – T4-08-04 |  | FM008 |  | 2022-02-13 00:20 | 2022-02-13 01:20 | 2022-02-14 01:20 | 24 | 2022-02-13 00:30 | 2022-02-13 02:30 | 120 | 120 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11878775 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS T4-08-04 |  | FM008 |  | 2023-06-13 22:43 | 2023-06-13 23:43 | 2023-06-14 23:43 | 24 | 2023-06-13 22:50 | 2023-06-13 23:20 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12159143 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | MOTOR AND BLOWER NOISY - AHU-A1110-407 – T4-08-04 |  | FM008 |  | 2023-09-08 14:00 | 2023-09-08 15:00 | 2023-09-09 15:00 | 24 | 2023-09-08 14:05 | 2023-09-08 18:35 | 270 | 810 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 133396 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12303745 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED - AHU-A1110-407 - T4-08-04 |  | FM008 |  | 2023-10-21 00:34 | 2023-10-21 01:34 | 2023-10-22 01:34 | 24 | 2023-10-21 00:40 | 2023-10-21 05:15 | 275 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10959214 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1110-407 - T4-08-04 |  | FM008 |  | 2022-08-22 13:42 | 2022-08-22 14:42 | 2022-08-23 14:42 | 24 | 2022-08-22 13:50 | 2022-08-22 18:00 | 250 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 124475 | 55709 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11028062 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM-AHU-A1110-407)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-09-17 00:12 | 2022-09-17 01:12 | 2022-09-18 01:12 | 24 | 2022-09-17 00:20 | 2022-09-17 01:55 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11480016 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM, AHU-A1110-407 , T4-08-04 |  | FM008 |  | 2023-02-24 07:01 | 2023-02-24 08:01 | 2023-02-25 08:01 | 24 | 2023-02-24 07:10 | 2023-02-24 08:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11557718 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | RETURN V-BELT IS DAMAGED |  | FM008 |  | 2023-03-13 00:24 | 2023-03-13 01:24 | 2023-03-14 01:24 | 24 | 2023-03-13 00:30 | 2023-03-13 02:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12064213 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU-A1110-407-RELIEF BELT DAMAGED |  | FM008 |  | 2023-08-09 13:51 | 2023-08-09 14:51 | 2023-08-10 14:51 | 24 | 2023-08-09 14:00 | 2023-08-09 17:20 | 200 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95217 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12341145 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | RETURN FAN BELT DAMAGED, AHU-A1110-407, T4-08-04 |  | FM008 |  | 2023-11-01 00:20 | 2023-11-01 01:20 | 2023-11-02 01:20 | 24 | 2023-11-01 00:25 | 2023-11-01 04:45 | 260 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11095817 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU-A1110-407 – T4-08-04- COOLING COIL DIRTY |  | FM008 |  | 2022-10-11 03:24 | 2022-10-11 04:24 | 2022-10-12 04:24 | 24 | 2022-10-11 03:30 | 2022-10-11 06:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17154 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-11836335 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB407.AHU407.SYSALM.DP1 / T4-08-04 |  | FM008 |  | 2023-05-29 09:01 | 2023-05-29 10:01 | 2023-05-30 10:01 | 24 | 2023-05-29 09:07 | 2023-05-29 12:10 | 183 | 187 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | Y - - - |  | BMS
| CM-2023-11888147 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARM - AHU-A1110-407 – T4 08 04 |  | FM008 |  | 2023-06-17 08:33 | 2023-06-17 09:33 | 2023-06-18 09:33 | 24 | 2023-06-17 08:40 | 2023-06-17 10:00 | 80 | 240 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12137395 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB407.AHU407.SYSALM.DP3 / /MECHANICAL ROOM T4-08-04 *TESTING ON GOING BY MATAR CONTROLS TEAM Thu 8/31/2023 2:04 PM* |  | FM008 |  | 2023-08-31 13:24 | 2023-08-31 14:24 | 2023-09-01 14:24 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | FOURTH FLOOR AREA 008 | N | DIRTY |  |  | 105233 | 94954 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - | REQUESTED BY REQUESTER | BMS
| CM-2024-12570867 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED – T4-08-04 |  | FM008 |  | 2024-01-18 00:19 | 2024-01-18 01:19 | 2024-01-19 01:19 | 24 | 2024-01-18 00:25 | 2024-01-18 03:10 | 165 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10071275 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU-A1110-407-FILTER DIRTY |  | FM008 |  | 2022-01-22 00:30 | 2022-01-22 01:30 | 2022-01-23 01:30 | 24 | 2022-01-22 00:35 | 2022-01-22 03:40 | 185 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10067403 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM SUPPLY ACCESS DOOR |  | FM008 |  | 2022-01-21 00:21 | 2022-01-21 01:21 | 2022-01-22 01:21 | 24 | 2022-01-21 00:25 | 2022-01-21 02:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 68060 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | BMS
| CM-2022-11095980 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING -- AHU-A1110-407 T4-08-04 |  | FM008 |  | 2022-10-12 00:14 | 2022-10-12 01:14 | 2022-10-13 01:14 | 24 | 2022-10-12 00:20 | 2022-10-12 02:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10568998 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU-A1110-407 T4-08-04 FILTER DIRTY |  | FM008 |  | 2022-04-22 19:10 | 2022-04-22 20:10 | 2022-04-23 20:10 | 24 | 2022-04-22 19:19 | 2022-04-22 23:10 | 231 | 230 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12132041 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU DP3 FILTER ALARM - T4-08-04 |  | FM008 |  | 2023-08-29 11:11 | 2023-08-29 12:11 | 2023-08-30 12:11 | 24 | 2023-08-29 11:15 | 2023-08-29 15:40 | 265 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17053 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-12277336 | ASD-MTB-FOF008-AHU020 | AIR HANDLING UNIT-05 | AHU LIGHTING SWITCH NOT WORKING |  | FM008 |  | 2023-10-11 01:08 | 2023-10-11 02:08 | 2023-10-12 02:08 | 24 | 2023-10-11 01:15 | 2023-10-11 04:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10121415 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | AHU-A1110-415 FILTER DIRTY |  | FM008 |  | 2022-02-10 18:55 | 2022-02-10 19:55 | 2022-02-11 19:55 | 24 | 2022-02-10 19:04 | 2022-02-10 21:04 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10786487 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | AHU DP3 FILTER ALARM - T4-08-04 |  | FM008 |  | 2022-06-26 22:12 | 2022-06-26 23:12 | 2022-06-27 23:12 | 24 | 2022-06-26 22:20 | 2022-06-26 23:55 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17053 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10789669 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-08-04 |  | FM008 |  | 2022-06-28 13:40 | 2022-06-28 14:40 | 2022-06-29 14:40 | 24 | 2022-06-28 13:49 | 2022-06-28 17:30 | 221 | 206 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11112406 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED AHU-A1110-415 |  | FM008 |  | 2022-10-18 13:04 | 2022-10-18 14:04 | 2022-10-19 14:04 | 24 | 2022-10-18 13:10 | 2022-10-18 18:40 | 330 | 290 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11654841 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | ABNORMAL NOISE COMING FROM SUPPLY BLOWER SIDE – T4-08-04 |  | FM008 |  | 2023-04-13 03:03 | 2023-04-13 04:03 | 2023-04-14 04:03 | 24 | 2023-04-13 03:10 | 2023-04-13 06:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11004827 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | AHU-A1110-415- CHILLED WATER LINE INSULLATION DAMAGED – T4-08-04 |  | FM008 |  | 2022-09-08 02:41 | 2022-09-08 03:41 | 2022-09-09 03:41 | 24 | 2022-09-08 02:50 | 2022-09-08 04:05 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11060273 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110 -415 |  | FM008 |  | 2022-09-25 22:42 | 2022-09-25 23:42 | 2022-09-26 23:42 | 24 | 2022-09-25 22:50 | 2022-09-26 00:30 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11799883 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1110-415, T4-08-04 |  | FM008 |  | 2023-05-16 19:48 | 2023-05-16 20:48 | 2023-05-17 20:48 | 24 | 2023-05-16 19:55 | 2023-05-16 22:30 | 155 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12097495 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | SN-1000 (LIQUOR STORE) ENTIRE STORE AC TOO HOT |  | FM008 |  | 2023-08-16 22:59 | 2023-08-16 23:59 | 2023-08-17 23:59 | 24 | 2023-08-16 23:05 | 2023-08-17 00:40 | 95 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 95217 |  |  | 128332 | Khanlari, Ms. Pardis | N - - - |  | Voice Communication
| CM-2022-10146660 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED |  | FM008 |  | 2022-02-16 20:57 | 2022-02-16 21:57 | 2022-02-17 21:57 | 24 | 2022-02-16 21:05 | 2022-02-16 23:30 | 145 | 290 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 95216 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10049897 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | AIR FROM SUPPLY DUCT ACCESS |  | FM008 |  | 2022-01-15 05:17 | 2022-01-15 06:17 | 2022-01-16 06:17 | 24 | 2022-01-15 05:25 | 2022-01-15 06:50 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | BMS
| CM-2022-10061276 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-01-17 00:04 | 2022-01-17 01:04 | 2022-01-18 01:04 | 24 | 2022-01-17 00:10 | 2022-01-17 01:50 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2023-11971356 | ASD-MTB-FOF008-AHU028 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AHU-A1110-415 – T4-08-04 |  | FM008 |  | 2023-07-10 19:06 | 2023-07-10 20:06 | 2023-07-11 20:06 | 24 | 2023-07-10 19:16 | 2023-07-11 00:10 | 294 | 303 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 87807 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-10121416 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU-A1110-417 FILTER DIRTY |  | FM008 |  | 2022-02-10 18:56 | 2022-02-10 19:56 | 2022-02-11 19:56 | 24 | 2022-02-10 19:06 | 2022-02-10 23:15 | 249 | 370 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10255706 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-03-16 11:19 | 2022-03-16 12:19 | 2022-03-17 12:19 | 24 | 2022-03-16 11:29 | 2022-03-16 13:00 | 91 | 182 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | BMS
| CM-2022-10670385 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU DRAIN LINE BLOCKED T4-08-04 |  | FM008 |  | 2022-05-15 23:31 | 2022-05-16 00:31 | 2022-05-17 00:31 | 24 | 2022-05-15 23:40 | 2022-05-16 00:50 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106914 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11004791 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU-A1110-417 – CHILLED WATER INSULATION IS DAMAGED – T4-08-04 |  | FM008 |  | 2022-09-07 19:19 | 2022-09-07 20:19 | 2022-09-08 20:19 | 24 | 2022-09-07 19:25 | 2022-09-07 21:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11029810 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | RELIEF BELT IS DAMAGED T4-08-04 |  | FM008 |  | 2022-09-17 19:18 | 2022-09-17 20:18 | 2022-09-18 20:18 | 24 | 2022-09-17 19:25 | 2022-09-17 20:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11688366 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU-A1110-417-ABNORMAL NOSY SUPPLY BLOWER SIDE--MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-04-20 01:51 | 2023-04-20 02:51 | 2023-04-21 02:51 | 24 | 2023-04-20 02:00 | 2023-04-20 05:30 | 210 | 630 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12408422 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AC TOO COLD - CAR PODIUM, NEXT TO GOLD SHOP |  | FM008 |  | 2023-11-26 06:10 | 2023-11-26 07:10 | 2023-11-27 07:10 | 24 | 2023-11-26 06:20 | 2023-11-26 12:30 | 370 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 87430 | Maharjan, Ms. Anisha | N - - - |  | Voice Communication
| CM-2022-11009664 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 030 (TAG NO:AHU-A1110-417) FILTER ALARM |  | FM008 |  | 2022-09-11 00:32 | 2022-09-11 01:32 | 2022-09-12 01:32 | 24 | 2022-09-11 00:41 | 2022-09-11 04:55 | 254 | 246 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68060 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11015581 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU LAMP NOT WORKING - T4-08-04 |  | FM008 |  | 2022-09-13 19:13 | 2022-09-13 20:13 | 2022-09-14 20:13 | 24 | 2022-09-13 19:15 | 2022-09-13 20:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11060274 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-417 - T4-08-04 |  | FM008 |  | 2022-09-25 22:44 | 2022-09-25 23:44 | 2022-09-26 23:44 | 24 | 2022-09-25 22:50 | 2022-09-26 00:30 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11216752 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-417 |  | FM008 |  | 2022-11-25 00:10 | 2022-11-25 01:10 | 2022-11-26 01:10 | 24 | 2022-11-25 00:15 | 2022-11-25 03:00 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11255766 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU-A1110-417 AHU ACCESS DOOR DAMAGED T4-08-04 |  | FM008 |  | 2022-12-09 13:41 | 2022-12-09 14:41 | 2022-12-10 14:41 | 24 | 2022-12-09 13:50 | 2022-12-09 15:55 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | DOOR HANDLE LOOSE/DAMAGED | REPAIRED/REPLACED | 106972 | 17053 |  |  | fm3093 | fm3093 | N - - - |  | Voice Communication
| CM-2023-11357221 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-08-04 |  | FM008 |  | 2023-01-08 13:26 | 2023-01-08 14:26 | 2023-01-09 14:26 | 24 | 2023-01-08 13:35 | 2023-01-08 15:00 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2023-11717555 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - MECHANICAL ROOM T4-08-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB417.AHU417.SYSALM.DP1 / |  | FM008 |  | 2023-04-28 14:27 | 2023-04-28 15:27 | 2023-04-29 15:27 | 24 | 2023-04-28 14:33 | 2023-04-28 23:05 | 512 | 187 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2023-11835648 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 030 (TAG NO:AHU-A1110-417) |  | FM008 |  | 2023-05-30 09:12 | 2023-05-30 10:12 | 2023-05-31 10:12 | 24 | 2023-05-30 09:15 | 2023-05-30 11:15 | 120 | 480 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12164615 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-417 - MECHANICAL ROOM T4-08-04 |  | FM008 |  | 2023-09-08 07:36 | 2023-09-08 08:36 | 2023-09-09 08:36 | 24 | 2023-09-08 07:40 | 2023-09-08 09:10 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2024-12527151 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-08-04 |  | FM008 |  | 2024-01-04 00:29 | 2024-01-04 01:29 | 2024-01-05 01:29 | 24 | 2024-01-04 00:35 | 2024-01-04 02:05 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2024-12557427 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | TEDDY BEAR AREA AC TOO COLD |  | FM008 |  | 2024-01-13 08:56 | 2024-01-13 09:56 | 2024-01-14 09:56 | 24 | 2024-01-13 09:00 | 2024-01-13 09:40 | 40 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 116187 | Mbuge, Mr. Felix Ochieng | N - - - |  | Voice Communication
| CM-2024-12791201 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AIR HANDLING UNIT 030 (TAG NO:AHU-A1110-417)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB417.AHU417.SYSALM.DP1 / |  | FM008 |  | 2024-04-01 09:46 | 2024-04-01 10:46 | 2024-04-02 10:46 | 24 | 2024-04-01 09:50 | 2024-04-01 16:30 | 400 | 350 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 138627 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-11148309 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-10-30 07:04 | 2022-10-30 08:04 | 2022-10-31 08:04 | 24 | 2022-10-30 07:10 | 2022-10-30 09:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11564907 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | SN-1003- NEW HARRODS INFRONT OF APPLE - AC IS TOO HOT-- |  | FM008 |  | 2023-03-16 00:48 | 2023-03-16 01:48 | 2023-03-17 01:48 | 24 | 2023-03-16 00:55 | 2023-03-16 05:45 | 290 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94953 | 17053 |  |  | 129454 | Alvarado, Ms. Rose Jean Eroles | N - - - |  | Voice Communication
| CM-2023-11823004 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | A/C IS TOO HOT AT THE TEDDY BEAR AREA |  | FM008 |  | 2023-05-24 18:09 | 2023-05-24 19:09 | 2023-05-25 19:09 | 24 | 2023-05-24 18:15 | 2023-05-24 20:05 | 110 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | T26780 | Laila, Ms. Lahlimi | N - - - |  | Voice Communication
| CM-2023-11971348 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT IS NOT WORKING |  | FM008 |  | 2023-07-10 18:58 | 2023-07-10 19:58 | 2023-07-11 19:58 | 24 | 2023-07-10 19:05 | 2023-07-10 21:35 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12325058 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1110-417 – T4-09-04 |  | FM008 |  | 2023-10-26 07:33 | 2023-10-26 08:33 | 2023-10-27 08:33 | 24 | 2023-10-26 07:35 | 2023-10-26 09:05 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-10145912 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU-A1110-417 RELIEF SIDE BELT DAMAGED / T4-08-04 |  | FM008 |  | 2022-02-15 19:25 | 2022-02-15 20:25 | 2022-02-16 20:25 | 24 | 2022-02-15 19:30 | 2022-02-15 21:10 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 87807 | 55709 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10568765 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | FILTER DIRTY- AHU-A1110-417- T4-08-04 |  | FM008 |  | 2022-04-20 19:12 | 2022-04-20 20:12 | 2022-04-21 20:12 | 24 | 2022-04-20 19:22 | 2022-04-20 22:35 | 193 | 228 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10731690 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – T4-08-04,MEC ROOM |  | FM008 |  | 2022-06-09 09:58 | 2022-06-09 10:57 | 2022-06-10 10:57 | 24 | 2022-06-09 10:07 | 2022-06-09 12:45 | 158 | 228 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 105233 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10919449 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AHU-A1110-417 DP1 FILTER ALARM T4-08-04 |  | FM008 |  | 2022-08-10 09:30 | 2022-08-10 10:30 | 2022-08-11 10:30 | 24 | 2022-08-10 09:40 | 2022-08-10 11:50 | 130 | 370 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11027884 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP3 FILTER ALAR - AHU-A1110-417 - MECHANICAL ROOM T4-08-04 |  | FM008 |  | 2022-09-16 00:26 | 2022-09-16 01:26 | 2022-09-17 01:26 | 24 | 2022-09-16 00:35 | 2022-09-16 05:20 | 285 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11176695 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AC TOO COLD,-SN-1010 AREA |  | FM008 |  | 2022-11-11 02:42 | 2022-11-11 03:42 | 2022-11-12 03:42 | 24 | 2022-11-11 02:50 | 2022-11-11 03:45 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 87430 | Maharjan, Ms. Anisha | N - - - |  | Voice Communication
| CM-2023-11340708 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AC TOO COLD - SN-1010 (TAG HEUER STORE) |  | FM008 |  | 2023-01-03 18:13 | 2023-01-03 19:13 | 2023-01-04 19:13 | 24 | 2023-01-03 18:20 | 2023-01-03 20:00 | 100 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 17053 |  |  | 87430 | Maharjan, Ms. Anisha | N - - - |  | Voice Communication
| CM-2023-11667635 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | AC IS TOO HOT -HIA TEDDY BEAR INFO DESK -TRANSFER A |  | FM008 |  | 2023-04-13 16:37 | 2023-04-13 17:37 | 2023-04-14 17:37 | 24 | 2023-04-13 16:42 | 2023-04-13 17:55 | 73 | 41 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 87807 |  |  | T26780 | Laila, Ms. Lahlimi | N - - - |  | Voice Communication
| CM-2023-11949306 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-08-04 |  | FM008 |  | 2023-07-05 18:57 | 2023-07-05 19:57 | 2023-07-06 19:57 | 24 | 2023-07-05 19:04 | 2023-07-05 21:00 | 116 | 232 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10061277 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | FILTER DIRTY :AHU-A1110-417 |  | FM008 |  | 2022-01-17 00:07 | 2022-01-17 01:07 | 2022-01-18 01:07 | 24 | 2022-01-17 00:15 | 2022-01-17 03:40 | 205 | 205 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2022-10671505 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | RELIEF SIDE BELT DAMAGED - T4-08-04 |  | FM008 |  | 2022-05-16 19:10 | 2022-05-16 20:10 | 2022-05-17 20:10 | 24 | 2022-05-16 19:20 | 2022-05-16 23:15 | 235 | 215 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17053 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10949918 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONDUIT DAMAGED -T4-08-04 |  | FM008 |  | 2022-08-15 13:48 | 2022-08-15 14:48 | 2022-08-16 14:48 | 24 | 2022-08-15 13:57 | 2022-08-15 18:38 | 281 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11446510 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY AHU-A1110-417 |  | FM008 |  | 2023-02-10 09:31 | 2023-02-10 10:31 | 2023-02-11 10:31 | 24 | 2023-02-10 09:40 | 2023-02-10 13:05 | 205 | 305 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11929804 | ASD-MTB-FOF008-AHU030 | AIR HANDLING UNIT-05 | A/C IS TOO HOT AT INFO DESK AT TEDDY BEAR |  | FM008 |  | 2023-06-26 00:55 | 2023-06-26 01:55 | 2023-06-27 01:55 | 24 | 2023-06-26 01:00 | 2023-06-26 04:30 | 210 | 68 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | 35585 | KATE | N - - - |  | Voice Communication
| CM-2022-10144153 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | RELEASE BELT DAMAGED-AHU-A110-421-IRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-02-14 09:38 | 2022-02-14 10:38 | 2022-02-15 10:38 | 24 | 2022-02-14 09:45 | 2022-02-14 11:20 | 95 | 155 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10750239 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-421 – T4-08-04 |  | FM008 |  | 2022-06-19 07:10 | 2022-06-19 08:10 | 2022-06-20 08:10 | 24 | 2022-06-19 07:15 | 2022-06-19 10:25 | 190 | 155 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11059277 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-08-04 |  | FM008 |  | 2022-09-26 00:50 | 2022-09-26 01:50 | 2022-09-27 01:50 | 24 | 2022-09-26 00:55 | 2022-09-26 02:30 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11149968 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 AHU INSIDE LIGHT NOT WORKING T4-08-04 |  | FM008 |  | 2022-10-31 19:14 | 2022-10-31 20:14 | 2022-11-01 20:14 | 24 | 2022-10-31 19:20 | 2022-10-31 20:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11166468 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-06 13:35 | 2022-11-06 14:35 | 2022-11-07 14:35 | 24 | 2022-11-06 13:40 | 2022-11-06 14:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 87807 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2022-11216421 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | COOLING FAN FAULTY AHU-A1110-421 |  | FM008 |  | 2022-11-23 15:21 | 2022-11-23 16:21 | 2022-11-24 16:21 | 24 | 2022-11-23 15:30 | 2022-11-23 16:55 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11253330 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421- CHILLED WATER LINE PAINT-- (AHU-A1110-417,415,419,405) |  | FM008 |  | 2022-12-07 08:20 | 2022-12-07 09:20 | 2022-12-08 09:20 | 24 | 2022-12-07 08:25 | 2022-12-07 15:30 | 425 | 850 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 94953 | 17053 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2023-12199033 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-08-04 |  | FM008 |  | 2023-09-19 00:08 | 2023-09-19 01:08 | 2023-09-20 01:08 | 24 | 2023-09-19 00:12 | 2023-09-19 02:02 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11365284 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 RELIEF FAN V BELT DAMAGED |  | FM008 |  | 2023-01-12 19:31 | 2023-01-12 20:31 | 2023-01-13 20:31 | 24 | 2023-01-12 19:40 | 2023-01-12 20:45 | 65 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11878034 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-421 - T4-08-04 |  | FM008 |  | 2023-06-15 00:05 | 2023-06-15 01:05 | 2023-06-16 01:05 | 24 | 2023-06-15 00:10 | 2023-06-15 01:55 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | BMS
| CM-2023-11893635 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED -AIR HANDLING UNIT 034 (TAG NO:AHU-A1110-421) |  | FM008 |  | 2023-06-19 01:04 | 2023-06-19 02:04 | 2023-06-20 02:04 | 24 | 2023-06-19 01:10 | 2023-06-19 02:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12036898 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421-DP1-FILTER ALARM- T4-09-04 |  | FM008 |  | 2023-08-02 19:16 | 2023-08-02 20:16 | 2023-08-03 20:16 | 24 | 2023-08-02 19:25 | 2023-08-02 22:30 | 185 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12064774 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | RELIEF V BELT DAMAGED |  | FM008 |  | 2023-08-09 08:28 | 2023-08-09 09:28 | 2023-08-10 09:28 | 24 | 2023-08-09 08:35 | 2023-08-09 17:15 | 520 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12063924 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | LIGHT FLEXIBLE CONNECTOR DAMAGE -AHU-A1110-421NEAR (T4-08-04) |  | FM008 |  | 2023-08-08 11:38 | 2023-08-08 12:38 | 2023-08-09 12:38 | 24 | 2023-08-08 11:45 | 2023-08-08 14:47 | 182 | 364 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-11015277 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421- AHU LAMP NOT WORKING- T4-08-04 |  | FM008 |  | 2022-09-12 19:59 | 2022-09-12 20:59 | 2022-09-13 20:59 | 24 | 2022-09-12 20:08 | 2022-09-12 23:58 | 230 | 186 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 87807 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11564948 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 – FILTER DIRTY -T4-08-04 |  | FM008 |  | 2023-03-16 06:59 | 2023-03-16 07:59 | 2023-03-17 07:59 | 24 | 2023-03-16 07:05 | 2023-03-16 08:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10672658 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | T4-08-04 AHU-A1110-421 RELIEF BELT DAMAGED |  | FM008 |  | 2022-05-17 10:34 | 2022-05-17 11:34 | 2022-05-18 11:34 | 24 | 2022-05-17 10:41 | 2022-05-17 14:40 | 239 | 278 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 55709 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2022-10911760 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 –SUPPLY DUCT INSULATION DAMAGED- - |  | FM008 |  | 2022-08-03 22:09 | 2022-08-03 23:09 | 2022-08-04 23:09 | 24 | 2022-08-03 22:15 | 2022-08-03 23:58 | 103 | 309 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 55709 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-11971748 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 – AHU CABIN LIGHTING SWITCH DAMAGED-T4-08-04 |  | FM008 |  | 2023-07-11 19:22 | 2023-07-11 20:22 | 2023-07-12 20:22 | 24 | 2023-07-11 19:30 | 2023-07-11 22:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 95217 | 87807 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | BMS
| CM-2022-10121301 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 DP1 FILTER ALARM |  | FM008 |  | 2022-02-09 19:09 | 2022-02-09 20:09 | 2022-02-10 20:09 | 24 | 2022-02-09 19:15 | 2022-02-09 23:20 | 245 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10122682 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421 SUPPLY SIDE BELT LOOSE T4-08-34 |  | FM008 |  | 2022-02-09 22:42 | 2022-02-09 23:42 | 2022-02-10 23:42 | 24 | 2022-02-09 22:50 | 2022-02-09 23:55 | 65 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 89127 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10154594 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | AHU-A1110-421-T4-08-04-RETURN DUCT TEST POINT AREA INSULATION DAMAGE |  | FM008 |  | 2022-02-21 21:54 | 2022-02-21 22:54 | 2022-02-22 22:54 | 24 | 2022-02-21 22:04 | 2022-02-21 23:34 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10660338 | ASD-MTB-FOF008-AHU034 | AIR HANDLING UNIT-05 | RELIEF FAN FAIL ALARM-T4-08-04 |  | FM008 |  | 2022-05-13 14:14 | 2022-05-13 15:14 | 2022-05-14 15:14 | 24 | 2022-05-13 14:20 | 2022-05-13 15:02 | 42 | 84 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 106914 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10694684 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU BELT DAMAGED |  | FM008 |  | 2022-05-27 00:06 | 2022-05-27 01:06 | 2022-05-28 01:06 | 24 | 2022-05-27 00:15 | 2022-05-27 01:40 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10787882 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-28 07:20 | 2022-06-28 08:20 | 2022-06-29 08:20 | 24 | 2022-06-28 07:25 | 2022-06-28 08:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11041311 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY |  | FM008 |  | 2022-09-23 00:05 | 2022-09-23 01:05 | 2022-09-24 01:05 | 24 | 2022-09-23 00:10 | 2022-09-23 01:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11060734 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU V-BELT DAMAGED - -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-09-28 10:48 | 2022-09-28 11:48 | 2022-09-29 11:48 | 24 | 2022-09-28 10:55 | 2022-09-28 16:45 | 350 | 135 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 121959 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11149912 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU-A1110-447 – MARINE LIGHT IS NOT WORKING – T4-08-04 |  | FM008 |  | 2022-10-31 14:07 | 2022-10-31 15:07 | 2022-11-01 15:07 | 24 | 2022-10-31 14:15 | 2022-10-31 15:44 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | THE EQUIPMENT HAS BEEN SWITCH OFF | THE POWER HAS BEEN RESTORED | 94954 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11859989 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU-A1110-447 AHU BELT DAMAGED |  | FM008 |  | 2023-06-06 10:14 | 2023-06-06 11:14 | 2023-06-07 11:14 | 24 | 2023-06-06 10:20 | 2023-06-06 11:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 94954 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11859990 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU-A1110-447 FILTER IS DIRTY |  | FM008 |  | 2023-06-06 10:16 | 2023-06-06 11:17 | 2023-06-07 11:17 | 24 | 2023-06-06 10:22 | 2023-06-06 14:00 | 218 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 94954 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12186727 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU-A1110-447 FILTER DIRTY T4-08-04 |  | FM008 |  | 2023-09-16 00:08 | 2023-09-16 01:08 | 2023-09-17 01:08 | 24 | 2023-09-16 00:15 | 2023-09-16 03:45 | 210 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11271526 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AC VENT DIRTY - VITALITY SPA CORRIDOR |  | FM008 |  | 2022-12-14 00:05 | 2022-12-14 01:05 | 2022-12-15 01:05 | 24 | 2022-12-14 00:15 | 2022-12-14 03:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 105233 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12210903 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-09-23 00:12 | 2023-09-23 01:12 | 2023-09-24 01:12 | 24 | 2023-09-23 00:15 | 2023-09-23 03:20 | 185 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12298704 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED - AHU-A1110-447- T4 08 04 |  | FM008 |  | 2023-10-17 20:14 | 2023-10-17 21:14 | 2023-10-18 21:14 | 24 | 2023-10-17 20:20 | 2023-10-17 23:10 | 170 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10037029 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED – T4-08-04 |  | FM008 |  | 2022-01-09 13:50 | 2022-01-09 14:50 | 2022-01-10 14:50 | 24 | 2022-01-09 14:00 | 2022-01-09 17:39 | 219 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 17154 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10160250 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU-A1110-447- - MOTOR BELT DAMAGED |  | FM008 |  | 2022-02-21 00:34 | 2022-02-21 01:34 | 2022-02-22 01:34 | 24 | 2022-02-21 00:40 | 2022-02-21 02:15 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10157508 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | DRAIN LINE IS BLOCKED – AHU-A1110-447 - T4-08-04 |  | FM008 |  | 2022-02-20 19:19 | 2022-02-20 20:19 | 2022-02-21 20:19 | 24 | 2022-02-20 19:25 | 2022-02-20 20:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17573 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | E-mail
| CM-2022-10118171 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-02-08 00:13 | 2022-02-08 01:13 | 2022-02-09 01:13 | 24 | 2022-02-08 00:23 | 2022-02-08 01:53 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10954069 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AMECHANICAL ROOM T4-08-04 |  | FM008 |  | 2022-08-17 14:12 | 2022-08-17 15:12 | 2022-08-18 15:12 | 24 | 2022-08-17 14:20 | 2022-08-17 16:00 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11200268 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | D1 FILTER ALARM -TG -08-04-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-11-19 19:23 | 2022-11-19 20:23 | 2022-11-20 20:23 | 24 | 2022-11-19 19:30 | 2022-11-19 21:55 | 145 | 235 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11668298 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-04-16 11:13 | 2023-04-16 12:13 | 2023-04-17 12:13 | 24 | 2023-04-16 11:20 | 2023-04-16 13:00 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10969404 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-08-26 12:14 | 2022-08-26 13:14 | 2022-08-27 13:14 | 24 | 2022-08-26 12:20 | 2022-08-26 15:15 | 175 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | BMS
| CM-2023-12188530 | ASD-MTB-FOF008-AHU060 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED – T4-08-04 |  | FM008 |  | 2023-09-16 01:11 | 2023-09-16 02:11 | 2023-09-17 02:11 | 24 | 2023-09-16 01:20 | 2023-09-16 06:00 | 280 | 276 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10731754 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | LIGHTING FIXABLE CONNECTOR DAMAGED - AHU-A1110-449 - MECHANICAL ROOM T4-08-04 |  | FM008 |  | 2022-06-09 13:17 | 2022-06-09 14:17 | 2022-06-10 14:17 | 24 | 2022-06-09 13:25 | 2022-06-09 16:16 | 171 | 181 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17573 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10859694 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC NOT WORKING IN VITALITY SPA THE SWIMMING PULL AREA -PLEASE CHECK |  | FM008 |  | 2022-07-18 22:36 | 2022-07-18 23:36 | 2022-07-19 23:36 | 24 | 2022-07-18 22:40 | 2022-07-18 23:49 | 69 | 64 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106914 | 95217 |  |  | 90974 | Mari, Mr. Luther Muriuki | N - - - |  | Voice Communication
| CM-2022-11077679 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | BEARING NOISY |  | FM008 |  | 2022-10-05 15:14 | 2022-10-05 16:14 | 2022-10-06 16:14 | 24 | 2022-10-05 15:20 | 2022-10-05 23:45 | 505 | 305 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106972 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11114685 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC NOT WORKING INSID THE POOL AREA - AIRSIDE-HOTEL-VITALITY |  | FM008 |  | 2022-10-20 08:54 | 2022-10-20 09:54 | 2022-10-21 09:54 | 24 | 2022-10-20 09:00 | 2022-10-20 13:45 | 285 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 107627 | Peter, Ms. Sony | N - - - |  | Voice Communication
| CM-2023-11463552 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449)-FLOOR AIR VENT DIRTY-VITALITY SPY |  | FM008 |  | 2023-02-14 19:56 | 2023-02-14 20:56 | 2023-02-15 20:56 | 24 | 2023-02-14 20:05 | 2023-02-14 23:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 95217 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-12016485 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED - AHU-A1110-449– T4 08 04 |  | FM008 |  | 2023-07-29 00:10 | 2023-07-29 01:10 | 2023-07-30 01:10 | 24 | 2023-07-29 00:16 | 2023-07-29 02:16 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 17053 |  |  | FM1127 | Rahman, Mr. Mohammad Habibur | N - - - |  | Voice Communication
| CM-2023-12050685 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | T4-08-04 SUPPLY BELT DAMAGED AHU-A1110-449 |  | FM008 |  | 2023-08-06 07:38 | 2023-08-06 08:38 | 2023-08-07 08:38 | 24 | 2023-08-06 07:45 | 2023-08-06 11:40 | 235 | 187 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM10619 | Junaid, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12163068 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY FAN FAIL ALARM - UNIT TRIPPED |  | FM008 |  | 2023-09-07 08:14 | 2023-09-07 09:14 | 2023-09-08 09:14 | 24 | 2023-09-07 08:20 | 2023-09-07 10:10 | 110 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106972 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-12206998 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-09-22 19:15 | 2023-09-22 20:15 | 2023-09-23 20:15 | 24 | 2023-09-22 19:20 | 2023-09-22 22:05 | 165 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12366987 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449 SUPPLY BELT DAMAGED-T4-08-04 |  | FM008 |  | 2023-11-11 00:33 | 2023-11-11 01:33 | 2023-11-12 01:33 | 24 | 2023-11-11 00:35 | 2023-11-11 04:45 | 250 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12422928 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC VENT DIRTY -32 GRILLS -VITALITY SPA -SWIMMING POOL AREA |  | FM008 |  | 2023-11-27 00:59 | 2023-11-27 01:59 | 2023-11-28 01:59 | 24 | 2023-11-27 01:05 | 2023-11-27 06:45 | 340 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 95217 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11007591 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449- SUPPLY FLOW LOW ALARM- |  | FM008 |  | 2022-09-09 07:00 | 2022-09-09 08:01 | 2022-09-10 08:01 | 24 | 2022-09-09 07:10 | 2022-09-09 08:45 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11015584 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU LAMP NOT WORKING - T4-08-04 |  | FM008 |  | 2022-09-13 19:32 | 2022-09-13 20:32 | 2022-09-14 20:32 | 24 | 2022-09-13 19:36 | 2022-09-13 22:20 | 164 | 186 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11064226 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY V-BELT DAMAGED -AHU-A1110-449)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-09-30 10:29 | 2022-09-30 11:29 | 2022-10-01 11:29 | 24 | 2022-09-30 10:35 | 2022-09-30 14:30 | 235 | 145 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11615917 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449- BELT DAMAGED – T4-08-04- |  | FM008 |  | 2023-04-04 00:23 | 2023-04-04 01:23 | 2023-04-05 01:23 | 24 | 2023-04-04 00:30 | 2023-04-04 02:25 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17154 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11917159 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | DP1 FILTER STATUS ALARM,AHU-A1110-449,MECHANICAL ROOM T4-08-04 |  | FM008 |  | 2023-06-23 07:32 | 2023-06-23 08:32 | 2023-06-24 08:32 | 24 | 2023-06-23 07:40 | 2023-06-23 13:30 | 350 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12090359 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | BELT DAMAGED -T4-08-04 |  | FM008 |  | 2023-08-17 09:53 | 2023-08-17 10:53 | 2023-08-18 10:53 | 24 | 2023-08-17 10:00 | 2023-08-17 14:00 | 240 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 17573 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12286746 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC NOT WORKING IN THE SWIMMING POOL AREA – NEAR T4-07-10 (PASSENGERS COMPLAINING) |  | FM008 |  | 2023-10-15 21:32 | 2023-10-15 22:02 | 2023-10-16 02:02 | 4 | 2023-10-15 21:40 | 2023-10-16 00:20 | 160 | 35 | 2 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 008 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 87807 |  |  | 89161 | Ndagawa, Mr. Sowedi | N - - - |  | Voice Communication
| CM-2024-12610507 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU MOTOR NOISY - AHU-A1110-449 - MECHANICAL ROOM T4-08-04 |  | FM008 |  | 2024-01-30 10:16 | 2024-01-30 11:16 | 2024-01-31 11:16 | 24 | 2024-01-30 10:25 | 2024-01-30 13:10 | 165 | 455 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17573 | 17053 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2024-12631409 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | V-BELT DAMAGED=-T4-08-04-AHU-A1110-449)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2024-02-06 20:17 | 2024-02-06 21:17 | 2024-02-07 21:17 | 24 | 2024-02-06 20:20 | 2024-02-07 01:20 | 300 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 95217 |  |  | FM5381 | Thomas, Mr. Joseph | N - - - |  | Voice Communication
| CM-2023-11918079 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ASD-MTB-FOF008-AHU062(AHU-A1110-449) MECHANICAL ROOM T4-08-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB449.AHU449.SYSALM.DP1 / Jun/25/2023 1:23:49 PM |  | FM008 |  | 2023-06-25 15:16 | 2023-06-25 16:16 | 2023-06-26 16:16 | 24 | 2023-06-25 15:25 | 2023-06-25 20:00 | 275 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11998089 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED |  | FM008 |  | 2023-07-22 00:05 | 2023-07-22 01:05 | 2023-07-23 01:05 | 24 | 2023-07-22 00:10 | 2023-07-22 02:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12286776 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY V-BELT DAMAGE - AIR HANDLING UNIT 062 (TAG NO:AHU-A1110-449)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-10-16 01:38 | 2023-10-16 02:38 | 2023-10-17 02:38 | 24 | 2023-10-16 01:45 | 2023-10-16 04:11 | 146 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 119320 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12565192 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY BLOWER SIDE ABNORMAL SOUND |  | FM008 |  | 2024-01-16 00:05 | 2024-01-16 01:05 | 2024-01-17 01:05 | 24 | 2024-01-16 00:10 | 2024-01-16 02:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12589957 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC NOT WORKING - HOTEL-VITALITY SWIMMING POOL |  | FM008 |  | 2024-01-23 15:38 | 2024-01-23 16:38 | 2024-01-24 16:38 | 24 | 2024-01-23 15:45 | 2024-01-23 18:40 | 175 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 95217 |  |  | 72798 | Napit, Mr. Laxman | N - - - |  | Voice Communication
| CM-2022-10157510 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY SIDE MOTOR BELT IS LOOSE – AHU-A1110-449 - T4-08-04 |  | FM008 |  | 2022-02-20 19:21 | 2022-02-20 20:21 | 2022-02-21 20:21 | 24 | 2022-02-20 19:30 | 2022-02-20 21:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10118374 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449 SUPPLY AIR TEMPERATURE SENSOR FAULTY T4-08-04 |  | FM008 |  | 2022-02-09 00:26 | 2022-02-09 01:26 | 2022-02-10 01:26 | 24 | 2022-02-09 00:30 | 2022-02-09 02:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 87807 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10118172 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-02-08 00:14 | 2022-02-08 01:14 | 2022-02-09 01:14 | 24 | 2022-02-08 00:24 | 2022-02-08 03:20 | 176 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10273746 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449- RELIEF BELT DAMAGED |  | FM008 |  | 2022-03-22 09:39 | 2022-03-22 10:39 | 2022-03-23 10:39 | 24 | 2022-03-22 09:45 | 2022-03-22 11:00 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17154 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10307609 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU-A1110-449 – DP 3 ALARM – T4-08-04 |  | FM008 |  | 2022-03-29 11:43 | 2022-03-29 12:43 | 2022-03-30 12:43 | 24 | 2022-03-29 11:50 | 2022-03-29 17:15 | 325 | 135 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 17154 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10966109 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | DRAIN LINE MESH COVER RUSTED AND FUNGS-T4-08-04 |  | FM008 |  | 2022-08-23 07:42 | 2022-08-23 08:42 | 2022-08-24 08:42 | 24 | 2022-08-23 07:50 | 2022-08-23 09:00 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95217 | 55709 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11200267 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | D3 FILTER ALARM--MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008. |  | FM008 |  | 2022-11-19 19:19 | 2022-11-19 20:19 | 2022-11-20 20:19 | 24 | 2022-11-19 19:25 | 2022-11-19 21:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11620778 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AHU MOTOR IS NOISY – T4-08-04 |  | FM008 |  | 2023-04-04 02:29 | 2023-04-04 03:30 | 2023-04-05 03:30 | 24 | 2023-04-04 02:35 | 2023-04-04 04:15 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11959213 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1110-449 - MECHANICAL ROOM T4-08-04 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP1.MTB449.AHU449.SYSALM.DP1 / |  | FM008 |  | 2023-07-07 15:18 | 2023-07-07 16:18 | 2023-07-08 16:18 | 24 | 2023-07-07 15:25 | 2023-07-07 20:30 | 305 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10170275 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC RETURN GRILL DIRTY SPA SWIMMING POOL AREA |  | FM008 |  | 2022-02-24 07:24 | 2022-02-24 08:24 | 2022-02-25 08:24 | 24 | 2022-02-24 07:30 | 2022-02-24 10:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10593140 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | FILTER DIRTY- T4-08-04 |  | FM008 |  | 2022-04-29 00:15 | 2022-04-29 01:15 | 2022-04-30 01:15 | 24 | 2022-04-29 00:24 | 2022-04-29 03:00 | 156 | 166 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10855125 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED- T4-08-04 |  | FM008 |  | 2022-07-18 22:04 | 2022-07-18 23:04 | 2022-07-19 23:04 | 24 | 2022-07-18 22:10 | 2022-07-18 23:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 95217 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-12163105 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC TOO HOT SWIMMING POOL AREA VITALITY SPA NEAR RECEPTION |  | FM008 |  | 2023-09-07 08:53 | 2023-09-07 09:53 | 2023-09-08 09:53 | 24 | 2023-09-07 09:00 | 2023-09-07 11:15 | 135 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 68485 | 17053 |  |  | 72798 | Napit, Mr. Laxman | N - - - |  | Voice Communication
| CM-2023-12178738 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | AC VENT DIRTY – (AHU-A1110-449 – SWIMMING POOL AREA |  | FM008 |  | 2023-09-13 07:49 | 2023-09-13 08:49 | 2023-09-14 08:49 | 24 | 2023-09-13 07:55 | 2023-09-13 18:30 | 635 | 725 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 132112 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12296790 | ASD-MTB-FOF008-AHU062 | AIR HANDLING UNIT-05 | SUPPLY BLOW AIR PAINT FADED |  | FM008 |  | 2023-10-18 00:08 | 2023-10-18 01:08 | 2023-10-19 01:08 | 24 | 2023-10-18 00:12 | 2023-10-18 04:50 | 278 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 95216 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10043981 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGE AHU-A1110-402 T4-09-04 |  | FM008 |  | 2022-01-10 13:41 | 2022-01-10 14:41 | 2022-01-11 14:41 | 24 | 2022-01-10 13:45 | 2022-01-10 14:44 | 59 | 118 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 85125 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10798884 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402 – DP1 FILTER ALARM |  | FM008 |  | 2022-07-01 18:58 | 2022-07-01 19:58 | 2022-07-02 19:58 | 24 | 2022-07-01 19:07 | 2022-07-01 20:37 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10863512 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - FILTERS 768-AIR HANDLING UNIT 015 (TAG NO:AHU-A1110-402)-AIRSIDE-MTB-FOURTH FLOOR AREA 009 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP2.MTB422.AHU402.SYSALM.DP1 / |  | FM008 |  | 2022-07-23 01:30 | 2022-07-23 02:30 | 2022-07-24 02:30 | 24 | 2022-07-23 01:35 | 2022-07-23 04:00 | 145 | 115 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10952609 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM TAG NO:AHU-A1110-402, - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-08-19 07:13 | 2022-08-19 08:13 | 2022-08-20 08:13 | 24 | 2022-08-19 07:23 | 2022-08-19 09:00 | 97 | 194 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11079828 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402 WATER LINE INSULATION DAMAGED T4-09-04 |  | FM008 |  | 2022-10-09 00:05 | 2022-10-09 01:05 | 2022-10-10 01:05 | 24 | 2022-10-09 00:10 | 2022-10-09 01:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11620394 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402 DRAIN LINE IS BLOCKED |  | FM008 |  | 2023-04-03 11:38 | 2023-04-03 12:38 | 2023-04-04 12:38 | 24 | 2023-04-03 11:45 | 2023-04-03 13:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-12092886 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | T4-09-04-CHILLED WATER LINE PAINT FADED -AIR HANDLING UNIT 015 (TAG NO:AHU-A1110-402)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-08-14 23:00 | 2023-08-15 | 2023-08-16 | 24 | 2023-08-14 23:05 | 2023-08-15 00:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2022-11039135 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | FILTER ALARM - AHU-A1110-402 |  | FM008 |  | 2022-09-23 07:12 | 2022-09-23 08:12 | 2022-09-24 08:12 | 24 | 2022-09-23 07:15 | 2022-09-23 08:30 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11826692 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-26 19:44 | 2023-05-26 20:44 | 2023-05-27 20:44 | 24 | 2023-05-26 19:50 | 2023-05-26 23:55 | 245 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-11993804 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-07-18 01:12 | 2023-07-18 02:12 | 2023-07-19 02:12 | 24 | 2023-07-18 01:20 | 2023-07-18 05:15 | 235 | 278 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11113874 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | MOTOR NOISY SUPPLY -T4-09-04 |  | FM008 |  | 2022-10-20 18:53 | 2022-10-20 19:53 | 2022-10-21 19:53 | 24 | 2022-10-20 19:02 | 2022-10-21 02:00 | 418 | 508 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 87807 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11117600 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402 - DP3 FILTER ALARM |  | FM008 |  | 2022-10-21 21:41 | 2022-10-21 22:41 | 2022-10-22 22:41 | 24 | 2022-10-21 21:45 | 2022-10-21 22:45 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11994802 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402)-BELT DAMAGE -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-07-18 00:29 | 2023-07-18 01:29 | 2023-07-19 01:29 | 24 | 2023-07-18 00:35 | 2023-07-18 02:05 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 87807 |  |  | FM1127 | Rahman, Mr. Mohammad Habibur | N - - - |  | Voice Communication
| CM-2024-12649821 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | BLOWER BEARING NOISY AHU-A1110-402 |  | FM008 |  | 2024-02-13 09:54 | 2024-02-13 10:54 | 2024-02-14 10:54 | 24 | 2024-02-13 10:00 | 2024-02-13 14:55 | 295 | 380 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106972 | 17053 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2023-12287951 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED |  | FM008 |  | 2023-10-17 00:03 | 2023-10-17 01:03 | 2023-10-18 01:03 | 24 | 2023-10-17 00:10 | 2023-10-17 04:50 | 280 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 124475 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12322881 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1110-402- T4-09-04 |  | FM008 |  | 2023-10-25 16:45 | 2023-10-25 17:45 | 2023-10-26 17:45 | 24 | 2023-10-25 16:50 | 2023-10-25 17:50 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2022-10116868 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402 FILTER DIRTY |  | FM008 |  | 2022-02-08 07:10 | 2022-02-08 08:10 | 2022-02-09 08:10 | 24 | 2022-02-08 07:15 | 2022-02-08 10:25 | 190 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10567416 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-402 T4-09-04 |  | FM008 |  | 2022-04-18 16:02 | 2022-04-18 17:02 | 2022-04-19 17:02 | 24 | 2022-04-18 16:10 | 2022-04-18 18:15 | 125 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 85125 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11005183 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 015 (TAG NO:AHU-A1110-402)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 FILTER ALARM |  | FM008 |  | 2022-09-09 00:14 | 2022-09-09 01:14 | 2022-09-10 01:14 | 24 | 2022-09-09 00:20 | 2022-09-09 02:00 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11102850 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402- SUPPLY AND RELIEF V BELT DAMAGED |  | FM008 |  | 2022-10-14 22:02 | 2022-10-14 23:02 | 2022-10-15 23:02 | 24 | 2022-10-14 22:05 | 2022-10-15 00:20 | 135 | 405 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11104575 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402- COOLING COIL DIRTY T4-09-04 |  | FM008 |  | 2022-10-14 19:20 | 2022-10-14 20:20 | 2022-10-15 20:20 | 24 | 2022-10-14 19:30 | 2022-10-14 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10670539 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402- DP1 FILTER ALARM-- |  | FM008 |  | 2022-05-16 19:04 | 2022-05-16 20:04 | 2022-05-17 20:04 | 24 | 2022-05-16 19:13 | 2022-05-16 21:13 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10912680 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | AHU-A1110-402- FILTER DIRTY- |  | FM008 |  | 2022-08-02 19:05 | 2022-08-02 20:05 | 2022-08-03 20:05 | 24 | 2022-08-02 19:15 | 2022-08-02 20:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 76858 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12296789 | ASD-MTB-FOF009-AHU015 | AIR HANDLING UNIT-05 | SUPPLY BLOW AIR PAINT FADED |  | FM008 |  | 2023-10-18 00:07 | 2023-10-18 01:07 | 2023-10-19 01:07 | 24 | 2023-10-18 00:15 | 2023-10-18 02:45 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95216 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10157560 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404 - SUPPLY DUCT INSULATION IS DAMAGED – T4-09-04 |  | FM008 |  | 2022-02-21 04:16 | 2022-02-21 05:16 | 2022-02-22 05:16 | 24 | 2022-02-21 04:25 | 2022-02-21 05:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10842756 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC TOO HOT HOUSEKEEPING BACK OFFICE T3-09-46 |  | FM008 |  | 2022-07-17 11:53 | 2022-07-17 12:53 | 2022-07-18 12:53 | 24 | 2022-07-17 12:00 | 2022-07-17 12:30 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 95217 |  |  | 122305 | Shankar, Mr. Sai | N - - - |  | Voice Communication
| CM-2022-11113757 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | CORRIDOR CEILING AC GRILL DETACHED NEAR ROOM # 138 -EAST WING THIRD FLOOR |  | FM008 |  | 2022-10-20 07:46 | 2022-10-20 08:46 | 2022-10-21 08:46 | 24 | 2022-10-20 07:55 | 2022-10-20 14:55 | 420 | 115 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 124475 | 17053 |  |  | 111139 | Kannan, Mr. Pradeep | N - - - |  | Voice Communication
| CM-2023-11348304 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC TOO COLD- AIRPORT HOTEL 3 RD FLOOR CORRIDOR AREA. |  | FM008 |  | 2023-01-05 18:34 | 2023-01-05 19:34 | 2023-01-06 19:34 | 24 | 2023-01-05 18:40 | 2023-01-05 20:00 | 80 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 17053 |  |  | 129378 | Mohan, Mr. Shamal | N - - - |  | Voice Communication
| CM-2023-11577505 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404 – BELT DAMAGED - T4-09-04- |  | FM008 |  | 2023-03-20 00:07 | 2023-03-20 01:07 | 2023-03-21 01:07 | 24 | 2023-03-20 00:16 | 2023-03-20 01:45 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17154 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11946668 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | Dirty AC diffuser in corridor area near T3-08-07-corridor area near T3-08-07 |  | FM008 |  | 2023-07-03 18:04 | 2023-07-03 19:04 | 2023-07-04 19:04 | 24 | 2023-07-03 18:10 | 2023-07-03 20:00 | 110 | 126 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | 134092 | Almario, Mr. Neftali Tinao | N - - - |  | Voice Communication
| CM-2023-11946669 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | Dirty AC diffuser in corridor area Level 3 near Elevator TSE-02 &TSE-01-Level 3 near Elevator TSE-02 &TSE-01 |  | FM008 |  | 2023-07-03 18:05 | 2023-07-03 19:05 | 2023-07-04 19:05 | 24 | 2023-07-03 18:10 | 2023-07-03 21:05 | 175 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | 134092 | Almario, Mr. Neftali Tinao | N - - - |  | Voice Communication
| CM-2023-11961460 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404-PD3-FILTER DIRTY -T4-09-04 |  | FM008 |  | 2023-07-08 19:00 | 2023-07-08 20:00 | 2023-07-09 20:00 | 24 | 2023-07-08 19:06 | 2023-07-08 21:55 | 169 | 167 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | FILTER DRIER OBSTRUCTED | CLEARED THE OBSTRUCTION | 77406 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12098096 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | CHILLER PAINT FADED - AHU-A1110-404 – T4-09-04 |  | FM008 |  | 2023-08-19 00:14 | 2023-08-19 01:14 | 2023-08-20 01:14 | 24 | 2023-08-19 00:20 | 2023-08-19 02:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 133396 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12245088 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | CABIN LAMP NOT WORKING - AHU-A1110-404 T4-08-04 |  | FM008 |  | 2023-10-02 03:38 | 2023-10-02 04:38 | 2023-10-03 04:38 | 24 | 2023-10-02 03:45 | 2023-10-02 06:28 | 163 | 301 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 87807 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2023-12297071 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLY FAN MOTOR ABNORMAL NOISY AHU-A1110-404 |  | FM008 |  | 2023-10-19 02:42 | 2023-10-19 03:42 | 2023-10-20 03:42 | 24 | 2023-10-19 02:50 | 2023-10-19 04:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12297072 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLY FAN BLOWER ABNORMAL SOUND AHU-A1110-404) |  | FM008 |  | 2023-10-19 02:43 | 2023-10-19 03:43 | 2023-10-20 03:43 | 24 | 2023-10-19 02:50 | 2023-10-19 05:08 | 138 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106972 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12303744 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLIER BLOWER PAINT FADED - AHU-A1110-404 – T4-09-04 |  | FM008 |  | 2023-10-21 00:33 | 2023-10-21 01:33 | 2023-10-22 01:33 | 24 | 2023-10-21 00:40 | 2023-10-21 02:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12303746 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED - AHU-A1110-404 – T4-09-04 |  | FM008 |  | 2023-10-21 00:35 | 2023-10-21 01:35 | 2023-10-22 01:35 | 24 | 2023-10-21 00:40 | 2023-10-21 03:40 | 180 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11206615 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -AHU-A1110-404)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-11-21 14:28 | 2022-11-21 15:28 | 2022-11-22 15:28 | 24 | 2022-11-21 14:35 | 2022-11-21 16:15 | 100 | 135 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11230659 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS DAMAGED - AHU-A1110-404 – T4-09-04 |  | FM008 |  | 2022-11-30 04:44 | 2022-11-30 05:44 | 2022-12-01 05:44 | 24 | 2022-11-30 04:50 | 2022-11-30 06:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11295742 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-404 - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2022-12-20 11:14 | 2022-12-20 12:14 | 2022-12-21 12:14 | 24 | 2022-12-20 11:20 | 2022-12-20 12:34 | 74 | 148 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11347188 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC TOO COLD - CORRIDOR AREA NEAR HOTEL ROOM 140 |  | FM008 |  | 2023-01-04 16:52 | 2023-01-04 17:52 | 2023-01-05 17:52 | 24 | 2023-01-04 17:00 | 2023-01-04 20:00 | 180 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17154 | 17053 |  |  | 124804 | Joy, Mr. Johnson | N - - - |  | Voice Communication
| CM-2023-11973634 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1110-404 - AIR HANDLING UNIT 017 (TAG NO:AHU-A1110-404)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP2.MTB408.AHU404.SYSALM.DP1 / |  | FM008 |  | 2023-07-14 14:08 | 2023-07-14 15:08 | 2023-07-15 15:08 | 24 | 2023-07-14 14:14 | 2023-07-14 20:30 | 376 | 277 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12017475 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC VENT DIRTY - AHU-A1110-404 – T3-09-06 |  | FM008 |  | 2023-07-30 10:14 | 2023-07-30 11:15 | 2023-07-31 11:15 | 24 | 2023-07-30 10:24 | 2023-07-30 12:00 | 96 | 288 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12111519 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC VENT DIRTY AHU-A1110-404 T3-07-27 HOTEL CORRIDOR EAST |  | FM008 |  | 2023-08-22 11:21 | 2023-08-22 12:21 | 2023-08-23 12:21 | 24 | 2023-08-22 11:25 | 2023-08-22 17:35 | 370 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10917289 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | FILTER ALARM - AHU-A1110-404 – T4-09-04 |  | FM008 |  | 2022-08-08 19:02 | 2022-08-08 20:02 | 2022-08-09 20:02 | 24 | 2022-08-08 19:10 | 2022-08-08 20:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2022-10996615 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404- DP3 FILTER ALARM-- |  | FM008 |  | 2022-09-02 10:32 | 2022-09-02 11:32 | 2022-09-03 11:32 | 24 | 2022-09-02 10:40 | 2022-09-02 11:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11161413 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC VENT DIRTY - T3-09-06 |  | FM008 |  | 2022-11-05 16:01 | 2022-11-05 17:01 | 2022-11-06 17:01 | 24 | 2022-11-05 16:08 | 2022-11-05 17:48 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11615996 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC TOO COLD IN CORRIDOR AREA NEAR ROOM # 142 ,HOTEL-EAST WING THIRD FLOOR |  | FM008 |  | 2023-04-04 11:24 | 2023-04-04 12:24 | 2023-04-05 12:24 | 24 | 2023-04-04 11:30 | 2023-04-04 12:55 | 85 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 122305 | Shankar, Mr. Sai | N - - - |  | Voice Communication
| CM-2023-11618460 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM, AHU A1110-404 , T4-09-04 |  | FM008 |  | 2023-04-06 02:14 | 2023-04-06 03:14 | 2023-04-07 03:14 | 24 | 2023-04-06 02:20 | 2023-04-06 03:20 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-11764797 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404)-PD3-FILTER DIRTY -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-05-05 10:33 | 2023-05-05 11:33 | 2023-05-06 11:33 | 24 | 2023-05-05 10:40 | 2023-05-05 12:20 | 100 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11825007 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS AHU-A1110-404 T4-09-04 |  | FM008 |  | 2023-05-27 22:47 | 2023-05-27 23:47 | 2023-05-28 23:47 | 24 | 2023-05-27 22:55 | 2023-05-28 00:30 | 95 | 175 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11867191 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-06-10 12:32 | 2023-06-10 13:32 | 2023-06-11 13:32 | 24 | 2023-06-10 12:37 | 2023-06-10 16:40 | 243 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11946667 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | Dirty AC diffuser in corridor area near T3-08-07 |  | FM008 |  | 2023-07-03 18:00 | 2023-07-03 19:00 | 2023-07-04 19:00 | 24 | 2023-07-03 18:08 | 2023-07-03 20:00 | 112 | 128 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | 134092 | Almario, Mr. Neftali Tinao | N - - - |  | Voice Communication
| CM-2023-11994798 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404-BELT DAMAGE,-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-07-18 00:27 | 2023-07-18 01:27 | 2023-07-19 01:27 | 24 | 2023-07-18 00:32 | 2023-07-18 03:40 | 188 | 278 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 87807 |  |  | FM1127 | Rahman, Mr. Mohammad Habibur | N - - - |  | Voice Communication
| CM-2024-12750397 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404 AC VENT DIRTY HOTEL CORRIDOR |  | FM008 |  | 2024-03-21 10:55 | 2024-03-21 11:55 | 2024-03-22 11:55 | 24 | 2024-03-21 11:00 | 2024-03-21 15:30 | 270 | 545 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12298199 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AC TOO COLD CORRIDOR AREA NEAR ROOM 192 |  | FM008 |  | 2023-10-19 03:12 | 2023-10-19 04:12 | 2023-10-20 04:12 | 24 | 2023-10-19 03:20 | 2023-10-19 06:30 | 190 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | 132547 | Sahoo, Mr. Rakesh Ranjan | N - - - |  | Voice Communication
| CM-2024-12821621 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED -T4-09-04 |  | FM008 |  | 2024-04-11 00:07 | 2024-04-11 01:07 | 2024-04-12 01:07 | 24 | 2024-04-11 00:15 | 2024-04-11 01:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10116867 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404 FILTER DIRTY |  | FM008 |  | 2022-02-08 07:09 | 2022-02-08 08:09 | 2022-02-09 08:09 | 24 | 2022-02-08 07:15 | 2022-02-08 08:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10612343 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM A1110-404 T4-09-04 |  | FM008 |  | 2022-04-29 12:49 | 2022-04-29 13:49 | 2022-04-30 13:49 | 24 | 2022-04-29 12:55 | 2022-04-29 13:45 | 50 | 100 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 85125 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10636309 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | HOTEL ROOM BTN 101 -148 CORRIDOR AREA – AC TOO COLD |  | FM008 |  | 2022-05-09 14:06 | 2022-05-09 15:06 | 2022-05-10 15:06 | 24 | 2022-05-09 14:10 | 2022-05-09 17:15 | 185 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 115535 | Hossain, Mr. Md Parveg | N - - - |  | Voice Communication
| CM-2022-10663531 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | COOLING COIL TEMPERATURE SENSOR NOT WORKING AHU-A1110-404 |  | FM008 |  | 2022-05-15 10:36 | 2022-05-15 11:36 | 2022-05-16 11:36 | 24 | 2022-05-15 10:45 | 2022-05-15 14:29 | 224 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10672612 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-17 08:14 | 2022-05-17 09:14 | 2022-05-18 09:14 | 24 | 2022-05-17 08:20 | 2022-05-17 10:00 | 100 | 155 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11090992 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | SUPPLY FAN V BELT DAMAGED - AHU-A1110-404 |  | FM008 |  | 2022-10-12 02:21 | 2022-10-12 03:21 | 2022-10-13 03:21 | 24 | 2022-10-12 02:30 | 2022-10-12 04:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11095977 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1110-404 T4-09-04 |  | FM008 |  | 2022-10-12 00:04 | 2022-10-12 01:04 | 2022-10-13 01:04 | 24 | 2022-10-12 00:10 | 2022-10-12 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11193463 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | CHILLWATER LINE PAINT FADED -T4-09-04 |  | FM008 |  | 2022-11-16 09:57 | 2022-11-16 10:57 | 2022-11-17 10:57 | 24 | 2022-11-16 10:06 | 2022-11-16 16:00 | 354 | 384 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11304691 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | V-BELT DAMAGED |  | FM008 |  | 2022-12-28 02:03 | 2022-12-28 03:03 | 2022-12-29 03:03 | 24 | 2022-12-28 02:10 | 2022-12-28 04:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 121959 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10790832 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-30 00:10 | 2022-06-30 01:10 | 2022-07-01 01:10 | 24 | 2022-06-30 00:20 | 2022-06-30 03:05 | 165 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2022-10799782 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404 FILTER DIRTY T4-09-04 |  | FM008 |  | 2022-07-02 20:47 | 2022-07-02 21:47 | 2022-07-03 21:47 | 24 | 2022-07-02 21:00 | 2022-07-02 22:00 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 95217 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2023-12139907 | ASD-MTB-FOF009-AHU017 | AIR HANDLING UNIT-05 | AHU-A1110-404 DP1 FILTER DIRTY |  | FM008 |  | 2023-09-01 19:11 | 2023-09-01 20:11 | 2023-09-02 20:11 | 24 | 2023-09-01 19:20 | 2023-09-01 23:45 | 265 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10669932 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU-A1110-406- DP 1 FILTER ALARM- |  | FM008 |  | 2022-05-19 10:36 | 2022-05-19 11:36 | 2022-05-20 11:36 | 24 | 2022-05-19 10:45 | 2022-05-19 13:10 | 145 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17154 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10750238 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-406 – T4-09-04 |  | FM008 |  | 2022-06-19 07:08 | 2022-06-19 08:08 | 2022-06-20 08:08 | 24 | 2022-06-19 07:15 | 2022-06-19 08:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11566503 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | SUPPLY DUCT AIR LEAKAGE T4-09-04 |  | FM008 |  | 2023-03-15 14:07 | 2023-03-15 15:07 | 2023-03-16 15:07 | 24 | 2023-03-15 14:15 | 2023-03-15 18:40 | 265 | 710 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 17053 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12382949 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | RELIEF BEARING NOISY - AHU-A1110-406 – T4-09-04 |  | FM008 |  | 2023-11-15 08:39 | 2023-11-15 09:39 | 2023-11-16 09:39 | 24 | 2023-11-15 08:45 | 2023-11-15 11:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106973 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2024-12533170 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AC TOO COLD - ARRIVAL HALL |  | FM008 |  | 2024-01-05 08:55 | 2024-01-05 09:55 | 2024-01-06 09:55 | 24 | 2024-01-05 09:00 | 2024-01-05 15:05 | 365 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 121959 | 17053 |  |  | 116187 | Mbuge, Mr. Felix Ochieng | N - - - |  | Voice Communication
| CM-2023-11885422 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | SUPPLY FAN FAIL ALARM - AHU-A1110-406 |  | FM008 |  | 2023-06-15 22:30 | 2023-06-15 23:30 | 2023-06-16 23:30 | 24 | 2023-06-15 22:40 | 2023-06-16 02:35 | 235 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 133396 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12299653 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | SUPPLY SIDE MOTOR TEMPERATURE HIGH AHU-A1110-432 |  | FM008 |  | 2023-10-17 15:29 | 2023-10-17 16:29 | 2023-10-18 16:29 | 24 | 2023-10-17 15:35 | 2023-10-17 18:40 | 185 | 85 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | OVER HEATING | REPAIRED THE FAULT | 106972 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-10952206 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU RELIEF BELT DAMAGED |  | FM008 |  | 2022-08-16 21:11 | 2022-08-16 22:11 | 2022-08-17 22:11 | 24 | 2022-08-16 21:15 | 2022-08-16 22:30 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11197303 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING.-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-11-17 14:06 | 2022-11-17 15:06 | 2022-11-18 15:06 | 24 | 2022-11-17 14:15 | 2022-11-17 16:10 | 115 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 77406 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11455679 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU-A1110-406 FILTER DIRTY |  | FM008 |  | 2023-02-14 03:55 | 2023-02-14 04:55 | 2023-02-15 04:55 | 24 | 2023-02-14 04:00 | 2023-02-14 06:15 | 135 | 270 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11918297 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | EXHAUST GRILL DIRTY --T1-11-36)- |  | FM008 |  | 2023-06-25 07:18 | 2023-06-25 08:18 | 2023-06-26 08:18 | 24 | 2023-06-25 07:25 | 2023-06-25 10:00 | 155 | 465 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 17053 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2024-12685944 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1110-406, T4-09-04 |  | FM008 |  | 2024-02-27 20:23 | 2024-02-27 21:23 | 2024-02-28 21:23 | 24 | 2024-02-27 20:30 | 2024-02-27 22:10 | 100 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2024-12707234 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU-A1110-406 FILTER DIRTY - T4-09-04 |  | FM008 |  | 2024-03-05 07:51 | 2024-03-05 08:51 | 2024-03-06 08:51 | 24 | 2024-03-05 07:55 | 2024-03-05 12:00 | 245 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12365262 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | SUPPLY BLOWER VERY NOISY - AHU-A1110-406 – C4 09 04 |  | FM008 |  | 2023-11-08 08:00 | 2023-11-08 09:00 | 2023-11-09 09:00 | 24 | 2023-11-08 08:10 | 2023-11-08 11:40 | 210 | 725 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 132112 | 17053 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2024-12609678 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY |  | FM008 |  | 2024-01-31 19:00 | 2024-01-31 20:00 | 2024-02-01 20:00 | 24 | 2024-01-31 19:05 | 2024-01-31 21:30 | 145 | 435 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 17053 |  |  | FM13044 | Jayasingha Arachchige, Mr. Sameera Wasana Indrajith | N - - - |  | Voice Communication
| CM-2022-10121074 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-09-04 |  | FM008 |  | 2022-02-09 07:48 | 2022-02-09 08:48 | 2022-02-10 08:48 | 24 | 2022-02-09 07:55 | 2022-02-09 12:00 | 245 | 115 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10343404 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | DP2 FILTER ALARM |  | FM008 |  | 2022-04-09 13:18 | 2022-04-09 14:18 | 2022-04-10 14:18 | 24 | 2022-04-09 13:25 | 2022-04-09 16:00 | 155 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 68060 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-10767364 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU-A1110-406- DRAIN LINE U TRAP BLOCKED –T4-09-04 |  | FM008 |  | 2022-06-20 21:48 | 2022-06-20 22:48 | 2022-06-21 22:48 | 24 | 2022-06-20 21:55 | 2022-06-20 23:30 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17154 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11041357 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-09-23 10:35 | 2022-09-23 11:35 | 2022-09-24 11:35 | 24 | 2022-09-23 10:40 | 2022-09-23 18:00 | 440 | 246 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11194410 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU-A1110-406- SUPPL AND RELIEF BELT DAMAGED - T4-09-04- |  | FM008 |  | 2022-11-17 09:05 | 2022-11-17 10:05 | 2022-11-18 10:05 | 24 | 2022-11-17 09:14 | 2022-11-17 12:00 | 166 | 332 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17154 | 87807 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11297182 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-406 – T4-08-04 |  | FM008 |  | 2022-12-20 07:15 | 2022-12-20 08:15 | 2022-12-21 08:15 | 24 | 2022-12-20 07:20 | 2022-12-20 09:30 | 130 | 260 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10299710 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T4-09-04 |  | FM008 |  | 2022-03-27 11:08 | 2022-03-27 12:08 | 2022-03-28 12:08 | 24 | 2022-03-27 11:17 | 2022-03-27 12:47 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10569037 | ASD-MTB-FOF009-AHU019 | AIR HANDLING UNIT-05 | AHU-A1110-406 FILTER DIRTY T4-09-04 |  | FM008 |  | 2022-04-23 00:07 | 2022-04-23 01:07 | 2022-04-24 01:07 | 24 | 2022-04-23 00:16 | 2022-04-23 03:50 | 214 | 339 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10354314 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY-AHU-A1110-409 |  | FM008 |  | 2022-04-11 04:11 | 2022-04-11 05:11 | 2022-04-12 05:11 | 24 | 2022-04-11 04:20 | 2022-04-11 05:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10654428 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-409 - DRAIN LINE IS RUSTED – T4-08-04 |  | FM008 |  | 2022-05-11 22:14 | 2022-05-11 23:14 | 2022-05-12 23:14 | 24 | 2022-05-11 22:20 | 2022-05-11 23:55 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94954 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-11985784 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | GREASE EXHAUST HOOD DIRTY,GEF-A1110-401, SN1030-SHAWARMA & JAIPUR |  | FM008 |  | 2023-07-17 07:54 | 2023-07-17 08:54 | 2023-07-18 08:54 | 24 | 2023-07-17 08:03 | 2023-07-17 12:00 | 237 | 1422 | 6 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12058315 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-409-FILTER DIRTY -FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-08-07 10:59 | 2023-08-07 11:59 | 2023-08-08 11:59 | 24 | 2023-08-07 11:05 | 2023-08-07 14:00 | 175 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11486769 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | GEH-1FKFC001 GREASE EXHAUST HOOD FILTER DIRTY SN-1030 KFC |  | FM008 |  | 2023-02-26 07:57 | 2023-02-26 08:57 | 2023-02-27 08:57 | 24 | 2023-02-26 08:05 | 2023-02-26 12:05 | 240 | 960 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-12209856 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1110-409) – T4 08 04 |  | FM008 |  | 2023-09-22 19:47 | 2023-09-22 20:47 | 2023-09-23 20:47 | 24 | 2023-09-22 19:50 | 2023-09-22 22:05 | 135 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12280644 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | ABNORMAL NOISE COMING FROM SUPPLY SIDE BEARING - AHU-A1110-409 – T4-08-04 |  | FM008 |  | 2023-10-12 14:04 | 2023-10-12 15:04 | 2023-10-13 15:04 | 24 | 2023-10-12 14:10 | 2023-10-12 18:45 | 275 | 865 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106973 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11006340 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-09-12 00:21 | 2022-09-12 01:21 | 2022-09-13 01:21 | 24 | 2022-09-12 00:30 | 2022-09-12 02:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11062617 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-409 DP1 FILTER DIRTY -AREA 010 |  | FM008 |  | 2022-09-27 19:14 | 2022-09-27 20:14 | 2022-09-28 20:14 | 24 | 2022-09-27 19:20 | 2022-09-27 22:15 | 175 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 87807 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11139028 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2022-10-30 14:30 | 2022-10-30 15:30 | 2022-10-31 15:30 | 24 | 2022-10-30 14:40 | 2022-10-30 16:08 | 88 | 176 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11862841 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | FILTER DIRTY - T4-10-03 |  | FM008 |  | 2023-06-08 00:29 | 2023-06-08 01:29 | 2023-06-09 01:29 | 24 | 2023-06-08 00:35 | 2023-06-08 02:05 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11935453 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED, AHU-A1110-409, C4-08-04 |  | FM008 |  | 2023-07-01 12:03 | 2023-07-01 13:03 | 2023-07-02 13:03 | 24 | 2023-07-01 12:10 | 2023-07-01 14:00 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 124475 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-10145743 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-409-FILTER DIRTY-T4-10-03 |  | FM008 |  | 2022-02-15 00:15 | 2022-02-15 01:15 | 2022-02-16 01:15 | 24 | 2022-02-15 00:25 | 2022-02-15 02:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-11970109 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T4-08-04 |  | FM008 |  | 2023-07-10 10:10 | 2023-07-10 11:10 | 2023-07-11 11:10 | 24 | 2023-07-10 10:15 | 2023-07-10 16:10 | 355 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10042179 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY -AHU-A1110-409)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010-T4-08-04 |  | FM008 |  | 2022-01-12 00:14 | 2022-01-12 01:14 | 2022-01-13 01:14 | 24 | 2022-01-12 00:20 | 2022-01-12 06:20 | 360 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10050002 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-409-HEAT WHEEL TERMINATOIN BOX FLEXIBLE CONNECTR DAMAGED |  | FM008 |  | 2022-01-15 09:45 | 2022-01-15 10:45 | 2022-01-16 10:45 | 24 | 2022-01-15 09:55 | 2022-01-15 11:22 | 87 | 174 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 95217 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10153392 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | RELIEF V BELT DAMAGED - AHU-A1110-409 – T4-10-03 |  | FM008 |  | 2022-02-19 11:03 | 2022-02-19 12:03 | 2022-02-20 12:03 | 24 | 2022-02-19 11:10 | 2022-02-19 14:15 | 185 | 155 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10308156 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | RAD OPEN FAIL ALARM –T4-10-03 |  | FM008 |  | 2022-04-01 17:12 | 2022-04-01 18:12 | 2022-04-02 18:12 | 24 | 2022-04-01 17:20 | 2022-04-01 18:10 | 50 | 100 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 17333 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10799783 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-109 FILTER DIRTY T4-08-04 |  | FM008 |  | 2022-07-02 20:50 | 2022-07-02 21:50 | 2022-07-03 21:50 | 24 | 2022-07-02 21:00 | 2022-07-02 23:05 | 125 | 125 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 95217 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2022-10912681 | ASD-MTB-FOF010-AHU022 | AIR HANDLING UNIT-05 | AHU-A1110-409- FILTER DIRTY- |  | FM008 |  | 2022-08-02 19:06 | 2022-08-02 20:06 | 2022-08-03 20:06 | 24 | 2022-08-02 19:10 | 2022-08-02 20:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 76858 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11188832 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT FUSED |  | FM008 |  | 2022-11-14 00:43 | 2022-11-14 01:43 | 2022-11-15 01:43 | 24 | 2022-11-14 00:50 | 2022-11-14 02:15 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 68060 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12058316 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | AHU-A1110-411-FILTER DIRTY-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-08-07 11:02 | 2023-08-07 12:02 | 2023-08-08 12:02 | 24 | 2023-08-07 11:10 | 2023-08-07 14:30 | 200 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12206999 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-09-22 19:16 | 2023-09-22 20:16 | 2023-09-23 20:16 | 24 | 2023-09-22 19:20 | 2023-09-22 23:40 | 260 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12511657 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | SUPPLY BLOWER BEARING NOISY - T4-08-04 (AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010) |  | FM008 |  | 2023-12-28 08:29 | 2023-12-28 09:29 | 2023-12-29 09:29 | 24 | 2023-12-28 08:35 | 2023-12-28 12:35 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 138627 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2024-12647972 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | MCC PANEL BASE RUSTED-AIR HANDLING UNIT 024 (TAG NO:AHU-A1110-411)- |  | FM008 |  | 2024-02-14 00:37 | 2024-02-14 01:37 | 2024-02-15 01:37 | 24 | 2024-02-14 00:46 | 2024-02-14 03:45 | 179 | 358 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 17053 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2023-11824399 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | AHU-A1121-203- BELT DAMAGED- T4-21-20 - |  | FM008 |  | 2023-05-25 12:40 | 2023-05-25 13:40 | 2023-05-26 13:40 | 24 | 2023-05-25 12:45 | 2023-05-25 16:00 | 195 | 235 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-11006341 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED |  | FM008 |  | 2022-09-12 00:22 | 2022-09-12 01:22 | 2022-09-13 01:22 | 24 | 2022-09-12 00:30 | 2022-09-12 02:05 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11063597 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1110-411 |  | FM008 |  | 2022-09-28 07:20 | 2022-09-28 08:20 | 2022-09-29 08:20 | 24 | 2022-09-28 07:25 | 2022-09-28 09:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106972 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10344092 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | RELIEF VFD DISPLAY NOT CLEAR-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-04-10 10:09 | 2022-04-10 11:09 | 2022-04-11 11:09 | 24 | 2022-04-10 10:18 | 2022-04-10 13:44 | 206 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106914 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11667925 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED – (AHU-A1110-411) - T4 21 03 |  | FM008 |  | 2023-04-15 09:03 | 2023-04-15 10:03 | 2023-04-16 10:03 | 24 | 2023-04-15 09:13 | 2023-04-15 11:11 | 118 | 236 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 132112 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10042180 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY -AHU-A1110-411)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010-T4-08-04 |  | FM008 |  | 2022-01-12 00:17 | 2022-01-12 01:17 | 2022-01-13 01:17 | 24 | 2022-01-12 00:26 | 2022-01-12 05:40 | 314 | 189 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10141354 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-15 19:07 | 2022-02-15 20:07 | 2022-02-16 20:07 | 24 | 2022-02-15 19:17 | 2022-02-15 23:25 | 248 | 250 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10153391 | ASD-MTB-FOF010-AHU024 | AIR HANDLING UNIT-05 | RELIEF V BELT DAMAGED - AHU-A1110-411 – T4-21-03 |  | FM008 |  | 2022-02-19 11:01 | 2022-02-19 12:01 | 2022-02-20 12:01 | 24 | 2022-02-19 11:05 | 2022-02-19 12:20 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10048481 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 BELT DAMAGED-- |  | FM008 |  | 2022-01-13 14:48 | 2022-01-13 15:48 | 2022-01-14 15:48 | 24 | 2022-01-13 14:57 | 2022-01-13 18:10 | 193 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11015293 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 FILTER ALARM- - |  | FM008 |  | 2022-09-13 00:10 | 2022-09-13 01:10 | 2022-09-14 01:10 | 24 | 2022-09-13 00:15 | 2022-09-13 01:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11029989 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413- AIR LEAKAGE FORM SUPPLY DUCT JOINT - T1-10-12 |  | FM008 |  | 2022-09-18 11:15 | 2022-09-18 12:15 | 2022-09-19 12:15 | 24 | 2022-09-18 11:20 | 2022-09-18 14:15 | 175 | 525 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 87807 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11261312 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | FRESH AIR DUCT INSULATION DAMAGED - AHU-A1110-413 - T4-08-21 |  | FM008 |  | 2022-12-11 10:36 | 2022-12-11 11:36 | 2022-12-12 11:36 | 24 | 2022-12-11 10:40 | 2022-12-11 15:10 | 270 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11354277 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413- DP3- FILTER ALARM ACTIVATED-- |  | FM008 |  | 2023-01-07 08:46 | 2023-01-07 09:46 | 2023-01-08 09:46 | 24 | 2023-01-07 08:55 | 2023-01-07 14:15 | 320 | 265 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11445728 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 DP1 FILTER DIRTY |  | FM008 |  | 2023-02-11 10:55 | 2023-02-11 11:55 | 2023-02-12 11:55 | 24 | 2023-02-11 11:04 | 2023-02-11 13:00 | 116 | 232 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12363711 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413- BEARING NOISY T4-08-04 |  | FM008 |  | 2023-11-07 08:17 | 2023-11-07 09:17 | 2023-11-08 09:17 | 24 | 2023-11-07 08:25 | 2023-11-07 14:05 | 340 | 905 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 87807 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-11823187 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | DP2 RELIEF FILTER STATUS - AIR HANDLING UNIT 026 (TAG NO:AHU-A1110-413)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-05-25 12:22 | 2023-05-25 13:22 | 2023-05-26 13:22 | 24 | 2023-05-25 12:30 | 2023-05-25 18:00 | 330 | 290 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17053 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2024-12650184 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU LIGHTING SWITCH FAULTY -AIR HANDLING UNIT 026 (TAG NO:AHU-A1110-413)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2024-02-14 19:03 | 2024-02-14 20:03 | 2024-02-15 20:03 | 24 | 2024-02-14 19:10 | 2024-02-14 21:53 | 163 | 326 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17336 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-11028057 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 – AHU INSIDE LAMP IS NOT WORKING – T4-10-03 |  | FM008 |  | 2022-09-16 21:47 | 2022-09-16 22:47 | 2022-09-17 22:47 | 24 | 2022-09-16 21:55 | 2022-09-16 23:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | THE EQUIPMENT HAS BEEN SWITCH OFF | THE POWER HAS BEEN RESTORED | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11062619 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 DP1 FILTER DIRTY |  | FM008 |  | 2022-09-27 19:17 | 2022-09-27 20:17 | 2022-09-28 20:17 | 24 | 2022-09-27 19:25 | 2022-09-27 23:55 | 270 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11660939 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413) – LIGHTING FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2023-04-14 14:40 | 2023-04-14 15:40 | 2023-04-15 15:40 | 24 | 2023-04-14 14:48 | 2023-04-14 16:15 | 87 | 174 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-12462053 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-12-11 20:40 | 2023-12-11 21:40 | 2023-12-12 21:40 | 24 | 2023-12-11 20:45 | 2023-12-11 22:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2023-12509921 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-413 |  | FM008 |  | 2023-12-27 10:33 | 2023-12-27 11:33 | 2023-12-28 11:33 | 24 | 2023-12-27 10:40 | 2023-12-27 12:10 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-10830354 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 DP1 FILTER ALARM T4-10-03 |  | FM008 |  | 2022-07-13 00:06 | 2022-07-13 01:06 | 2022-07-14 01:06 | 24 | 2022-07-13 00:10 | 2022-07-13 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10934705 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | AHU-A1110-413 – DP2 AND 3 FILTER ALARM – T4-10-03 |  | FM008 |  | 2022-08-13 11:13 | 2022-08-13 12:13 | 2022-08-14 12:13 | 24 | 2022-08-13 11:20 | 2022-08-13 13:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12257210 | ASD-MTB-FOF010-AHU026 | AIR HANDLING UNIT-05 | FLEXIBLE CONNECTOR DAMAGED -T4-10-03 |  | FM008 |  | 2023-10-07 01:39 | 2023-10-07 02:39 | 2023-10-08 02:39 | 24 | 2023-10-07 01:45 | 2023-10-07 05:00 | 195 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17333 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10160474 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | CHILLED WATER LINE INSULATION DAMAGED - T4-08-04 |  | FM008 |  | 2022-02-21 22:25 | 2022-02-21 23:25 | 2022-02-22 23:25 | 24 | 2022-02-21 22:35 | 2022-02-21 23:55 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2022-10570398 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU-A1110-408 – DP 3 FILTER ALARM T4-09-04 |  | FM008 |  | 2022-04-18 01:45 | 2022-04-18 02:45 | 2022-04-19 02:45 | 24 | 2022-04-18 01:54 | 2022-04-18 03:30 | 96 | 170 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10669936 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU-A1110-408- DP 3 FILTER ALARM- |  | FM008 |  | 2022-05-19 10:39 | 2022-05-19 11:39 | 2022-05-20 11:39 | 24 | 2022-05-19 10:45 | 2022-05-19 12:00 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17154 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10998401 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | CHILLED WATER INSULATION IS DAMAGED T4-09-04 |  | FM008 |  | 2022-09-07 07:40 | 2022-09-07 08:40 | 2022-09-08 08:40 | 24 | 2022-09-07 07:45 | 2022-09-07 09:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-11101545 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | RELEASE AND SUPPLY V BELT DAMAGED - T4-09-04 |  | FM008 |  | 2022-10-13 21:01 | 2022-10-13 22:01 | 2022-10-14 22:01 | 24 | 2022-10-13 21:10 | 2022-10-14 00:35 | 205 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 87807 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2023-11680852 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU-A1110-408 AHU CABIN LIGHT NOT WORKING T4-09-04 |  | FM008 |  | 2023-04-17 19:20 | 2023-04-17 20:20 | 2023-04-18 20:20 | 24 | 2023-04-17 19:25 | 2023-04-17 23:50 | 265 | 255 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2024-12728968 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU-A1110-408;ABNORMAL SOUND FROM SUPPLY SIDE - T4-07-31 |  | FM008 |  | 2024-03-11 07:40 | 2024-03-11 08:40 | 2024-03-12 08:40 | 24 | 2024-03-11 07:45 | 2024-03-11 18:30 | 645 | 605 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11028063 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM-AHU-A1110-408)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-09-17 00:14 | 2022-09-17 01:14 | 2022-09-18 01:14 | 24 | 2022-09-17 00:23 | 2022-09-17 03:45 | 202 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11993805 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-07-18 01:13 | 2023-07-18 02:13 | 2023-07-19 02:13 | 24 | 2023-07-18 01:20 | 2023-07-18 06:50 | 330 | 278 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12346853 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | BLOWER PAINT FADED - AHU-A1110-408 – T4-09-04 |  | FM008 |  | 2023-11-04 07:08 | 2023-11-04 08:08 | 2023-11-05 08:08 | 24 | 2023-11-04 07:15 | 2023-11-04 09:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 133396 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10997914 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | CHILLED WATER INSULATION DAMAGED - T4-09-04, MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-09-04 15:31 | 2022-09-04 16:31 | 2022-09-05 16:31 | 24 | 2022-09-04 15:40 | 2022-09-04 18:00 | 140 | 280 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2023-11459340 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | DP3-FILETER ALARM-AHU-A1110-408-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-02-14 22:17 | 2023-02-14 23:17 | 2023-02-15 23:17 | 24 | 2023-02-14 22:25 | 2023-02-14 23:40 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11835023 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-408– MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-05-29 21:27 | 2023-05-29 22:27 | 2023-05-30 22:27 | 24 | 2023-05-29 21:30 | 2023-05-29 22:55 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-11878877 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | D1 FILTER ALARM -T4-09-04 |  | FM008 |  | 2023-06-14 10:56 | 2023-06-14 11:56 | 2023-06-15 11:56 | 24 | 2023-06-14 11:05 | 2023-06-14 16:00 | 295 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | BMS
| CM-2024-12595621 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -T4-09-04 |  | FM008 |  | 2024-01-27 00:09 | 2024-01-27 01:09 | 2024-01-28 01:09 | 24 | 2024-01-27 00:15 | 2024-01-27 01:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12798658 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2024-04-07 09:07 | 2024-04-07 10:07 | 2024-04-08 10:07 | 24 | 2024-04-07 09:15 | 2024-04-07 14:40 | 325 | 290 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10275927 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | AHU-A1110-408-T4-09-04-AHU FILTER DIRTY |  | FM008 |  | 2022-03-24 07:05 | 2022-03-24 08:05 | 2022-03-25 08:05 | 24 | 2022-03-24 07:10 | 2022-03-24 08:00 | 50 | 100 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10634398 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-05-09 13:29 | 2022-05-09 14:29 | 2022-05-10 14:29 | 24 | 2022-05-09 13:35 | 2022-05-09 17:40 | 245 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11197780 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1110-408 |  | FM008 |  | 2022-11-19 07:13 | 2022-11-19 08:13 | 2022-11-20 08:13 | 24 | 2022-11-19 07:20 | 2022-11-19 10:50 | 210 | 420 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 124475 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10781902 | ASD-MTB-FOF009-AHU021 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM |  | FM008 |  | 2022-06-27 14:43 | 2022-06-27 15:43 | 2022-06-28 15:43 | 24 | 2022-06-27 14:50 | 2022-06-27 16:50 | 120 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68060 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10160504 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | DRAIN LINE FLOOR TRAP RUSTY -T4-02-04 |  | FM008 |  | 2022-02-22 04:23 | 2022-02-22 05:23 | 2022-02-23 05:23 | 24 | 2022-02-22 04:30 | 2022-02-22 05:30 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | UNIT IS RUSTED | CLEANED & REPAINT THE UNIT | 17333 | 55709 |  |  | FM9818 | Ajay Kumar Singh, Mr. | N - - - |  | Voice Communication
| CM-2022-10342337 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-416 – T4-09-04 |  | FM008 |  | 2022-04-09 18:10 | 2022-04-09 19:10 | 2022-04-10 19:10 | 24 | 2022-04-09 18:20 | 2022-04-10 00:30 | 370 | 370 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10972007 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU-A1110-416-ACCESS DOOR AIR LEAKAGE-T4-09-04 |  | FM008 |  | 2022-08-26 01:17 | 2022-08-26 02:17 | 2022-08-27 02:17 | 24 | 2022-08-26 01:25 | 2022-08-26 03:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 95217 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-11806323 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU-A1110-416- DP1 FILTER ALARM-T4-09-04 |  | FM008 |  | 2023-05-19 00:35 | 2023-05-19 01:35 | 2023-05-20 01:35 | 24 | 2023-05-19 00:45 | 2023-05-19 03:40 | 175 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12097466 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU-A1110-416 SUPPLY DUCT DAMAGED T4-09-04 |  | FM008 |  | 2023-08-16 19:15 | 2023-08-16 20:15 | 2023-08-17 20:15 | 24 | 2023-08-16 19:20 | 2023-08-16 23:35 | 255 | 545 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12095205 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | CHILLED WATER PIPE LINE PAINT FADED :AHU-A1110-416-418-408 |  | FM008 |  | 2023-08-15 22:23 | 2023-08-15 23:23 | 2023-08-16 23:23 | 24 | 2023-08-15 22:30 | 2023-08-15 23:59 | 89 | 267 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-11623534 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-416 – MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-04-05 07:53 | 2023-04-05 08:53 | 2023-04-06 08:53 | 24 | 2023-04-05 08:00 | 2023-04-05 13:00 | 300 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 132112 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10932265 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU-A1110-416 FILTER ALARM T4-09-04 |  | FM008 |  | 2022-08-13 19:03 | 2022-08-13 20:03 | 2022-08-14 20:03 | 24 | 2022-08-13 19:10 | 2022-08-13 21:00 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11103145 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU-A1110-416 ACTUATOR MISALIGNED |  | FM008 |  | 2022-10-16 07:26 | 2022-10-16 08:26 | 2022-10-17 08:26 | 24 | 2022-10-16 07:35 | 2022-10-16 11:30 | 235 | 145 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68485 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12321062 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1110-416 – T4-09-04 |  | FM008 |  | 2023-10-24 13:29 | 2023-10-24 14:29 | 2023-10-25 14:29 | 24 | 2023-10-24 13:36 | 2023-10-24 18:15 | 279 | 230 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-12384941 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | BEARING NOISY – (AHU-A1110-416) - T4 09 04 |  | FM008 |  | 2023-11-16 07:56 | 2023-11-16 08:56 | 2023-11-17 08:56 | 24 | 2023-11-16 08:05 | 2023-11-16 11:35 | 210 | 630 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 132112 | 17053 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12297869 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1110-416 - T4-09-04 |  | FM008 |  | 2023-10-18 10:54 | 2023-10-18 11:54 | 2023-10-19 11:54 | 24 | 2023-10-18 11:00 | 2023-10-18 17:00 | 360 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2023-12430020 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2023-12-01 11:02 | 2023-12-01 12:02 | 2023-12-02 12:02 | 24 | 2023-12-01 11:10 | 2023-12-01 18:30 | 440 | 246 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM12612 | SUGIL UNUKKOOR, | N - - - |  | Voice Communication
| CM-2022-10750052 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | DRAIN PAN U-TRAP BLOCKED AHU-A1110-416 - T4-09-04 |  | FM008 |  | 2022-06-18 03:46 | 2022-06-18 04:46 | 2022-06-19 04:46 | 24 | 2022-06-18 03:55 | 2022-06-18 05:35 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 121959 | 87807 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2022-11041354 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-09-23 10:32 | 2022-09-23 11:32 | 2022-09-24 11:32 | 24 | 2022-09-23 10:40 | 2022-09-23 15:15 | 275 | 230 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11080755 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | CHILLED WATER LINE INSULATION DAMAGED |  | FM008 |  | 2022-10-09 01:50 | 2022-10-09 02:50 | 2022-10-10 02:50 | 24 | 2022-10-09 01:58 | 2022-10-09 05:00 | 182 | 280 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11116226 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT ILLUMINATING - AHU-1110-416 – T4-09-04 |  | FM008 |  | 2022-10-18 04:54 | 2022-10-18 05:54 | 2022-10-19 05:54 | 24 | 2022-10-18 05:02 | 2022-10-18 06:32 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11113258 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | SUPPLY AND RELIEF FAN V BELT DAMAGED - MEC ROOM T4-09-04 |  | FM008 |  | 2022-10-18 00:07 | 2022-10-18 01:07 | 2022-10-19 01:07 | 24 | 2022-10-18 00:10 | 2022-10-18 03:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11277363 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | AHU-A1110-416– CHILLED WATER LINE INSULATION DAMAGED- - |  | FM008 |  | 2022-12-18 00:34 | 2022-12-18 01:34 | 2022-12-19 01:34 | 24 | 2022-12-18 00:40 | 2022-12-18 02:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10164097 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-23 09:59 | 2022-02-23 10:59 | 2022-02-24 10:59 | 24 | 2022-02-23 10:05 | 2022-02-23 12:00 | 115 | 345 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-12296791 | ASD-MTB-FOF009-AHU029 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2023-10-18 00:09 | 2023-10-18 01:09 | 2023-10-19 01:09 | 24 | 2023-10-18 00:15 | 2023-10-18 05:40 | 325 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10133681 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU031 FILTER BLOCKED – T4-09-04 |  | FM008 |  | 2022-02-13 09:17 | 2022-02-13 10:17 | 2022-02-14 10:17 | 24 | 2022-02-13 09:25 | 2022-02-13 11:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106976 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10321672 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS AHU-A1110-418 |  | FM008 |  | 2022-04-05 10:55 | 2022-04-05 11:55 | 2022-04-06 11:55 | 24 | 2022-04-05 11:05 | 2022-04-05 20:20 | 555 | 155 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10995488 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AC NOT WORKING - TEDDY BEAR INFORMATION DESK AREA |  | FM008 |  | 2022-09-06 17:43 | 2022-09-06 18:43 | 2022-09-07 18:43 | 24 | 2022-09-06 17:53 | 2022-09-06 18:40 | 47 | 47 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 94954 |  |  | 91583 | Castor, Ms. Leann Joy Dela Pena | N - - - |  | E-mail
| CM-2022-11159431 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-418 - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-11-03 07:09 | 2022-11-03 08:09 | 2022-11-04 08:09 | 24 | 2022-11-03 07:15 | 2022-11-03 09:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11697979 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | RELEASE FAN BELT DAMAGED - AHU-A1110-418 – MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-04-24 22:00 | 2023-04-24 23:00 | 2023-04-25 23:00 | 24 | 2023-04-24 22:06 | 2023-04-24 23:58 | 112 | 336 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11859991 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU-A1110-418 FILTER IS DIRTY |  | FM008 |  | 2023-06-06 10:19 | 2023-06-06 11:19 | 2023-06-07 11:19 | 24 | 2023-06-06 10:29 | 2023-06-06 17:10 | 401 | 366 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 94954 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12189304 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – T4-09-04 |  | FM008 |  | 2023-09-16 09:42 | 2023-09-16 10:42 | 2023-09-17 10:42 | 24 | 2023-09-16 09:50 | 2023-09-16 11:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10922490 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | TEDDY BEAR INFORMATION DESK AREA - AC TOO HOT |  | FM008 |  | 2022-08-07 23:27 | 2022-08-08 00:27 | 2022-08-09 00:27 | 24 | 2022-08-07 23:35 | 2022-08-08 00:05 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 55709 |  |  | 73060 | Sherestha, Mr. Kumar | N - - - |  | Voice Communication
| CM-2022-10949869 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED - AHU-A1110-418 – T4-09-04 |  | FM008 |  | 2022-08-15 09:26 | 2022-08-15 10:26 | 2022-08-16 10:26 | 24 | 2022-08-15 09:35 | 2022-08-15 12:30 | 175 | 215 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 55709 |  |  | FM9671 | Karunagoda Mudalige, Mr. Kasun Lakmal | N - - - |  | Voice Communication
| CM-2022-11112455 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | REILF & SUPPLY WEE BELT IS DAMAGED - AHU-A1110-418 - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2022-10-18 19:07 | 2022-10-18 20:07 | 2022-10-19 20:07 | 24 | 2022-10-18 19:15 | 2022-10-18 22:30 | 195 | 390 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11893632 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AC IS TOO HOT - TEDDY BEAR AREA INFORMATION DESK |  | FM008 |  | 2023-06-19 00:58 | 2023-06-19 01:58 | 2023-06-20 01:58 | 24 | 2023-06-19 01:03 | 2023-06-19 06:25 | 322 | 67 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 87807 | 87807 |  |  | 73060 | Sherestha, Mr. Kumar | N - - - |  | Voice Communication
| CM-2023-11908448 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED-AIR HANDLING UNIT 031 (TAG NO:AHU-A1110-418)- |  | FM008 |  | 2023-06-20 03:25 | 2023-06-20 04:25 | 2023-06-21 04:25 | 24 | 2023-06-20 03:30 | 2023-06-20 05:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17573 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11973073 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP2.MTB418.AHU418.SYSALM.DP3 / ?AIR HANDLING UNIT 031 (TAG NO:AHU-A1110-418)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-07-12 17:19 | 2023-07-12 18:19 | 2023-07-13 18:19 | 24 | 2023-07-12 17:20 | 2023-07-12 20:30 | 190 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12095213 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU-A1110-418 filter dirty T4-09-04 |  | FM008 |  | 2023-08-16 00:05 | 2023-08-16 01:05 | 2023-08-17 01:05 | 24 | 2023-08-16 00:10 | 2023-08-16 01:45 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12206489 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-09-21 11:03 | 2023-09-21 12:03 | 2023-09-22 12:03 | 24 | 2023-09-21 11:10 | 2023-09-21 13:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12378188 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AC TOO COLD - TEDDY BEAR AREA |  | FM008 |  | 2023-11-15 02:55 | 2023-11-15 03:55 | 2023-11-16 03:55 | 24 | 2023-11-15 03:06 | 2023-11-15 04:06 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 87807 |  |  | 116187 | Mbuge, Mr. Felix Ochieng | N - - - |  | Voice Communication
| CM-2024-12572033 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -T4-09-04 |  | FM008 |  | 2024-01-19 15:02 | 2024-01-19 16:02 | 2024-01-20 16:02 | 24 | 2024-01-19 15:10 | 2024-01-19 17:45 | 155 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-11138976 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AIR LEAKING FROM ACCESS DOOR NEAR OF SN-1020 AHU-A1110-418 |  | FM008 |  | 2022-10-30 09:03 | 2022-10-30 10:03 | 2022-10-31 10:03 | 24 | 2022-10-30 09:12 | 2022-10-30 11:45 | 153 | 346 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106972 | 17053 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2023-11465201 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2023-02-17 00:03 | 2023-02-17 01:03 | 2023-02-18 01:03 | 24 | 2023-02-17 00:10 | 2023-02-17 01:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2023-11579537 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP2 FILTER DIRTY - AHU-A1110-418 , T4-09-04 |  | FM008 |  | 2023-03-21 00:10 | 2023-03-21 01:10 | 2023-03-22 01:10 | 24 | 2023-03-21 00:20 | 2023-03-21 01:45 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11674639 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU-A1110-418 FILTER DIRTY T4-09-04 |  | FM008 |  | 2023-04-18 00:04 | 2023-04-18 01:04 | 2023-04-19 01:04 | 24 | 2023-04-18 00:08 | 2023-04-18 02:08 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11918299 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED -AHU-A1110-418)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-06-25 07:21 | 2023-06-25 08:21 | 2023-06-26 08:21 | 24 | 2023-06-25 07:25 | 2023-06-25 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-12321065 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1110-418 – T4-08-04 |  | FM008 |  | 2023-10-24 13:31 | 2023-10-24 14:31 | 2023-10-25 14:31 | 24 | 2023-10-24 13:37 | 2023-10-24 16:50 | 193 | 230 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2024-12575787 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1110-418,T4-09-04 |  | FM008 |  | 2024-01-20 00:26 | 2024-01-20 01:26 | 2024-01-21 01:26 | 24 | 2024-01-20 00:32 | 2024-01-20 03:00 | 148 | 296 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM13044 | Jayasingha Arachchige, Mr. Sameera Wasana Indrajith | N - - - |  | Voice Communication
| CM-2023-12363297 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | ORYX LOUNGE AC IN TOO COLD (BLOWING TOWARDS LOU VIRION STORE/ BEHIND THE TEDDY BEAR) |  | FM008 |  | 2023-11-07 08:52 | 2023-11-07 09:52 | 2023-11-08 09:52 | 24 | 2023-11-07 09:00 | 2023-11-07 14:30 | 330 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  |  | rodger-LV staff | N - - - |  | Voice Communication
| CM-2022-10080446 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – T4-09-04 |  | FM008 |  | 2022-01-27 00:44 | 2022-01-27 01:44 | 2022-01-28 01:44 | 24 | 2022-01-27 00:50 | 2022-01-27 04:40 | 230 | 215 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10325097 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AC TOO HOT - TEDDY BEAR INFO DESK |  | FM008 |  | 2022-04-04 17:15 | 2022-04-04 18:15 | 2022-04-05 18:15 | 24 | 2022-04-04 17:25 | 2022-04-04 18:00 | 35 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 17053 |  |  | 99105 | Calagos, Ms. Mae Loren Anabeso | N - - - |  | Voice Communication
| CM-2022-10934639 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1110-418 |  | FM008 |  | 2022-08-12 19:51 | 2022-08-12 20:51 | 2022-08-13 20:51 | 24 | 2022-08-12 20:00 | 2022-08-12 23:20 | 200 | 248 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 55709 |  |  | FM0459 | MANHANDAVIDA SHAHEEL | N - - - |  | BMS
| CM-2022-11041356 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-09-23 10:33 | 2022-09-23 11:33 | 2022-09-24 11:33 | 24 | 2022-09-23 10:40 | 2022-09-23 16:35 | 355 | 238 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11112523 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU-A1110-418 – DP1 FILTER ALARM – T4-09-04 |  | FM008 |  | 2022-10-19 00:27 | 2022-10-19 01:27 | 2022-10-20 01:27 | 24 | 2022-10-19 00:35 | 2022-10-19 02:05 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11297183 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-418 – T4-09-04 |  | FM008 |  | 2022-12-20 07:17 | 2022-12-20 08:17 | 2022-12-21 08:17 | 24 | 2022-12-20 07:25 | 2022-12-20 09:30 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11674549 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT ILLUMINATING - AHU-A1110-418 – T4-09-04 |  | FM008 |  | 2023-04-17 13:40 | 2023-04-17 14:40 | 2023-04-18 14:40 | 24 | 2023-04-17 13:49 | 2023-04-17 15:18 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-9966948 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1110-418 ( ASD-MTB-FOF009-AHU031-FIL784 ) |  | FM008 |  | 2022-01-02 16:50 | 2022-01-02 17:50 | 2022-01-03 17:50 | 24 | 2022-01-02 16:59 | 2022-01-02 20:00 | 181 | 130 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 55709 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | BMS
| CM-2022-10131534 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | SUPPLY SIDE V-BELT IS DAMAGED – AHU-A1110-418 - T4-09-04 |  | FM008 |  | 2022-02-11 07:10 | 2022-02-11 08:10 | 2022-02-12 08:10 | 24 | 2022-02-11 07:15 | 2022-02-11 09:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-11471960 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AC IS TOO HOT - TEDDY BEAR AREA |  | FM008 |  | 2023-02-19 23:34 | 2023-02-20 00:34 | 2023-02-21 00:34 | 24 | 2023-02-19 23:40 | 2023-02-20 00:15 | 35 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 87807 | 17053 |  |  | 89126 | Red, Ms. Chelsea Lontok | N - - - |  | Voice Communication
| CM-2023-12295884 | ASD-MTB-FOF009-AHU031 | AIR HANDLING UNIT-05 | AHU-A1110-418 BEARING NOISY T4-09-04 |  | FM008 |  | 2023-10-17 11:07 | 2023-10-17 12:07 | 2023-10-18 12:07 | 24 | 2023-10-17 11:15 | 2023-10-17 15:15 | 240 | 960 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68485 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2022-10696045 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-28 19:04 | 2022-05-28 20:04 | 2022-05-29 20:04 | 24 | 2022-05-28 19:14 | 2022-05-28 20:45 | 91 | 273 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-11103087 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT AND RELIEF FAN BELT DAMAGED |  | FM008 |  | 2022-10-15 18:58 | 2022-10-15 19:58 | 2022-10-16 19:58 | 24 | 2022-10-15 19:05 | 2022-10-15 21:40 | 155 | 465 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11684320 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 AHU CABIN LIGHT NOT WORKING T4-09-04 |  | FM008 |  | 2023-04-19 03:11 | 2023-04-19 04:11 | 2023-04-20 04:11 | 24 | 2023-04-19 03:15 | 2023-04-19 05:30 | 135 | 270 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11916979 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -T4-09-04 |  | FM008 |  | 2023-06-24 21:44 | 2023-06-24 22:44 | 2023-06-25 22:44 | 24 | 2023-06-24 21:49 | 2023-06-24 23:42 | 113 | 206 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11930936 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED - AHU-A1110-422 – T4 09 04 |  | FM008 |  | 2023-06-26 19:06 | 2023-06-26 20:06 | 2023-06-27 20:06 | 24 | 2023-06-26 19:10 | 2023-06-26 23:50 | 280 | 278 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11834168 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T4-07-31 |  | FM008 |  | 2023-05-28 21:55 | 2023-05-28 22:55 | 2023-05-29 22:55 | 24 | 2023-05-28 22:00 | 2023-05-28 23:59 | 119 | 272 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12090086 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS LEAKAGE - AHU-A1110-422 – T4-09-04 |  | FM008 |  | 2023-08-16 11:05 | 2023-08-16 12:05 | 2023-08-17 12:05 | 24 | 2023-08-16 11:10 | 2023-08-16 18:35 | 445 | 530 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 106973 | 17053 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12096858 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DP3-FILTER DIRTY-AHU-A1110-422(t4-09-04) |  | FM008 |  | 2023-08-17 23:06 | 2023-08-18 00:06 | 2023-08-19 00:06 | 24 | 2023-08-17 23:10 | 2023-08-18 00:15 | 65 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM7396 | Chowdhury, Mr. Biswajit | N - - - |  | Voice Communication
| CM-2023-12298880 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | (Ahu-a1110-422 )SUPPLY SIDE MOTOR BARRING NOISY - (T4-09-04) |  | FM008 |  | 2023-10-18 11:10 | 2023-10-18 12:10 | 2023-10-19 12:10 | 24 | 2023-10-18 11:15 | 2023-10-18 14:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 77406 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-10930519 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- T4-09-04 |  | FM008 |  | 2022-08-10 19:20 | 2022-08-10 20:20 | 2022-08-11 20:20 | 24 | 2022-08-10 19:25 | 2022-08-10 22:10 | 165 | 495 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11101861 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-10-16 00:11 | 2022-10-16 01:11 | 2022-10-17 01:11 | 24 | 2022-10-16 00:20 | 2022-10-16 02:55 | 155 | 465 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11115022 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 -FILTER ALARMS -T4-09-04 |  | FM008 |  | 2022-10-22 02:59 | 2022-10-22 03:59 | 2022-10-23 03:59 | 24 | 2022-10-22 03:05 | 2022-10-22 06:00 | 175 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 87807 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11668317 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | SUPPLY BLOWER NOISY |  | FM008 |  | 2023-04-16 12:24 | 2023-04-16 13:24 | 2023-04-17 13:24 | 24 | 2023-04-16 12:30 | 2023-04-16 15:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 95216 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-11674640 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 FILTER DIRTY T4-09-04 |  | FM008 |  | 2023-04-18 00:04 | 2023-04-18 01:04 | 2023-04-19 01:04 | 24 | 2023-04-18 00:10 | 2023-04-18 04:15 | 245 | 368 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11763154 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED |  | FM008 |  | 2023-05-03 00:07 | 2023-05-03 01:07 | 2023-05-04 01:07 | 24 | 2023-05-03 00:13 | 2023-05-03 01:40 | 87 | 174 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 95216 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11999825 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | SF FAIL ALARM - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2023-07-22 11:28 | 2023-07-22 12:28 | 2023-07-23 12:28 | 24 | 2023-07-22 11:38 | 2023-07-22 12:30 | 52 | 104 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 121959 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12093129 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 DUCT INSULATION DAMAGED T4-09-04 |  | FM008 |  | 2023-08-15 19:12 | 2023-08-15 20:12 | 2023-08-16 20:12 | 24 | 2023-08-15 19:15 | 2023-08-15 22:00 | 165 | 495 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12322882 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-422 – T4-09-04 |  | FM008 |  | 2023-10-25 16:46 | 2023-10-25 17:46 | 2023-10-26 17:46 | 24 | 2023-10-25 16:55 | 2023-10-25 18:40 | 105 | 140 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2023-12429499 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – T4-09-04 |  | FM008 |  | 2023-12-01 01:03 | 2023-12-01 02:03 | 2023-12-02 02:03 | 24 | 2023-12-01 01:10 | 2023-12-01 03:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-10116869 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 FILTER DIRTY |  | FM008 |  | 2022-02-08 07:11 | 2022-02-08 08:11 | 2022-02-09 08:11 | 24 | 2022-02-08 07:15 | 2022-02-08 09:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10158793 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 – DUCT INSULATION DAMAGED – T4-09-04 |  | FM008 |  | 2022-02-20 21:16 | 2022-02-20 22:16 | 2022-02-21 22:16 | 24 | 2022-02-20 21:25 | 2022-02-20 22:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10654822 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -T4-09-04 |  | FM008 |  | 2022-05-13 00:08 | 2022-05-13 01:08 | 2022-05-14 01:08 | 24 | 2022-05-13 00:15 | 2022-05-13 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11080754 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | AHU-A1110-422 CHILLED WATER LINE INSULATION DAMAGED |  | FM008 |  | 2022-10-09 01:48 | 2022-10-09 02:48 | 2022-10-10 02:48 | 24 | 2022-10-09 01:55 | 2022-10-09 03:25 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10593760 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-422 T4-09-04 |  | FM008 |  | 2022-04-27 12:49 | 2022-04-27 13:49 | 2022-04-28 13:49 | 24 | 2022-04-27 12:55 | 2022-04-27 14:00 | 65 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10801855 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-:AHU-A1110-422)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 009 |  | FM008 |  | 2022-07-04 06:59 | 2022-07-04 07:59 | 2022-07-05 07:59 | 24 | 2022-07-04 07:05 | 2022-07-04 08:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11620692 | ASD-MTB-FOF009-AHU035 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2023-04-03 13:55 | 2023-04-03 14:55 | 2023-04-04 14:55 | 24 | 2023-04-03 14:00 | 2023-04-03 17:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-10652544 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | AHU-A1110-448- SUPPLY CHAIN BELT LOOSE – T4-09-04 |  | FM008 |  | 2022-05-11 22:20 | 2022-05-11 23:20 | 2022-05-12 23:20 | 24 | 2022-05-11 22:25 | 2022-05-11 23:50 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 17154 | 17053 |  |  | fm3093 | fm3093 | N - - - |  | Voice Communication
| CM-2022-10902789 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | FILTER DIRTY T4-09-04 |  | FM008 |  | 2022-08-02 07:15 | 2022-08-02 08:15 | 2022-08-03 08:15 | 24 | 2022-08-02 07:20 | 2022-08-02 08:30 | 70 | 210 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 76858 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-12062920 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM, AHU-A1110-448,T4-09-04 |  | FM008 |  | 2023-08-09 14:01 | 2023-08-09 15:01 | 2023-08-10 15:01 | 24 | 2023-08-09 14:10 | 2023-08-09 15:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 124475 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12798668 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – (AHU-A1110-448) |  | FM008 |  | 2024-04-07 09:33 | 2024-04-07 10:33 | 2024-04-08 10:33 | 24 | 2024-04-07 09:40 | 2024-04-07 11:40 | 120 | 260 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM12908 | Kumar, Mr. Abhishek | N - - - |  | Voice Communication
| CM-2023-11463434 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | SUPPLY BLOWER AND MOTOR NOISY |  | FM008 |  | 2023-02-14 00:12 | 2023-02-14 01:12 | 2023-02-15 01:12 | 24 | 2023-02-14 00:20 | 2023-02-14 03:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 95217 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2023-12092847 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED-T4-09-04 |  | FM008 |  | 2023-08-14 14:58 | 2023-08-14 15:58 | 2023-08-15 15:58 | 24 | 2023-08-14 15:07 | 2023-08-14 17:40 | 153 | 306 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2022-11216054 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | CHILLED WATER LINE HANGING SUPPORT LOOSE-T4-09-04 |  | FM008 |  | 2022-11-27 01:33 | 2022-11-27 02:33 | 2022-11-28 02:33 | 24 | 2022-11-27 01:40 | 2022-11-27 04:30 | 170 | 510 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11711624 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS(PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP2.MTB448.AHU448.SYSALM.DP1 /-T4-09-04 |  | FM008 |  | 2023-04-27 18:50 | 2023-04-27 19:50 | 2023-04-28 19:50 | 24 | 2023-04-27 19:00 | 2023-04-27 23:05 | 245 | 70 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12429895 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1110-448,T4-09-04 |  | FM008 |  | 2023-12-02 19:45 | 2023-12-02 20:45 | 2023-12-03 20:45 | 24 | 2023-12-02 19:50 | 2023-12-02 22:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 87807 |  |  | FM12549 | Veera Sundaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10045476 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | AHU-A1110-448 - RAD OPEN FAIL ALARM T4-09-04 |  | FM008 |  | 2022-01-14 09:34 | 2022-01-14 10:34 | 2022-01-15 10:34 | 24 | 2022-01-14 09:40 | 2022-01-14 10:50 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17053 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10158862 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-448 T4-09-04 |  | FM008 |  | 2022-02-22 07:17 | 2022-02-22 08:17 | 2022-02-23 08:17 | 24 | 2022-02-22 07:20 | 2022-02-22 08:45 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2022-10710385 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | AHU-A1110-448 DRAIN LINE BLOCKED |  | FM008 |  | 2022-06-02 05:12 | 2022-06-02 06:12 | 2022-06-03 06:12 | 24 | 2022-06-02 05:20 | 2022-06-02 06:20 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68485 | 17053 |  |  | FM9671 | Karunagoda Mudalige, Mr. Kasun Lakmal | N - - - |  | Voice Communication
| CM-2022-10661486 | ASD-MTB-FOF009-AHU061 | AIR HANDLING UNIT-05 | AHU-A1110-448 -DP3 FILTER ALARM - T4-09-04 |  | FM008 |  | 2022-05-14 22:14 | 2022-05-14 23:14 | 2022-05-15 23:14 | 24 | 2022-05-14 22:23 | 2022-05-15 01:30 | 187 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10103531 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-02 00:07 | 2022-02-02 01:07 | 2022-02-03 01:07 | 24 | 2022-02-02 00:16 | 2022-02-02 03:25 | 189 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10124964 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | AIR FILTER IS DIRTY - :AHU-A1110-438 - T4-09-04 |  | FM008 |  | 2022-02-12 13:52 | 2022-02-12 14:52 | 2022-02-13 14:52 | 24 | 2022-02-12 14:00 | 2022-02-12 16:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | E-mail
| CM-2022-11232317 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-11-29 12:28 | 2022-11-29 13:28 | 2022-11-30 13:28 | 24 | 2022-11-29 12:35 | 2022-11-29 16:35 | 240 | 480 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95216 | 17053 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2024-12735963 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | AHU-A1110-438 T4-09-04 SUPPLY SIDE BELT DAMAGED |  | FM008 |  | 2024-03-17 10:09 | 2024-03-17 11:09 | 2024-03-18 11:09 | 24 | 2024-03-17 10:15 | 2024-03-17 15:15 | 300 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 138627 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12014149 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING |  | FM008 |  | 2023-07-25 19:17 | 2023-07-25 20:17 | 2023-07-26 20:17 | 24 | 2023-07-25 19:25 | 2023-07-26 00:30 | 305 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11060312 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-09-26 07:15 | 2022-09-26 08:15 | 2022-09-27 08:15 | 24 | 2022-09-26 07:20 | 2022-09-26 09:30 | 130 | 260 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11157760 | ASD-MTB-FOF024-AHU051 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM CANVAS RELEAF SIDE - AHU-A1110-438 – T4-09-04 |  | FM008 |  | 2022-11-02 21:14 | 2022-11-02 22:14 | 2022-11-03 22:14 | 24 | 2022-11-02 21:20 | 2022-11-02 22:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10699647 | ASD-MTB-FOF024-AHU053 | AIR HANDLING UNIT-05 | SUPPLY DUCT EXHAUST DOOR AIR LEAKAGE - T4-09-04 MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-05-29 07:17 | 2022-05-29 08:17 | 2022-05-30 08:17 | 24 | 2022-05-29 07:20 | 2022-05-29 08:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11267037 | ASD-MTB-FOF024-AHU053 | AIR HANDLING UNIT-05 | AHU-A1110-440 CHILLED WATER LINE INSULATION DAMAGED |  | FM008 |  | 2022-12-12 00:06 | 2022-12-12 01:06 | 2022-12-13 01:06 | 24 | 2022-12-12 00:10 | 2022-12-12 03:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12007172 | ASD-MTB-FOF024-AHU053 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM, AHU-A1110-440, T4-09-04 |  | FM008 |  | 2023-07-24 07:12 | 2023-07-24 08:12 | 2023-07-25 08:12 | 24 | 2023-07-24 07:20 | 2023-07-24 12:15 | 295 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12494696 | ASD-MTB-FOF024-AHU053 | AIR HANDLING UNIT-05 | RETURN BLOWER SIDE ABNORMAL SOUND |  | FM008 |  | 2023-12-24 09:20 | 2023-12-24 10:20 | 2023-12-25 10:20 | 24 | 2023-12-24 09:30 | 2023-12-24 13:05 | 215 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68060 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11060321 | ASD-MTB-FOF024-AHU053 | AIR HANDLING UNIT-05 | FILTER ALARM- T4-09-04 |  | FM008 |  | 2022-09-26 07:50 | 2022-09-26 08:50 | 2022-09-27 08:50 | 24 | 2022-09-26 08:00 | 2022-09-26 10:45 | 165 | 166 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12364496 | ASD-MTB-FOF024-AHU053 | AIR HANDLING UNIT-05 | DEPARTURE FIRST CLASS ROW 1 COUNTER 1 AC TOO COLD |  | FM008 |  | 2023-11-10 17:13 | 2023-11-10 18:13 | 2023-11-11 18:13 | 24 | 2023-11-10 17:20 | 2023-11-10 18:15 | 55 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2022-10141714 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 – CH1 PREMIUM OFFICE AC VENT DIRTY |  | FM008 |  | 2022-02-17 19:00 | 2022-02-17 20:00 | 2022-02-18 20:00 | 24 | 2022-02-17 19:10 | 2022-02-17 22:10 | 180 | 175 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10593691 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -T4-09-04 |  | FM008 |  | 2022-04-26 19:05 | 2022-04-26 20:05 | 2022-04-27 20:05 | 24 | 2022-04-26 19:10 | 2022-04-26 21:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10750240 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-422 – T4-09-04 |  | FM008 |  | 2022-06-19 07:11 | 2022-06-19 08:11 | 2022-06-20 08:11 | 24 | 2022-06-19 07:20 | 2022-06-19 10:15 | 175 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10858160 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO HOT IN ALMURJAN COUNTER ROW NUMBER 2 |  | FM008 |  | 2022-07-17 21:51 | 2022-07-17 22:51 | 2022-07-18 22:51 | 24 | 2022-07-17 21:55 | 2022-07-17 23:15 | 80 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 95217 |  |  | 84448 | Marata, Ms. Michelle De Los Angeles | N - - - |  | Voice Communication
| CM-2022-10954326 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442- CH1 PERMIUM OFFICE AC VENT DIRTY |  | FM008 |  | 2022-08-18 22:52 | 2022-08-18 23:52 | 2022-08-19 23:52 | 24 | 2022-08-18 23:00 | 2022-08-19 00:30 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 87807 | 55709 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2022-11112527 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT IS DIRTY - AHU-A1110-442 - CH1 PREMIUM OFFICE |  | FM008 |  | 2022-10-19 00:31 | 2022-10-19 01:31 | 2022-10-20 01:31 | 24 | 2022-10-19 00:35 | 2022-10-19 02:05 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11159432 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -AHU-A1110-442 - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-11-03 07:11 | 2022-11-03 08:11 | 2022-11-04 08:11 | 24 | 2022-11-03 07:15 | 2022-11-03 09:00 | 105 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11193370 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | FIRST CLASS COUNTER NUMBER 1 AC TOO COLD |  | FM008 |  | 2022-11-16 02:28 | 2022-11-16 03:28 | 2022-11-17 03:28 | 24 | 2022-11-16 02:35 | 2022-11-16 04:15 | 100 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 65032 | Mwashe, Mr. Paul Musonga | N - - - |  | Voice Communication
| CM-2022-11210684 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN ROW 1-COUNTER 1 |  | FM008 |  | 2022-11-21 05:05 | 2022-11-21 06:05 | 2022-11-22 06:05 | 24 | 2022-11-21 05:10 | 2022-11-21 06:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 105584 | K C, Ms. Sharda | N - - - |  | Voice Communication
| CM-2022-11322043 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | BUSINESS CLASS ROW NO 1 AC TOO COLD |  | FM008 |  | 2022-12-28 17:39 | 2022-12-28 18:39 | 2022-12-29 18:39 | 24 | 2022-12-28 17:45 | 2022-12-28 18:15 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 86790 | Werasinghe Arachchige, Mr. Gayan Harshana Wijerathne | N - - - |  | Voice Communication
| CM-2022-11328848 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD -ROW 2 SALES OFFICE |  | FM008 |  | 2022-12-31 03:23 | 2022-12-31 04:23 | 2023-01-01 04:23 | 24 | 2022-12-31 03:30 | 2022-12-31 05:00 | 90 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 97921 | Ansari, Ms. Sana Naaz Mohammed Mehmood | N - - - |  | Voice Communication
| CM-2023-11511582 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN ROW 1 |  | FM008 |  | 2023-03-04 05:08 | 2023-03-04 06:08 | 2023-03-05 06:08 | 24 | 2023-03-04 05:15 | 2023-03-04 06:20 | 65 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17154 | 87807 |  |  | 111247 | Taifi, Ms. Alae | N - - - |  | Voice Communication
| CM-2023-11512804 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD, CHECK IN ROW-1 COUNTER #1 |  | FM008 |  | 2023-03-05 03:10 | 2023-03-05 04:10 | 2023-03-06 04:10 | 24 | 2023-03-05 03:15 | 2023-03-05 06:54 | 219 | 118 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 87807 |  |  | 120421 | Thandayamparambil Jyothi Basu, Mrs. Jyothilakshmi | N - - - |  | Voice Communication
| CM-2023-11568704 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | CHECK IN ROW 3 COUNTER 1 - AC TOO COLD |  | FM008 |  | 2023-03-17 16:09 | 2023-03-17 17:09 | 2023-03-18 17:09 | 24 | 2023-03-17 16:15 | 2023-03-17 16:45 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 95217 |  |  | R10014 | Castro, Ms. Sandra Manaois | N - - - |  | Voice Communication
| CM-2023-11564891 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DEPARTURE FIRST CLASS CHECK IN COUNTER 1 AND 2 AREA TOO COLD |  | FM008 |  | 2023-03-15 23:30 | 2023-03-16 00:30 | 2023-03-17 00:30 | 24 | 2023-03-15 23:35 | 2023-03-16 01:00 | 85 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 68350 | Elghazouani, Ms. Fatima Ezzahraa | N - - - |  | Voice Communication
| CM-2023-11691424 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT DIRTY -ROW 2 SALES OFFICE |  | FM008 |  | 2023-04-22 00:23 | 2023-04-22 01:23 | 2023-04-23 01:23 | 24 | 2023-04-22 00:30 | 2023-04-22 02:45 | 135 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11784417 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | BUSINESS CLASS DEPARTURE SCREENING AREA AC TOO COLD |  | FM008 |  | 2023-05-11 22:34 | 2023-05-11 23:34 | 2023-05-12 23:34 | 24 | 2023-05-11 22:40 | 2023-05-11 23:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | CT16734 | JOSEPH | N - - - |  | Voice Communication
| CM-2023-11969278 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | BEHIND CHECK IN IN ROW 2 PREMIUM SALES NEXT TO BUSINESS CLASS COUNTERS/AC TOO COLD |  | FM008 |  | 2023-07-11 06:31 | 2023-07-11 07:31 | 2023-07-12 07:31 | 24 | 2023-07-11 06:35 | 2023-07-11 09:40 | 185 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 87807 |  |  | 117583 | Bargach, Ms. Sabah | N - - - |  | Voice Communication
| CM-2023-12000897 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AS VENT DIRTY - PREMIUM SALE OFFICE CH-1 |  | FM008 |  | 2023-07-22 21:09 | 2023-07-22 22:09 | 2023-07-23 22:09 | 24 | 2023-07-22 21:15 | 2023-07-22 23:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12007801 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH DAMAGED |  | FM008 |  | 2023-07-26 19:00 | 2023-07-26 20:00 | 2023-07-27 20:00 | 24 | 2023-07-26 19:10 | 2023-07-26 23:49 | 279 | 363 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68060 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12079543 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | FIRST CLASS DEPARTURE CHECK IN ROW 1 AC TOO HOT |  | FM008 |  | 2023-08-13 17:35 | 2023-08-13 18:35 | 2023-08-14 18:35 | 24 | 2023-08-13 17:41 | 2023-08-13 19:50 | 129 | 64 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | 68350 | Elghazouani, Ms. Fatima Ezzahraa | N - - - |  | Voice Communication
| CM-2023-12087402 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-08-14 09:32 | 2023-08-14 10:32 | 2023-08-15 10:32 | 24 | 2023-08-14 09:40 | 2023-08-14 18:15 | 515 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-12119730 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD– DEPARTURES ROW 1 COUNTER 1 TO 4 |  | FM008 |  | 2023-08-27 14:36 | 2023-08-27 15:36 | 2023-08-28 15:36 | 24 | 2023-08-27 14:45 | 2023-08-28 00:15 | 570 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-12179259 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN AREA ROW 1 AREA |  | FM008 |  | 2023-09-11 04:08 | 2023-09-11 05:08 | 2023-09-12 05:08 | 24 | 2023-09-11 04:15 | 2023-09-11 05:40 | 85 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-12245110 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – T4-09-04 |  | FM008 |  | 2023-10-02 06:55 | 2023-10-02 07:55 | 2023-10-03 07:55 | 24 | 2023-10-02 07:00 | 2023-10-02 09:50 | 170 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-12302779 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | PREMIUN SALES AREA BEHIND ROW 03,CHECK IN – AC TOO COLD |  | FM008 |  | 2023-10-20 23:34 | 2023-10-21 00:04 | 2023-10-21 04:04 | 4 | 2023-10-20 23:40 | 2023-10-21 02:06 | 146 | 65 | 2 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 024 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 105233 | 87807 |  |  | 117583 | Bargach, Ms. Sabah | N - - - |  | Voice Communication
| CM-2023-12326121 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES CHECK-IN ROW 1 COUNTER AREA |  | FM008 |  | 2023-10-29 04:33 | 2023-10-29 05:33 | 2023-10-30 05:33 | 24 | 2023-10-29 04:41 | 2023-10-29 05:55 | 74 | 34 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 117086 | Chikhaoui, Ms. Roueda | N - - - |  | Voice Communication
| CM-2023-12363230 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW 1 COUNTER AREA |  | FM008 |  | 2023-11-06 18:35 | 2023-11-06 19:35 | 2023-11-07 19:35 | 24 | 2023-11-06 18:40 | 2023-11-06 22:10 | 210 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 108163 | Addali, Ms. Molka | N - - - |  | Voice Communication
| CM-2023-12377895 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD – DEPARTURE CHECK IN ROW 1 AREA |  | FM008 |  | 2023-11-14 01:32 | 2023-11-14 02:32 | 2023-11-15 02:32 | 24 | 2023-11-14 01:35 | 2023-11-14 05:55 | 260 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 133396 | 87807 |  |  | 121171 | Khine, Ms. May Thet | N - - - |  | Voice Communication
| CM-2023-12429917 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW ONE FIRST CLASS |  | FM008 |  | 2023-12-02 22:22 | 2023-12-02 23:22 | 2023-12-03 23:22 | 24 | 2023-12-02 22:30 | 2023-12-02 23:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | 119781 | Ayadi, Ms. Chaima | N - - - |  | Voice Communication
| CM-2023-12451906 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES - FIRST CLASS CHECKING COUNTER 1 |  | FM008 |  | 2023-12-09 15:58 | 2023-12-09 16:58 | 2023-12-10 16:58 | 24 | 2023-12-09 16:05 | 2023-12-09 23:50 | 465 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 111247 | Taifi, Ms. Alae | N - - - |  | Voice Communication
| CM-2023-12489979 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD – DEPARTURES ROW 1 COUNTER 1 |  | FM008 |  | 2023-12-20 22:21 | 2023-12-20 23:21 | 2023-12-21 23:21 | 24 | 2023-12-20 22:25 | 2023-12-21 00:35 | 130 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | BLOWER FAN FAULTY | REPLACED THE FAN | 132112 | 87807 |  |  | 117086 | Chikhaoui, Ms. Roueda | N - - - |  | Voice Communication
| CM-2024-12632899 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1110-442 - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2024-02-10 00:06 | 2024-02-10 01:06 | 2024-02-11 01:06 | 24 | 2024-02-10 00:10 | 2024-02-10 01:32 | 82 | 246 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2024-12741249 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 CH1 PREMIUM OFFICE AC VENT DIRTY |  | FM008 |  | 2024-03-20 01:04 | 2024-03-20 02:04 | 2024-03-21 02:04 | 24 | 2024-03-20 01:10 | 2024-03-20 03:55 | 165 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12846873 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #2 COUNTER #13 & 14 AREA |  | FM008 |  | 2024-04-22 05:20 | 2024-04-22 06:20 | 2024-04-23 06:20 | 24 | 2024-04-22 05:25 | 2024-04-22 06:20 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 142195 | Ishraq, Mr. Mohsin | N - - - |  | Voice Communication
| CM-2024-12846129 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD, ROW-1 ALL COUNTER AREA |  | FM008 |  | 2024-04-23 20:41 | 2024-04-23 21:41 | 2024-04-24 21:41 | 24 | 2024-04-23 20:50 | 2024-04-24 01:00 | 250 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2024-12850085 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD PREMIUM TICKETING OFFICE BETWEEN CHECK IN ROW 1 - 3 |  | FM008 |  | 2024-04-25 08:14 | 2024-04-25 09:14 | 2024-04-26 09:14 | 24 | 2024-04-25 08:20 | 2024-04-25 16:00 | 460 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 110306 | Aicha, Ms. Said | N - - - |  | Voice Communication
| CM-2022-11023793 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO HOT -QR PREMIUM SALES COUNTER NEAR ROW 2 |  | FM008 |  | 2022-09-13 13:31 | 2022-09-13 14:31 | 2022-09-14 14:31 | 24 | 2022-09-13 13:40 | 2022-09-13 15:40 | 120 | 37 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 17053 |  |  | 110306 | Aicha, Ms. Said | N - - - |  | Voice Communication
| CM-2022-11029660 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 – AC VENT IS DIRTY – T4-09-04 |  | FM008 |  | 2022-09-17 01:31 | 2022-09-17 02:31 | 2022-09-18 02:31 | 24 | 2022-09-17 01:41 | 2022-09-17 05:35 | 234 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11028188 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 DP1 FILTER ALARM |  | FM008 |  | 2022-09-17 13:57 | 2022-09-17 14:57 | 2022-09-18 14:57 | 24 | 2022-09-17 14:05 | 2022-09-17 15:45 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11206982 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TEMPERATURE TOO COLD - ALFSAFWA CHECK IN ROW 1 COUNTER 1 |  | FM008 |  | 2022-11-23 05:12 | 2022-11-23 06:12 | 2022-11-24 06:12 | 24 | 2022-11-23 05:20 | 2022-11-23 06:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 105584 | K C, Ms. Sharda | N - - - |  | Voice Communication
| CM-2023-11624341 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD- ALSAFWA CHECKING COUNTERS |  | FM008 |  | 2023-04-09 04:42 | 2023-04-09 05:42 | 2023-04-10 05:42 | 24 | 2023-04-09 04:50 | 2023-04-09 05:30 | 40 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 78918 | Pathirage Don, Mr. Tiron Lanka Gunawardhana | N - - - |  | Voice Communication
| CM-2023-11800798 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES PREMIUM SALES BEHIND ROW 4 AND 5 |  | FM008 |  | 2023-05-16 15:02 | 2023-05-16 16:02 | 2023-05-17 16:02 | 24 | 2023-05-16 15:10 | 2023-05-16 16:00 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 17053 |  |  | 117583 | Bargach, Ms. Sabah | N - - - |  | Voice Communication
| CM-2023-11802460 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | NEAR ROW 2 - QR SALES PREMIUM OFFICE AC TOO COLD |  | FM008 |  | 2023-05-17 07:56 | 2023-05-17 08:56 | 2023-05-18 08:56 | 24 | 2023-05-17 08:00 | 2023-05-17 12:15 | 255 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 89127 | 17053 |  |  | 97921 | Ansari, Ms. Sana Naaz Mohammed Mehmood | N - - - |  | Voice Communication
| CM-2023-11824845 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECKING COUNTER 1 ROW #1 DEPARTURES |  | FM008 |  | 2023-05-27 04:05 | 2023-05-27 05:05 | 2023-05-28 05:05 | 24 | 2023-05-27 04:10 | 2023-05-27 09:10 | 300 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-11879113 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | A/C IS TOO COLD QR PREMIUM COUNTER BEHIND ROW 5 |  | FM008 |  | 2023-06-15 08:14 | 2023-06-15 09:14 | 2023-06-16 09:14 | 24 | 2023-06-15 08:20 | 2023-06-15 09:15 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 115734 | Riad, Ms. Hind | N - - - |  | Voice Communication
| CM-2023-12035578 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DEPARTURE BUSINESS CLASS AREA AC TOO COLD - |  | FM008 |  | 2023-08-02 11:21 | 2023-08-02 12:21 | 2023-08-03 12:21 | 24 | 2023-08-02 11:35 | 2023-08-02 15:35 | 240 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | CT14362 | Isaac | N - - - |  | Voice Communication
| CM-2023-12043050 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD IN DEPARTURE CHECK IN AREA - |  | FM008 |  | 2023-08-03 12:00 | 2023-08-03 13:00 | 2023-08-04 13:00 | 24 | 2023-08-03 12:05 | 2023-08-03 16:45 | 280 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | CT15033 | JAMES | N - - - |  | Voice Communication
| CM-2023-12056956 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | TEMPERATURE LOW IN CABINS -Business Class / First Class |  | FM008 |  | 2023-08-06 20:54 | 2023-08-06 21:54 | 2023-08-07 21:54 | 24 | 2023-08-06 21:00 | 2023-08-06 23:59 | 179 | 64 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 119877 | Appalsamy, Mr. Lee Beste | N - - - |  | E-mail
| CM-2023-12092869 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO HOT – CHECKING COUNTER ROW 1 AND 2 DEPARTURES |  | FM008 |  | 2023-08-14 18:35 | 2023-08-14 19:35 | 2023-08-15 19:35 | 24 | 2023-08-14 18:45 | 2023-08-14 19:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 17053 |  |  | 88372 | De Sierra, Ms. Angelica Cabal | N - - - |  | Voice Communication
| CM-2023-12097564 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO HOT CHECK IN ROW 2 BUSINESS CLASS DEPARTURE |  | FM008 |  | 2023-08-17 05:36 | 2023-08-17 06:36 | 2023-08-18 06:36 | 24 | 2023-08-17 05:40 | 2023-08-17 09:35 | 235 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 78918 | Pathirage Don, Mr. Tiron Lanka Gunawardhana | N - - - |  | Voice Communication
| CM-2023-12231007 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD-DEPARTURE CHECK-IN ROW #2 AREA(CM-2023-05-1588) |  | FM008 |  | 2023-09-26 22:11 | 2023-09-26 23:11 | 2023-09-27 23:11 | 24 | 2023-09-26 22:16 | 2023-09-26 23:16 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94954 | 87807 |  |  | 68350 | FATIMA | - - - |  | Voice Communication
| CM-2023-12363897 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - PREMIUM OFFICE NUMBER A1-2FCH1-04 LANDSIDE CHECK IN COUNTER SIDE |  | FM008 |  | 2023-11-08 02:28 | 2023-11-08 03:28 | 2023-11-09 03:28 | 24 | 2023-11-08 02:35 | 2023-11-08 05:10 | 155 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 31900 | Bachini, Ms. Katrina Granados | N - - - |  | Voice Communication
| CM-2023-12426649 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - FIRST CLASS DEPARTURE ROW 1 |  | FM008 |  | 2023-12-01 22:47 | 2023-12-01 23:47 | 2023-12-02 23:47 | 24 | 2023-12-01 22:55 | 2023-12-02 01:05 | 130 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | 115507 | Arbi, Ms. Istabrak | N - - - |  | Voice Communication
| CM-2023-12490006 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD CHECK IN ROW # 2 DEPARTURE HALL |  | FM008 |  | 2023-12-20 23:49 | 2023-12-21 00:49 | 2023-12-22 00:49 | 24 | 2023-12-20 23:55 | 2023-12-21 01:20 | 85 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | 108163 | Addali, Ms. Molka | N - - - |  | Voice Communication
| CM-2024-12616389 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD PREMIUM CHECK IN ROW # 01 |  | FM008 |  | 2024-02-04 03:18 | 2024-02-04 04:18 | 2024-02-05 04:18 | 24 | 2024-02-04 03:25 | 2024-02-04 05:30 | 125 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 68350 | Elghazouani, Ms. Fatima Ezzahraa | N - - - |  | Voice Communication
| CM-2024-12647798 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW 1 COUNTER 1 |  | FM008 |  | 2024-02-13 02:36 | 2024-02-13 03:36 | 2024-02-14 03:36 | 24 | 2024-02-13 02:40 | 2024-02-13 05:30 | 170 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 108163 | Addali, Ms. Molka | N - - - |  | Voice Communication
| CM-2024-12735908 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC IS TOO COLD -DEPARTURE ROW NO-1-CHECK IN COUNTERS - 1ST CLASS LOUNGE |  | FM008 |  | 2024-03-17 05:58 | 2024-03-17 06:58 | 2024-03-18 06:58 | 24 | 2024-03-17 06:05 | 2024-03-17 10:05 | 240 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2022-11060311 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-09-26 07:14 | 2022-09-26 08:14 | 2022-09-27 08:14 | 24 | 2022-09-26 07:20 | 2022-09-26 09:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11149339 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 LIGHT IS NOT ILLUINATING |  | FM008 |  | 2022-10-30 03:19 | 2022-10-30 04:19 | 2022-10-31 04:19 | 24 | 2022-10-30 03:25 | 2022-10-30 04:30 | 65 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 94953 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11235422 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 CHILLED WATER LINE INSULATION DAMAGED |  | FM008 |  | 2022-12-04 00:36 | 2022-12-04 01:36 | 2022-12-05 01:36 | 24 | 2022-12-04 00:45 | 2022-12-04 02:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11268109 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 1 COUNTERS 1,2 AND 3 |  | FM008 |  | 2022-12-12 01:15 | 2022-12-12 02:15 | 2022-12-13 02:15 | 24 | 2022-12-12 01:20 | 2022-12-12 03:20 | 120 | 5 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 86359 | Gopez, Ms. Jaychelle Carreon | N - - - |  | Voice Communication
| CM-2022-11270873 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC IS TOO COLD-PREMIUM COUNTERS ROW 2- 1 OFFICE BEHIND - |  | FM008 |  | 2022-12-14 15:08 | 2022-12-14 16:08 | 2022-12-15 16:08 | 24 | 2022-12-14 15:18 | 2022-12-14 17:40 | 142 | 57 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 39926 | Fernandes, Ms. Dilecta Dominic | N - - - |  | Voice Communication
| CM-2022-11276478 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 1 ALL COUNTERS |  | FM008 |  | 2022-12-17 16:03 | 2022-12-17 17:03 | 2022-12-18 17:03 | 24 | 2022-12-17 16:10 | 2022-12-17 17:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 104101 | Rossi, Ms. Nicol | N - - - |  | Voice Communication
| CM-2022-11291704 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 – AC VENT IS DIRTY – DEPARTURE BUSINESS CLASS CHECK-IN AREA, PREMIUM OFFICE |  | FM008 |  | 2022-12-20 20:04 | 2022-12-20 21:04 | 2022-12-21 21:04 | 24 | 2022-12-20 20:10 | 2022-12-20 22:40 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94954 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11298829 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD PREMIUM SALES OFFICE DEPARTURE ROW 2 |  | FM008 |  | 2022-12-25 08:36 | 2022-12-25 09:36 | 2022-12-26 09:36 | 24 | 2022-12-25 08:45 | 2022-12-25 12:35 | 230 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 97921 | Ansari, Ms. Sana Naaz Mohammed Mehmood | N - - - |  | Voice Communication
| CM-2022-11330632 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD IN -QR PREMIUM SALES OFFICE NEAR CHECK IN COUNTER DEPATURE SECOND FLOOR. |  | FM008 |  | 2022-12-31 11:16 | 2022-12-31 12:16 | 2023-01-01 12:16 | 24 | 2022-12-31 11:25 | 2022-12-31 12:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 117583 | Bargach, Ms. Sabah | N - - - |  | Voice Communication
| CM-2023-11342333 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD -CHECK IN ROW 1 |  | FM008 |  | 2023-01-03 08:10 | 2023-01-03 09:10 | 2023-01-04 09:10 | 24 | 2023-01-03 08:15 | 2023-01-03 09:45 | 90 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-11363173 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - IN PTC ROW #4 AND 5 PREMIUM SALES BUSINESS CLASS CHECKING COUNTER |  | FM008 |  | 2023-01-11 03:37 | 2023-01-11 04:37 | 2023-01-12 04:37 | 24 | 2023-01-11 03:45 | 2023-01-11 06:35 | 170 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 117583 | Bargach, Ms. Sabah | N - - - |  | Voice Communication
| CM-2023-11478515 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT DIRTY - CH1 PREMIUM OFFICE |  | FM008 |  | 2023-02-21 00:03 | 2023-02-21 01:03 | 2023-02-22 01:03 | 24 | 2023-02-21 00:05 | 2023-02-21 01:45 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-11572819 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT DIRTY – PREMIUM OFFICE CH1- AHU-A1110-442 |  | FM008 |  | 2023-03-19 02:38 | 2023-03-19 03:38 | 2023-03-20 03:38 | 24 | 2023-03-19 02:45 | 2023-03-19 05:00 | 135 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11826759 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 FILTER DIRTY T4-24-01 |  | FM008 |  | 2023-05-27 00:37 | 2023-05-27 01:37 | 2023-05-28 01:37 | 24 | 2023-05-27 00:45 | 2023-05-27 05:10 | 265 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-11917187 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FILTER STATUS-ASD-MTB-FOF024-AHU055(AHU-A1110-442) / -MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-06-23 10:40 | 2023-06-23 11:40 | 2023-06-24 11:40 | 24 | 2023-06-23 10:45 | 2023-06-23 15:20 | 275 | 205 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11936388 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) – DEPARTURE ROW 2 PREMIUM CHECK IN COUNTER |  | FM008 |  | 2023-07-01 09:34 | 2023-07-01 10:34 | 2023-07-02 10:34 | 24 | 2023-07-01 09:40 | 2023-07-01 11:35 | 115 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 86627 | Maciel Scholze, Mr. Richardson Claudemir | N - - - |  | Voice Communication
| CM-2023-12097758 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO WARM - CHECK IN ROW # 2 AREA |  | FM008 |  | 2023-08-18 07:44 | 2023-08-18 08:44 | 2023-08-19 08:44 | 24 | 2023-08-18 07:50 | 2023-08-18 16:50 | 540 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 69005 | Kahandawita Gamage Don, Mr. Shion Delshan | N - - - |  | Voice Communication
| CM-2024-12849645 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | CH1 SALES OFFICE A/C VENTS DIRTY |  | FM008 |  | 2024-04-23 18:57 | 2024-04-23 19:57 | 2024-04-24 19:57 | 24 | 2024-04-23 19:03 | 2024-04-23 21:35 | 152 | 367 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68060 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12409043 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | A/C VENTS IS DIRTY PREMIUM SALE OFFICE |  | FM008 |  | 2023-11-25 01:21 | 2023-11-25 02:21 | 2023-11-26 02:21 | 24 | 2023-11-25 01:25 | 2023-11-25 03:10 | 105 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | FAN BLOWER IS DIRTY | CLEANED THE BLOWER | 68060 | 17053 |  |  | FM11321 | Ondari, Ms. Delvin Moraa | N - - - |  | Voice Communication
| CM-2024-12606585 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC NOT WORKING AREA HOT DEPARTURE LANDSIDE, PREMIUM SALES BACK OFFICE NEXT TO CHECK IN ROW 2 |  | FM008 |  | 2024-01-29 07:22 | 2024-01-29 08:22 | 2024-01-30 08:22 | 24 | 2024-01-29 07:30 | 2024-01-29 09:35 | 125 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 52517 | Estero, Ms. Elaine Marie Cornelia | N - - - |  | Voice Communication
| CM-2024-12649739 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | CHECK IN HALL ROW 1 AC TOO COLD |  | FM008 |  | 2024-02-13 06:28 | 2024-02-13 07:28 | 2024-02-14 07:28 | 24 | 2024-02-13 06:35 | 2024-02-13 12:45 | 370 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2024-12650412 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO HOT - THE WHOLE OF CHECK IN ROW 2 |  | FM008 |  | 2024-02-15 21:34 | 2024-02-15 22:34 | 2024-02-16 22:34 | 24 | 2024-02-15 21:40 | 2024-02-15 23:59 | 139 | 62 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 121959 | 95217 |  |  | 86362 | Wilson, Mr. Abin | N - - - |  | Voice Communication
| CM-2024-12739765 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC IS TOO COLD - DEPARTURE ROW.NO.1 -COUNTER 1 |  | FM008 |  | 2024-03-17 21:55 | 2024-03-17 22:55 | 2024-03-18 22:55 | 24 | 2024-03-17 22:00 | 2024-03-18 00:30 | 150 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 108163 | Addali, Ms. Molka | N - - - |  | Voice Communication
| CM-2024-12810638 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC NOT WORKING -ROW 2 DEPARTURE |  | FM008 |  | 2024-04-10 00:50 | 2024-04-10 01:50 | 2024-04-11 01:50 | 24 | 2024-04-10 00:55 | 2024-04-10 03:04 | 129 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17333 | 17053 |  |  | 69005 | Kahandawita Gamage Don, Mr. Shion Delshan | N - - - |  | Voice Communication
| CM-2024-12822268 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE CHECK-IN ROW #2 AREA |  | FM008 |  | 2024-04-11 16:50 | 2024-04-11 17:50 | 2024-04-12 17:50 | 24 | 2024-04-11 16:55 | 2024-04-11 17:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 85564 | Mudiyanselage, Ms. Demindhi Tharuki Wethalawa Wethalawe Rajapaksha | N - - - |  | Voice Communication
| CM-2024-12826349 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DEPARTURE ROW 1 AND 2 A/C IS TOO HOT |  | FM008 |  | 2024-04-15 23:17 | 2024-04-16 00:17 | 2024-04-17 00:17 | 24 | 2024-04-15 23:23 | 2024-04-16 01:02 | 99 | 67 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | 121172 | Hajji, Mr. Haythem | N - - - |  | Voice Communication
| CM-2023-12322942 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD – CHI ROW – 1-3 |  | FM008 |  | 2023-10-26 06:13 | 2023-10-26 07:13 | 2023-10-27 07:13 | 24 | 2023-10-26 06:20 | 2023-10-26 07:30 | 70 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-12385673 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD ,ROW-1, COUNTER-1,2,& 3 |  | FM008 |  | 2023-11-17 00:48 | 2023-11-17 01:48 | 2023-11-18 01:48 | 24 | 2023-11-17 00:55 | 2023-11-17 03:15 | 140 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | 117086 | Chikhaoui, Ms. Roueda | N - - - |  | Voice Communication
| CM-2023-12387268 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | BEARING NOISE - :AHU-A1110-442 - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-11-19 08:24 | 2023-11-19 09:24 | 2023-11-20 09:24 | 24 | 2023-11-19 08:30 | 2023-11-19 17:10 | 520 | 970 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 95217 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2023-12420529 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TEMP VERY COLD -FIRST CLASS CHECK IN COUNTER 1 AREA,DEPARTURE . |  | FM008 |  | 2023-11-30 00:57 | 2023-11-30 01:57 | 2023-12-01 01:57 | 24 | 2023-11-30 01:05 | 2023-11-30 04:35 | 210 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 87807 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-12510045 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD -CHECK IN ROW # 1 |  | FM008 |  | 2023-12-27 22:56 | 2023-12-27 23:56 | 2023-12-28 23:56 | 24 | 2023-12-27 23:00 | 2023-12-28 00:20 | 80 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2024-12652917 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 1 COUNTER 1 |  | FM008 |  | 2024-02-17 00:32 | 2024-02-17 01:32 | 2024-02-18 01:32 | 24 | 2024-02-17 00:35 | 2024-02-17 06:30 | 355 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | 108163 | Addali, Ms. Molka | N - - - |  | Voice Communication
| CM-2024-12828534 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD – FIRST CLASS CHECKING COUNTERS ROW 1, CHECKING AREA |  | FM008 |  | 2024-04-17 23:03 | 2024-04-18 00:03 | 2024-04-19 00:03 | 24 | 2024-04-17 23:10 | 2024-04-17 23:55 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 111249 | Zarrouk, Mr. Ismail | N - - - |  | Voice Communication
| CM-2022-10031501 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - PREMIUM SALES OFFICE IN BETWEEN ROW 1 AND 2 |  | FM008 |  | 2022-01-06 15:57 | 2022-01-06 16:57 | 2022-01-07 16:57 | 24 | 2022-01-06 16:06 | 2022-01-06 20:00 | 234 | 70 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 55709 |  |  | 70843 | Mohammed, Mr. Abdul Razak | N - - - |  | Voice Communication
| CM-2022-10096539 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU-A1110-442 RELIEF SIDE BLOWER NOISY T4-09-04 |  | FM008 |  | 2022-01-31 00:20 | 2022-01-31 01:20 | 2022-02-01 01:20 | 24 | 2022-01-31 00:25 | 2022-01-31 02:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 87807 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10160284 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | MTB, LEVEL 2, CHECK-IN ROW 1, COUNTER NUMBER 1 - AC TEMPERATURE IS TOO COLD (PASSENGER COMPLAINT) |  | FM008 |  | 2022-02-21 03:04 | 2022-02-21 03:34 | 2022-02-21 07:34 | 4 | 2022-02-21 03:10 | 2022-02-21 05:15 | 125 | 65 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94954 | 55709 |  |  | 95212 | Kossinnage Dona, Ms. Isuri Tharushi Omka Senevirathna | N - - - |  | Voice Communication
| CM-2022-10154620 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD -CH1 ROW 1 COUNTER 2 |  | FM008 |  | 2022-02-22 04:11 | 2022-02-22 05:11 | 2022-02-23 05:11 | 24 | 2022-02-22 04:15 | 2022-02-22 05:50 | 95 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 55709 |  |  | 85974 | Barra, Ms. Pauline Lhea Galicia | N - - - |  | Voice Communication
| CM-2022-10082377 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - QR PREMIUM SALES DEPARTURE BETWEEN ROO 1 & 2 |  | FM008 |  | 2022-01-27 14:05 | 2022-01-27 15:05 | 2022-01-28 15:05 | 24 | 2022-01-27 14:15 | 2022-01-27 15:05 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 55709 |  |  | 70843 | Mohammed, Mr. Abdul Razak | N - - - |  | Voice Communication
| CM-2022-10569385 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-04-18 08:28 | 2022-04-18 09:28 | 2022-04-19 09:28 | 24 | 2022-04-18 08:37 | 2022-04-18 10:00 | 83 | 249 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95216 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10862466 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TEMPERATURE IS TOO HOT - MTB, LEVEL 2, PREMIUM SALES OFFICE, CHECK-IN ROW 2 |  | FM008 |  | 2022-07-22 22:51 | 2022-07-22 23:51 | 2022-07-23 23:51 | 24 | 2022-07-22 22:55 | 2022-07-22 23:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94954 | 95217 |  |  | 74913 | Macasaet, Mr. Eldred Cruz | N - - - |  | Voice Communication
| CM-2022-11267318 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #1 AREA |  | FM008 |  | 2022-12-13 01:10 | 2022-12-13 02:10 | 2022-12-14 02:10 | 24 | 2022-12-13 01:20 | 2022-12-13 04:10 | 170 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 86359 | Gopez, Ms. Jaychelle Carreon | N - - - |  | Voice Communication
| CM-2022-11296088 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - PREMIUM SALES OFFICE IN BETWEEN ROW 4 AND 5 |  | FM008 |  | 2022-12-21 23:05 | 2022-12-22 00:05 | 2022-12-23 00:05 | 24 | 2022-12-21 23:15 | 2022-12-22 00:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17154 | 17053 |  |  | 117583 | Bargach, Ms. Sabah | N - - - |  | Voice Communication
| CM-2023-11367406 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | QR PREMIUM SALES OFFICE-NEAR CHECK IN ROW#02-AC TOO COLD |  | FM008 |  | 2023-01-14 07:54 | 2023-01-14 08:54 | 2023-01-15 08:54 | 24 | 2023-01-14 08:00 | 2023-01-14 15:15 | 435 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95217 | 55709 |  |  | 97921 | Ansari, Ms. Sana Naaz Mohammed Mehmood | N - - - |  | Voice Communication
| CM-2023-11560320 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES - ROW #1 - COUNTER #1 |  | FM008 |  | 2023-03-15 04:51 | 2023-03-15 05:51 | 2023-03-16 05:51 | 24 | 2023-03-15 05:00 | 2023-03-15 06:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 132112 | 17053 |  |  | 121150 | Haroun, Mr. Salheddine Aymen | N - - - |  | Voice Communication
| CM-2023-11598684 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN ROW 1 |  | FM008 |  | 2023-03-26 14:48 | 2023-03-26 15:48 | 2023-03-27 15:48 | 24 | 2023-03-26 14:55 | 2023-03-26 15:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 118220 | Toktomova, Ms. Nuraiym | N - - - |  | Voice Communication
| CM-2023-11970457 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC NOT WORKING – DEPARTURE IMMIGRATION AREA |  | FM008 |  | 2023-07-11 23:31 | 2023-07-12 00:31 | 2023-07-13 00:31 | 24 | 2023-07-11 23:35 | 2023-07-12 01:02 | 87 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 60639 | Lim, Mr. Ralph Ivan Espiritu | N - - - |  | Voice Communication
| CM-2022-10121257 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AIR FILTER IS DIRTY - AHU-A1110-442 – T4-09-04 |  | FM008 |  | 2022-02-09 15:31 | 2022-02-09 16:31 | 2022-02-10 16:31 | 24 | 2022-02-09 15:40 | 2022-02-09 17:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10366396 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC TOO HOT CHECK IN ROW 1 AND 2 |  | FM008 |  | 2022-04-15 11:16 | 2022-04-15 12:16 | 2022-04-16 12:16 | 24 | 2022-04-15 11:20 | 2022-04-15 12:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 111094 | El Johri, Ms. Houda | N - - - |  | Voice Communication
| CM-2022-10570585 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT DIRTY - CH1 PREMIUM OFFICE |  | FM008 |  | 2022-04-19 05:02 | 2022-04-19 06:02 | 2022-04-20 06:02 | 24 | 2022-04-19 05:12 | 2022-04-19 06:20 | 68 | 136 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10767339 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AHU GRILL IS DIRTY - AHU-A1110-442 - CH1 PREMIUM SALES OFFICE |  | FM008 |  | 2022-06-20 19:46 | 2022-06-20 20:46 | 2022-06-21 20:46 | 24 | 2022-06-20 19:50 | 2022-06-20 21:30 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10951389 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – T4-09-04 |  | FM008 |  | 2022-08-15 13:23 | 2022-08-15 14:23 | 2022-08-16 14:23 | 24 | 2022-08-15 13:30 | 2022-08-15 17:00 | 210 | 176 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 105233 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11513536 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP 2 FILTER ALARM AHU-A1110-442) |  | FM008 |  | 2023-03-04 08:52 | 2023-03-04 09:52 | 2023-03-05 09:52 | 24 | 2023-03-04 09:00 | 2023-03-04 12:19 | 199 | 182 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11507627 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 055 (TAG NO:AHU-A1110-442)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP4.MTB442.AHU442.SYSALM.DP1 / |  | FM008 |  | 2023-03-03 22:29 | 2023-03-03 23:29 | 2023-03-04 23:29 | 24 | 2023-03-03 22:35 | 2023-03-04 01:55 | 200 | 225 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94954 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11609840 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | CHECK IN COUNTER 1 AC TOO COLD |  | FM008 |  | 2023-03-31 05:23 | 2023-03-31 06:23 | 2023-04-01 06:23 | 24 | 2023-03-31 05:30 | 2023-03-31 06:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 118220 | Toktomova, Ms. Nuraiym | N - - - |  | Voice Communication
| CM-2023-12187599 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | SAMSONITE SHOP- CC140 NEAR VIP GATE NO 1 -AC NOT WORKING |  | FM008 |  | 2023-09-15 22:52 | 2023-09-15 23:52 | 2023-09-16 23:52 | 24 | 2023-09-15 22:55 | 2023-09-16 01:05 | 130 | 125 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106914 | 95217 |  |  | 125796 | Sathar, Mr. Anil Abdul | N - - - |  | Voice Communication
| CM-2023-12230261 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT DIRTY - AHU-A1110-442 – CH1 PREMIUM SALES OFFICE |  | FM008 |  | 2023-09-27 18:59 | 2023-09-27 19:59 | 2023-09-28 19:59 | 24 | 2023-09-27 19:05 | 2023-09-27 23:05 | 240 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12793270 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC VENT DIRTY - CH1 PREMIUM SALES OFFICE |  | FM008 |  | 2024-04-03 00:01 | 2024-04-03 01:01 | 2024-04-04 01:01 | 24 | 2024-04-03 00:06 | 2024-04-03 02:06 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12796567 | ASD-MTB-FOF024-AHU055 | AIR HANDLING UNIT-05 | AC NOT WORKING -RO1 AND 2 DEPARTURE AREA |  | FM008 |  | 2024-04-06 10:24 | 2024-04-06 11:24 | 2024-04-07 11:24 | 24 | 2024-04-06 10:30 | 2024-04-06 14:55 | 265 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 121172 | Hajji, Mr. Haythem | N - - - |  | Voice Communication
| CM-2022-10124974 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AIR FILTER IS DIRTY - AHU-A1110-444 - T4-09-04 |  | FM008 |  | 2022-02-12 13:56 | 2022-02-12 14:56 | 2022-02-13 14:56 | 24 | 2022-02-12 14:05 | 2022-02-12 16:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10700847 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-05-29 08:50 | 2022-05-29 09:50 | 2022-05-30 09:50 | 24 | 2022-05-29 09:00 | 2022-05-29 11:25 | 145 | 175 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10728680 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED T4-09-04 |  | FM008 |  | 2022-06-06 20:54 | 2022-06-06 21:54 | 2022-06-07 21:54 | 24 | 2022-06-06 21:00 | 2022-06-06 22:30 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 17053 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2022-10858156 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS-FILTERS 810-AIR HANDLING UNIT 057 (TAG NO:AHU-A1110-444)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-07-17 21:44 | 2022-07-17 22:44 | 2022-07-18 22:44 | 24 | 2022-07-17 21:50 | 2022-07-18 01:00 | 190 | 115 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11196303 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AC VENT DIRTY CH1 PREMIUM OFFICE |  | FM008 |  | 2022-11-18 00:14 | 2022-11-18 01:14 | 2022-11-19 01:14 | 24 | 2022-11-18 00:20 | 2022-11-18 02:10 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11232499 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AHU-A1110-444, AHU-A1110-442, AHU-A1110-440 T4-09-04 |  | FM008 |  | 2022-11-30 08:41 | 2022-11-30 09:41 | 2022-12-01 09:41 | 24 | 2022-11-30 08:50 | 2022-11-30 15:00 | 370 | 1110 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2023-11691028 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - MECHANICAL ROOM T4-09-04 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP5.MTB444.AHU444.SYSALM.DP1 / |  | FM008 |  | 2023-04-20 14:59 | 2023-04-20 15:59 | 2023-04-21 15:59 | 24 | 2023-04-20 15:05 | 2023-04-20 17:50 | 165 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12492666 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU-A1110-444-CABIN LAMP FAULTY (T4-24-01) |  | FM008 |  | 2023-12-21 09:22 | 2023-12-21 10:22 | 2023-12-22 10:22 | 24 | 2023-12-21 09:30 | 2023-12-21 12:15 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 77406 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-11004452 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU-A1110-444 T4-09-04 FILTER ALARM |  | FM008 |  | 2022-09-06 00:13 | 2022-09-06 01:13 | 2022-09-07 01:13 | 24 | 2022-09-06 00:20 | 2022-09-06 01:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 94954 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11834170 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY T4-24-01 |  | FM008 |  | 2023-05-28 21:57 | 2023-05-28 22:57 | 2023-05-29 22:57 | 24 | 2023-05-28 22:00 | 2023-05-29 01:59 | 239 | 233 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17053 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12043458 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AHU-A1110-444 – T4-09-04 |  | FM008 |  | 2023-08-04 19:02 | 2023-08-04 20:02 | 2023-08-05 20:02 | 24 | 2023-08-04 19:10 | 2023-08-05 00:15 | 305 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12200464 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | RELIEF FAN BELT DAMAGED -T4-09-04 |  | FM008 |  | 2023-09-21 00:01 | 2023-09-21 01:01 | 2023-09-22 01:01 | 24 | 2023-09-21 00:05 | 2023-09-21 01:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12200465 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED -T4-09-04 |  | FM008 |  | 2023-09-21 00:02 | 2023-09-21 01:03 | 2023-09-22 01:03 | 24 | 2023-09-21 00:05 | 2023-09-21 03:40 | 215 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11328216 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE IST CLASS CHECK-IN COUNTER AREA |  | FM008 |  | 2022-12-28 18:11 | 2022-12-28 19:11 | 2022-12-29 19:11 | 24 | 2022-12-28 18:20 | 2022-12-28 18:50 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | E-mail
| CM-2023-11360977 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU-A1110-444 DP1 FILTER ALARM T4-09-04 |  | FM008 |  | 2023-01-10 07:29 | 2023-01-10 08:29 | 2023-01-11 08:29 | 24 | 2023-01-10 07:35 | 2023-01-10 08:35 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11476021 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-444 – T4-09-04 |  | FM008 |  | 2023-02-20 07:07 | 2023-02-20 08:07 | 2023-02-21 08:07 | 24 | 2023-02-20 07:15 | 2023-02-20 09:35 | 140 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12000099 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU-A1110-444)-DP1 FILTER ALARM-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-07-23 10:54 | 2023-07-23 11:54 | 2023-07-24 11:54 | 24 | 2023-07-23 11:00 | 2023-07-23 18:45 | 465 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-12211096 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | FILTER DIRTY -AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 -T4-09-04 |  | FM008 |  | 2023-09-23 19:04 | 2023-09-23 20:04 | 2023-09-24 20:04 | 24 | 2023-09-23 19:10 | 2023-09-23 23:15 | 245 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12707233 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU-A1110-444 FILTER DIRTY - T4-09-04 |  | FM008 |  | 2024-03-05 07:49 | 2024-03-05 08:49 | 2024-03-06 08:49 | 24 | 2024-03-05 07:55 | 2024-03-05 10:05 | 130 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12349646 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | SUPPLY SIDE BEARING NOISY T4-09-04 |  | FM008 |  | 2023-11-05 08:35 | 2023-11-05 09:35 | 2023-11-06 09:35 | 24 | 2023-11-05 08:40 | 2023-11-05 14:00 | 320 | 815 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68060 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2024-12828077 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | ROW NO 2 & COUNTER NO 2 AC TOO HOT |  | FM008 |  | 2024-04-16 01:10 | 2024-04-16 02:10 | 2024-04-17 02:10 | 24 | 2024-04-16 01:16 | 2024-04-16 03:40 | 144 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 119320 | 17053 |  |  | 87215 | Sy, Ms. Nicoulette Lacap | N - - - |  | Voice Communication
| CM-2024-12829615 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | T4-09-04;MECHANICALROOM – HEAVY WATER LEAKAGE |  | FM008 |  | 2024-04-19 08:31 | 2024-04-19 09:01 | 2024-04-19 13:01 | 4 | 2024-04-19 08:35 | 2024-04-19 09:35 | 60 | 180 | 3 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 024 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 17053 |  |  | 3981 | CHARLSE | N - - - |  | Voice Communication
| CM-2022-10863766 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM CEILING-NEAR INFORMATION DESK-MEET AND GREET AREA |  | FM008 |  | 2022-07-22 16:45 | 2022-07-22 17:15 | 2022-07-22 21:15 | 4 | 2022-07-22 16:50 | 2022-07-22 17:50 | 60 | 60 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 024 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95217 | 95217 |  |  | FM11261 | Ssessanga, Mr. Isaac | N - - - |  | Voice Communication
| CM-2022-11295511 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU-A1110-444 FILTER ALARM |  | FM008 |  | 2022-12-19 19:08 | 2022-12-19 20:08 | 2022-12-20 20:08 | 24 | 2022-12-19 19:15 | 2022-12-19 21:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10903873 | ASD-MTB-FOF024-AHU057 | AIR HANDLING UNIT-05 | AHU FILTER ALARM |  | FM008 |  | 2022-08-02 19:09 | 2022-08-02 20:09 | 2022-08-03 20:09 | 24 | 2022-08-02 19:15 | 2022-08-02 22:45 | 210 | 225 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 76858 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10747182 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401 FILTER DIRTY T4-24-01 |  | FM008 |  | 2022-06-16 01:25 | 2022-06-16 02:25 | 2022-06-17 02:25 | 24 | 2022-06-16 01:30 | 2022-06-16 03:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 87807 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-10820716 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-07-05 20:11 | 2022-07-05 21:11 | 2022-07-06 21:11 | 24 | 2022-07-05 20:20 | 2022-07-05 22:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10989358 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS – (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-09-02 00:17 | 2022-09-02 01:17 | 2022-09-03 01:17 | 24 | 2022-09-02 00:25 | 2022-09-02 01:25 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11138339 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | FILTER DIRTY - T4-24-01 |  | FM008 |  | 2022-10-28 10:52 | 2022-10-28 11:52 | 2022-10-29 11:52 | 24 | 2022-10-28 11:00 | 2022-10-28 16:00 | 300 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11217302 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-11-24 03:14 | 2022-11-24 04:14 | 2022-11-25 04:14 | 24 | 2022-11-24 03:20 | 2022-11-24 06:00 | 160 | 155 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11764066 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AHU-A1157-401 - AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW401.AHU401.SYSALM.DP3 / |  | FM008 |  | 2023-05-03 14:50 | 2023-05-03 15:50 | 2023-05-04 15:50 | 24 | 2023-05-03 15:00 | 2023-05-03 16:00 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17573 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11768656 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401 – BELT DAMAGED- - |  | FM008 |  | 2023-05-07 15:37 | 2023-05-07 16:37 | 2023-05-08 16:37 | 24 | 2023-05-07 15:45 | 2023-05-07 18:50 | 185 | 105 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11862442 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AHU-A1157-401 - |  | FM008 |  | 2023-06-06 20:02 | 2023-06-06 21:02 | 2023-06-07 21:02 | 24 | 2023-06-06 20:10 | 2023-06-06 22:40 | 150 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12012255 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401-RETURN GRILL BLOCKED . |  | FM008 |  | 2023-07-25 13:37 | 2023-07-25 14:37 | 2023-07-26 14:37 | 24 | 2023-07-25 13:45 | 2023-07-25 17:45 | 240 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12198774 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-09-18 01:04 | 2023-09-18 02:04 | 2023-09-19 02:04 | 24 | 2023-09-18 01:10 | 2023-09-18 03:10 | 120 | 125 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12324697 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | FILTER DIRTY - T4-24-01 |  | FM008 |  | 2023-10-25 07:11 | 2023-10-25 08:11 | 2023-10-26 08:11 | 24 | 2023-10-25 07:20 | 2023-10-25 08:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12511516 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1157-401) - T4 24 01 |  | FM008 |  | 2023-12-27 19:48 | 2023-12-27 20:48 | 2023-12-28 20:48 | 24 | 2023-12-27 19:50 | 2023-12-27 23:00 | 190 | 380 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2022-11028079 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - FILTERS 946-AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW401.AHU401.SYSALM.DP3 / |  | FM008 |  | 2022-09-17 01:43 | 2022-09-17 02:43 | 2022-09-18 02:43 | 24 | 2022-09-17 01:50 | 2022-09-17 04:30 | 160 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11365428 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1157-401 – T4-24-01 |  | FM008 |  | 2023-01-13 17:31 | 2023-01-13 18:31 | 2023-01-14 18:31 | 24 | 2023-01-13 17:35 | 2023-01-13 18:55 | 80 | 320 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12059222 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401)-COOLING COIL DIRTY-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-08-09 19:34 | 2023-08-09 20:34 | 2023-08-10 20:34 | 24 | 2023-08-09 19:40 | 2023-08-09 23:00 | 200 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12366280 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – TG-24-01 |  | FM008 |  | 2023-11-10 19:41 | 2023-11-10 20:41 | 2023-11-11 20:41 | 24 | 2023-11-10 19:50 | 2023-11-10 23:00 | 190 | 380 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2022-10952933 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401-AHU FILTER DIRTY |  | FM008 |  | 2022-08-17 02:46 | 2022-08-17 03:46 | 2022-08-18 03:46 | 24 | 2022-08-17 02:50 | 2022-08-17 06:05 | 195 | 370 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11078637 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW401.AHU401.SYSALM.DP3 / |  | FM008 |  | 2022-10-06 11:27 | 2022-10-06 12:27 | 2022-10-07 12:27 | 24 | 2022-10-06 11:35 | 2022-10-06 13:30 | 115 | 65 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2022-11175970 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1157-401 – T4-24-01 |  | FM008 |  | 2022-11-09 08:46 | 2022-11-09 09:46 | 2022-11-10 09:46 | 24 | 2022-11-09 08:50 | 2022-11-09 16:35 | 465 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11883864 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ASD-MTB-FOF024-AHU193 AHU-A1157-401 AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW401.AHU4 |  | FM008 |  | 2023-06-16 06:38 | 2023-06-16 07:38 | 2023-06-17 07:38 | 24 | 2023-06-16 06:45 | 2023-06-16 08:35 | 110 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2024-12670459 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | RETURN DUCT BLOCKED -T4-24-01 |  | FM008 |  | 2024-02-20 13:20 | 2024-02-20 14:20 | 2024-02-21 14:20 | 24 | 2024-02-20 13:25 | 2024-02-20 16:10 | 165 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12511670 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | SUPPLY BLOWER NOISY |  | FM008 |  | 2023-12-28 08:58 | 2023-12-28 09:58 | 2023-12-29 09:58 | 24 | 2023-12-28 09:05 | 2023-12-28 12:35 | 210 | 630 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12511822 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-12-28 18:22 | 2023-12-28 19:22 | 2023-12-29 19:22 | 24 | 2023-12-28 18:30 | 2023-12-28 21:00 | 150 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 106914 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12667408 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401 FILTER DIRTY A4-24-01 |  | FM008 |  | 2024-02-21 13:43 | 2024-02-21 14:43 | 2024-02-22 14:43 | 24 | 2024-02-21 13:50 | 2024-02-21 15:30 | 100 | 125 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 17053 |  |  | FM5553 | MOHAMAD HANEEF ABDUL HAMEED MAJGAONKAR, | N - - - |  | Voice Communication
| CM-2023-12514925 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- AHU-A1157-401 – T4-24-01 |  | FM008 |  | 2023-12-29 12:32 | 2023-12-29 13:32 | 2023-12-30 13:32 | 24 | 2023-12-29 12:40 | 2023-12-29 15:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10331492 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - FILTERS 946-AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024;PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW401.AHU401.SYSALM.DP3 / |  | FM008 |  | 2022-04-07 10:10 | 2022-04-07 11:10 | 2022-04-08 11:10 | 24 | 2022-04-07 10:20 | 2022-04-07 17:10 | 410 | 125 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10147540 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – T4-24-01 |  | FM008 |  | 2022-02-19 19:23 | 2022-02-19 20:23 | 2022-02-20 20:23 | 24 | 2022-02-19 19:30 | 2022-02-19 23:45 | 255 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-10273812 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS FILTERS 946-AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-03-22 14:18 | 2022-03-22 15:18 | 2022-03-23 15:18 | 24 | 2022-03-22 14:25 | 2022-03-22 21:00 | 395 | 250 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17154 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11066514 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AHU-A1157-401 FILTER AIR HANDLING UNIT 193 (TAG NO:AHU-A1157-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-10-01 18:50 | 2022-10-01 19:50 | 2022-10-02 19:50 | 24 | 2022-10-01 19:00 | 2022-10-01 20:00 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-11096038 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT CANVAS DAMAGED - AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-10-12 07:44 | 2022-10-12 08:44 | 2022-10-13 08:44 | 24 | 2022-10-12 07:50 | 2022-10-12 09:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11173005 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | SUPPLY BLOWER SENSOR TUBE DAMAGED - AHU-A1157-401 |  | FM008 |  | 2022-11-08 07:42 | 2022-11-08 08:42 | 2022-11-09 08:42 | 24 | 2022-11-08 07:50 | 2022-11-08 09:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2023-11365573 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT -CABIN LIGHT DAMAGE -T4-24-01 |  | FM008 |  | 2023-01-14 10:03 | 2023-01-14 11:03 | 2023-01-15 11:03 | 24 | 2023-01-14 10:13 | 2023-01-14 13:10 | 177 | 354 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 77406 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-12164627 | ASD-MTB-FOF024-AHU193 | AIR HANDLING UNIT-05 | COOLING COIL DIRY -AHU-A11157-401-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-09-08 09:00 | 2023-09-08 10:00 | 2023-09-09 10:00 | 24 | 2023-09-08 09:10 | 2023-09-08 12:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-10043947 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1157-402 |  | FM008 |  | 2022-01-10 12:28 | 2022-01-10 13:28 | 2022-01-11 13:28 | 24 | 2022-01-10 12:35 | 2022-01-10 15:30 | 175 | 350 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-10041970 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-01-10 14:21 | 2022-01-10 15:21 | 2022-01-11 15:21 | 24 | 2022-01-10 14:30 | 2022-01-10 17:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 55709 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | BMS
| CM-2022-10917167 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AHU-A1157-402 – FILTER DIRTY-- |  | FM008 |  | 2022-08-08 07:42 | 2022-08-08 08:42 | 2022-08-09 08:42 | 24 | 2022-08-08 07:50 | 2022-08-08 12:15 | 265 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12202204 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT 194 (TAG NO:AHU-A1157-402)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-09-19 07:16 | 2023-09-19 08:16 | 2023-09-20 08:16 | 24 | 2023-09-19 07:20 | 2023-09-19 09:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12324975 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-10-26 00:02 | 2023-10-26 01:02 | 2023-10-27 01:02 | 24 | 2023-10-26 00:10 | 2023-10-26 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11145418 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | FILTER DIRTY- AHU-A1157-402 |  | FM008 |  | 2022-10-27 23:02 | 2022-10-28 00:02 | 2022-10-29 00:02 | 24 | 2022-10-27 23:10 | 2022-10-28 01:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-11216933 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - ROOM# T4-24-01 |  | FM008 |  | 2022-11-25 19:36 | 2022-11-25 20:36 | 2022-11-26 20:36 | 24 | 2022-11-25 19:45 | 2022-11-25 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11259518 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AHU-A1157-402 COOLING COIL DIRTY T4-24-01 |  | FM008 |  | 2022-12-09 19:13 | 2022-12-09 20:13 | 2022-12-10 20:13 | 24 | 2022-12-09 19:25 | 2022-12-09 23:25 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11365295 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AHU-A1157-402 COOLING COIL DIRTY |  | FM008 |  | 2023-01-12 20:48 | 2023-01-12 21:48 | 2023-01-13 21:48 | 24 | 2023-01-12 20:55 | 2023-01-13 | 185 | 555 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17053 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12059221 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AHU-A1157-402,-FILTER DIRTY-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-08-09 19:33 | 2023-08-09 20:33 | 2023-08-10 20:33 | 24 | 2023-08-09 19:40 | 2023-08-09 23:40 | 240 | 480 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12138854 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AHU-COOLING COIL DIRTY (T4-24-01) |  | FM008 |  | 2023-09-02 19:45 | 2023-09-02 20:45 | 2023-09-03 20:45 | 24 | 2023-09-02 19:50 | 2023-09-02 22:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 77406 | 77406 |  |  | FM5273 | Hannanur Rahman, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-11249722 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 194,-FILTER DIRTY--MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-12-06 01:12 | 2022-12-06 02:12 | 2022-12-07 02:12 | 24 | 2022-12-06 01:20 | 2022-12-06 04:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11548489 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1157-402 - T4-24-01 |  | FM008 |  | 2023-03-10 08:33 | 2023-03-10 09:33 | 2023-03-11 09:33 | 24 | 2023-03-10 08:40 | 2023-03-10 14:40 | 360 | 725 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12515060 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1157-402 -T4-24-01 |  | FM008 |  | 2023-12-30 08:23 | 2023-12-30 09:23 | 2023-12-31 09:23 | 24 | 2023-12-30 08:30 | 2023-12-30 11:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12671552 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | PANEL BASE RUSTED MCC-AHU-1157-402 - T4-24-01 |  | FM008 |  | 2024-02-22 01:24 | 2024-02-22 02:24 | 2024-02-23 02:24 | 24 | 2024-02-22 01:30 | 2024-02-22 05:47 | 257 | 359 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | UNIT IS RUSTED | CLEANED & REPAINT THE UNIT | 106914 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-11367516 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT ILLUMINATING - AHU-A1157-402 T4-24-01, |  | FM008 |  | 2023-01-14 19:20 | 2023-01-14 20:20 | 2023-01-15 20:20 | 24 | 2023-01-14 19:30 | 2023-01-14 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 133396 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11625584 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2023-04-06 19:10 | 2023-04-06 20:10 | 2023-04-07 20:10 | 24 | 2023-04-06 19:15 | 2023-04-06 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12164757 | ASD-MTB-FOF024-AHU194 | AIR HANDLING UNIT-05 | T4-24-01 AHU-A1157-402 COOLING COIL DIRTY |  | FM008 |  | 2023-09-08 19:55 | 2023-09-08 20:55 | 2023-09-09 20:55 | 24 | 2023-09-08 20:00 | 2023-09-08 23:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2022-10368407 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | AHU-A1157-403 – FILTER DIRTY-- |  | FM008 |  | 2022-04-15 19:21 | 2022-04-15 20:21 | 2022-04-16 20:21 | 24 | 2022-04-15 19:30 | 2022-04-15 21:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10933021 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW401.AHU403.SYSALM.DP3 / |  | FM008 |  | 2022-08-13 23:35 | 2022-08-14 00:35 | 2022-08-15 00:35 | 24 | 2022-08-13 23:40 | 2022-08-14 00:40 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM0459 | MANHANDAVIDA SHAHEEL | N - - - |  | E-mail
| CM-2023-11652605 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | CABIN LIGHT NOT WORKING-AHU-A1157-403-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-04-11 19:08 | 2023-04-11 20:08 | 2023-04-12 20:08 | 24 | 2023-04-11 19:15 | 2023-04-11 22:00 | 165 | 235 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 77406 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-11853763 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AIR HANDLING UNIT 195 (TAG NO:AHU-A1157-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-06-05 22:47 | 2023-06-05 23:48 | 2023-06-06 23:48 | 24 | 2023-06-05 22:55 | 2023-06-06 02:00 | 185 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 94954 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11972933 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | AHU-A1157-403 DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-07-13 17:39 | 2023-07-13 18:39 | 2023-07-14 18:39 | 24 | 2023-07-13 17:45 | 2023-07-13 18:55 | 70 | 85 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12055168 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | FILTER DIRTY – AHU-A1157-403- T4 24 01 |  | FM008 |  | 2023-08-07 00:11 | 2023-08-07 01:11 | 2023-08-08 01:11 | 24 | 2023-08-07 00:20 | 2023-08-07 02:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12062661 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | QA1 MAIN DINING – AC NOT WORKING |  | FM008 |  | 2023-08-08 11:43 | 2023-08-08 12:43 | 2023-08-09 12:43 | 24 | 2023-08-08 11:50 | 2023-08-08 16:30 | 280 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17573 | 87807 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-12511515 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1157-403) – T4 24 01 |  | FM008 |  | 2023-12-27 19:46 | 2023-12-27 20:46 | 2023-12-28 20:46 | 24 | 2023-12-27 19:50 | 2023-12-27 23:00 | 190 | 570 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2024-12536703 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | RETURN SIDE BLOWER NOISY – T4-24-01 |  | FM008 |  | 2024-01-06 08:35 | 2024-01-06 09:35 | 2024-01-07 09:35 | 24 | 2024-01-06 08:40 | 2024-01-06 13:00 | 260 | 370 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2024-12537799 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | AHU-A1157-403 DUCT INSULATION DAMAGED T4-24-01 |  | FM008 |  | 2024-01-06 19:54 | 2024-01-06 20:54 | 2024-01-07 20:54 | 24 | 2024-01-06 20:00 | 2024-01-06 22:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11145420 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-403 |  | FM008 |  | 2022-10-27 23:03 | 2022-10-28 00:03 | 2022-10-29 00:03 | 24 | 2022-10-27 23:10 | 2022-10-28 03:25 | 255 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-11250916 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | Logical View.BAC3.IBF EAST.IBF E Fourth Floor T4-24-01.IBF DDC-A1157-AHU-403+401.DDC-A1157-AHU-403.System Alarms PH1-Supply Duct Hi Pressure Alm [PhAlm] - A1157-CON B IBF-AHU-403 PH1 SUPPLY DUCT HI PRESSURE ALARM |  | FM008 |  | 2022-12-05 22:02 | 2022-12-05 23:02 | 2022-12-06 23:02 | 24 | 2022-12-05 22:10 | 2022-12-05 23:10 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 17154 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11559242 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | AC TOO HOT IN THE VIP LOUNGE GROUND FLOOR – IN THE RECEPTION AND COUNTERS AREA |  | FM008 |  | 2023-03-13 08:00 | 2023-03-13 09:00 | 2023-03-14 09:00 | 24 | 2023-03-13 08:05 | 2023-03-13 14:30 | 385 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 59398 | Jait, Mr. Mounir | N - - - |  | Voice Communication
| CM-2023-11883616 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | PH1-SUPPLY DUCT HI PRESSURE ALARM, AHU-A1157-403 |  | FM008 |  | 2023-06-15 06:16 | 2023-06-15 07:16 | 2023-06-16 07:16 | 24 | 2023-06-15 06:25 | 2023-06-15 08:00 | 95 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 124475 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12154553 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT INSULATION DAMAGED – (AHU-A1157-403) T4 24 01 |  | FM008 |  | 2023-09-04 14:48 | 2023-09-04 15:48 | 2023-09-05 15:48 | 24 | 2023-09-04 14:55 | 2023-09-04 16:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-10924488 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-08-08 16:38 | 2022-08-08 17:38 | 2022-08-09 17:38 | 24 | 2022-08-08 16:45 | 2022-08-08 17:15 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11826961 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | AHU-A1157-403 FILTER DIRTY |  | FM008 |  | 2023-05-27 21:08 | 2023-05-27 22:08 | 2023-05-28 22:08 | 24 | 2023-05-27 21:15 | 2023-05-27 23:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11948280 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-403 |  | FM008 |  | 2023-07-05 09:38 | 2023-07-05 10:38 | 2023-07-06 10:38 | 24 | 2023-07-05 09:45 | 2023-07-05 12:30 | 165 | 370 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12099134 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | PH1-SUPPLY DUCT HI PRESSURE ALM-AIR HANDLING UNIT 195 (TAG NO:AHU-A1157-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024-LOGICAL VIEW.BAC3.IBF EAST.IBF E FOURTH FLOOR T4-24-01.IBF DDC-A1157-AHU-403+401.DDC-A1157-AHU-403.SYSTEM A |  | FM008 |  | 2023-08-20 04:07 | 2023-08-20 05:07 | 2023-08-21 05:07 | 24 | 2023-08-20 04:15 | 2023-08-20 04:45 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | AHU TRIP ALARM | RESET UNIT | 95217 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12230374 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | PH1-SUPPLY DUCT HI PRESSURE ALM [PHALM] -AIR HANDLING UNIT 195 (TAG NO:AHU-A1157-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-09-28 12:28 | 2023-09-28 13:28 | 2023-09-29 13:28 | 24 | 2023-09-28 12:35 | 2023-09-28 13:05 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 106914 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2023-12511669 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | SUPPLY BLOWER NOISY |  | FM008 |  | 2023-12-28 08:57 | 2023-12-28 09:57 | 2023-12-29 09:57 | 24 | 2023-12-28 09:05 | 2023-12-28 12:35 | 210 | 630 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12534925 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY - T4-24-01 |  | FM008 |  | 2024-01-06 12:30 | 2024-01-06 13:30 | 2024-01-07 13:30 | 24 | 2024-01-06 12:35 | 2024-01-06 14:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10863488 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM GLASS PANEL – NEAREST DOOR NUMBER B1-17A-08 |  | FM008 |  | 2022-07-22 19:29 | 2022-07-22 19:59 | 2022-07-22 23:59 | 4 | 2022-07-22 19:35 | 2022-07-22 20:35 | 60 | 60 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 024 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94954 | 95217 |  |  | FM8002 | Ruku, Mr. Antony Chege | N - - - |  | Voice Communication
| CM-2022-11326816 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1157-403 – T4-24-01 |  | FM008 |  | 2022-12-27 07:30 | 2022-12-27 08:30 | 2022-12-28 08:30 | 24 | 2022-12-27 07:35 | 2022-12-27 09:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106973 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10034706 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY;AHU-A1157-403 - T4-24-01 |  | FM008 |  | 2022-01-09 09:25 | 2022-01-09 10:25 | 2022-01-10 10:25 | 24 | 2022-01-09 09:30 | 2022-01-09 11:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 55709 |  |  | FM5553 | Mohamad Haneef Abdul Hameed, Mr. Majgaonkar | N - - - |  | Voice Communication
| CM-2022-10888839 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | B1-16A-05 - WATER LEAKAGE FROM GLASS PANEL - NEAR WALKALATOR B-MW-2)- |  | FM008 |  | 2022-07-31 11:27 | 2022-07-31 12:27 | 2022-08-01 12:27 | 24 | 2022-07-31 11:30 | 2022-07-31 12:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 87807 |  |  | FM8002 | Ruku, Mr. Antony Chege | N - - - |  | Voice Communication
| CM-2023-11948554 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | RETUNE DUCT ABNORMAL NOISE - AHU-A1157-403 – T4-24-01 |  | FM008 |  | 2023-07-06 07:28 | 2023-07-06 08:28 | 2023-07-07 08:28 | 24 | 2023-07-06 07:35 | 2023-07-06 09:00 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17573 | 94954 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12229126 | ASD-MTB-FOF024-AHU195 | AIR HANDLING UNIT-05 | PH1-SUPPLY DUCT HI PRESSURE ALM [PHALM] AIR HANDLING UNIT 195 (TAG NO:AHU-A1157-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-09-27 10:19 | 2023-09-27 11:18 | 2023-09-28 11:18 | 24 | 2023-09-27 10:25 | 2023-09-27 11:25 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-11440721 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -AIR HANDLING UNIT 196 (TAG NO:AHU-A1157-404)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-02-09 13:21 | 2023-02-09 14:21 | 2023-02-10 14:21 | 24 | 2023-02-09 13:25 | 2023-02-09 15:30 | 125 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11932400 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-06-27 07:35 | 2023-06-27 08:35 | 2023-06-28 08:35 | 24 | 2023-06-27 07:40 | 2023-06-27 09:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12507529 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AHU-FILTER DIRTY -T4-24-01 |  | FM008 |  | 2023-12-26 07:55 | 2023-12-26 08:55 | 2023-12-27 08:55 | 24 | 2023-12-26 08:00 | 2023-12-26 10:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12507764 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - T4-24-01 |  | FM008 |  | 2023-12-27 07:52 | 2023-12-27 08:52 | 2023-12-28 08:52 | 24 | 2023-12-27 08:00 | 2023-12-27 14:30 | 390 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 121959 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11570375 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 196 (TAG NO:AHU-A1157-404)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-03-20 10:37 | 2023-03-20 11:37 | 2023-03-21 11:37 | 24 | 2023-03-20 10:45 | 2023-03-20 15:45 | 300 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12226055 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1157-404 |  | FM008 |  | 2023-09-25 16:29 | 2023-09-25 17:29 | 2023-09-26 17:29 | 24 | 2023-09-25 16:35 | 2023-09-26 01:00 | 505 | 234 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12231318 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH FAULTY - T4-24-01 |  | FM008 |  | 2023-09-28 02:00 | 2023-09-28 03:00 | 2023-09-29 03:00 | 24 | 2023-09-28 02:10 | 2023-09-28 05:09 | 179 | 358 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 87807 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2024-12756990 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | PH1-SUPPLY DUCT HI PRESSURE ALM AHU-A1157-404 |  | FM008 |  | 2024-03-24 09:36 | 2024-03-24 10:36 | 2024-03-25 10:36 | 24 | 2024-03-24 09:45 | 2024-03-24 10:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | THERMOSTAT VALUE MISMATCH | RECTIFIED | 89127 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12445920 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM AIR HANDLING UNIT |  | FM008 |  | 2023-12-05 11:04 | 2023-12-05 12:04 | 2023-12-06 12:04 | 24 | 2023-12-05 11:10 | 2023-12-05 18:00 | 410 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12514923 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AHU -CABIN LAMP FAULTY -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-12-29 12:30 | 2023-12-29 13:30 | 2023-12-30 13:30 | 24 | 2023-12-29 12:40 | 2023-12-29 18:15 | 335 | 335 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 77406 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12845759 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AHU-A1157-404)-FILTER DIRTY -T4-24-01 |  | FM008 |  | 2024-04-22 00:20 | 2024-04-22 01:20 | 2024-04-23 01:20 | 24 | 2024-04-22 00:25 | 2024-04-22 04:20 | 235 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2022-11078305 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | FILTER ALARM – T4-24-01 |  | FM008 |  | 2022-10-04 08:22 | 2022-10-04 09:22 | 2022-10-05 09:22 | 24 | 2022-10-04 08:30 | 2022-10-04 10:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106914 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11148185 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-404 |  | FM008 |  | 2022-10-28 19:45 | 2022-10-28 20:45 | 2022-10-29 20:45 | 24 | 2022-10-28 19:50 | 2022-10-28 23:55 | 245 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11645230 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AHU-A1157-404 DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-04-11 01:21 | 2023-04-11 02:21 | 2023-04-12 02:21 | 24 | 2023-04-11 01:30 | 2023-04-11 06:00 | 270 | 225 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 94954 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10032087 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-01-07 19:24 | 2022-01-07 20:24 | 2022-01-08 20:24 | 24 | 2022-01-07 19:30 | 2022-01-07 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10162323 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | AC TOO HOT T3-24-47 |  | FM008 |  | 2022-02-24 10:56 | 2022-02-24 11:56 | 2022-02-25 11:56 | 24 | 2022-02-24 11:05 | 2022-02-24 12:05 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 55709 |  |  | 58414 | Fernando, Mr. Karunamuni Kavinda Ransiri | N - - - |  | Voice Communication
| CM-2022-10223747 | ASD-MTB-FOF024-AHU196 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1157-404 T4-24-01 |  | FM008 |  | 2022-03-07 22:41 | 2022-03-07 23:41 | 2022-03-08 23:41 | 24 | 2022-03-07 22:50 | 2022-03-08 01:45 | 175 | 310 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 85125 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11219609 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT INSULATION DAMAGED |  | FM008 |  | 2022-11-26 16:43 | 2022-11-26 17:43 | 2022-11-27 17:43 | 24 | 2022-11-26 16:55 | 2022-11-26 18:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM5553 | MOHAMAD HANEEF ABDUL HAMEED MAJGAONKAR, | N - - - |  | Voice Communication
| CM-2023-12232205 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – T4-24-01 |  | FM008 |  | 2023-09-27 20:39 | 2023-09-27 21:39 | 2023-09-28 21:39 | 24 | 2023-09-27 20:45 | 2023-09-27 23:00 | 135 | 405 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 105233 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12324698 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | AHU-A1157-405 FILTER DIRTY – T4-24-01 |  | FM008 |  | 2023-10-25 07:13 | 2023-10-25 08:13 | 2023-10-26 08:13 | 24 | 2023-10-25 07:20 | 2023-10-25 10:30 | 190 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11936392 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH DAMAGED - AHU-A1157-405 – T4-24-01 |  | FM008 |  | 2023-07-01 09:42 | 2023-07-01 10:42 | 2023-07-02 10:42 | 24 | 2023-07-01 09:51 | 2023-07-01 12:20 | 149 | 298 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2023-12223634 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1157-405 - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.4FLRP1.IBFW404.AHU405.SYSALM.DP1 / |  | FM008 |  | 2023-09-25 10:30 | 2023-09-25 11:30 | 2023-09-26 11:30 | 24 | 2023-09-25 10:40 | 2023-09-25 13:00 | 140 | 280 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12450986 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT -UNUSUAL SOUND FROM AHU-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-12-06 09:26 | 2023-12-06 10:26 | 2023-12-07 10:26 | 24 | 2023-12-06 09:35 | 2023-12-06 13:00 | 205 | 725 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 77406 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12505166 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | AHU-FILTER DIRTY -T4-24-01 |  | FM008 |  | 2023-12-26 07:54 | 2023-12-26 08:54 | 2023-12-27 08:54 | 24 | 2023-12-26 08:00 | 2023-12-26 14:40 | 400 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10171345 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | T3-24-45 AC TOO HOT |  | FM008 |  | 2022-02-24 10:28 | 2022-02-24 11:28 | 2022-02-25 11:28 | 24 | 2022-02-24 10:35 | 2022-02-24 13:25 | 170 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 55709 |  |  | 53546 | Garcia, Mr. Cer Zyrus Manukay | N - - - |  | Voice Communication
| CM-2022-10171360 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | T3-24-49 AC TOO HOT |  | FM008 |  | 2022-02-24 10:50 | 2022-02-24 11:50 | 2022-02-25 11:50 | 24 | 2022-02-24 10:55 | 2022-02-24 14:55 | 240 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 55709 |  |  | 90037 | Solomon, Mr. Jaison | N - - - |  | Voice Communication
| CM-2022-10125131 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – T4-24-01 |  | FM008 |  | 2022-02-12 19:42 | 2022-02-12 20:42 | 2022-02-13 20:42 | 24 | 2022-02-12 19:50 | 2022-02-12 22:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM5553 | Mohamad Haneef Abdul Hameed, Mr. Majgaonkar | N - - - |  | Voice Communication
| CM-2022-11148184 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1157-405 |  | FM008 |  | 2022-10-28 19:43 | 2022-10-28 20:43 | 2022-10-29 20:43 | 24 | 2022-10-28 19:50 | 2022-10-28 21:45 | 115 | 345 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 124475 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2022-11298888 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | AHU-A1157-405 MARINE LIGHT NOT WORKING |  | FM008 |  | 2022-12-25 09:58 | 2022-12-25 10:58 | 2022-12-26 10:58 | 24 | 2022-12-25 10:05 | 2022-12-25 13:05 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68485 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10031995 | ASD-MTB-FOF024-AHU197 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1157-405)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-01-07 14:33 | 2022-01-07 15:33 | 2022-01-08 15:33 | 24 | 2022-01-07 14:40 | 2022-01-07 16:45 | 125 | 375 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-10723336 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-05 20:42 | 2022-06-05 21:42 | 2022-06-06 21:42 | 24 | 2022-06-05 20:50 | 2022-06-05 22:00 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2022-10863511 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - FILTERS 785-AIR HANDLING UNIT 032 (TAG NO:AHU-A1110-419)-AIRSIDE-MTB-FOURTH FLOOR AREA 010 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP3.MTB445.AHU419.SYSALM.DP1 / |  | FM008 |  | 2022-07-23 01:28 | 2022-07-23 02:28 | 2022-07-24 02:28 | 24 | 2022-07-23 01:35 | 2022-07-23 02:58 | 83 | 121 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11015292 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU-A1110-419 FILTER ALARM- - |  | FM008 |  | 2022-09-13 00:09 | 2022-09-13 01:09 | 2022-09-14 01:09 | 24 | 2022-09-13 00:15 | 2022-09-13 01:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11022208 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU LAMP NOT WORKING - AHU-A1110-419 |  | FM008 |  | 2022-09-13 20:30 | 2022-09-13 21:30 | 2022-09-14 21:30 | 24 | 2022-09-13 20:40 | 2022-09-13 23:50 | 190 | 175 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | FAULTY CONTROL THERMOSTAT | REPLACED THE THERMOSTAT | 17053 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11178097 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-419 – T4-10-03 |  | FM008 |  | 2022-11-12 19:15 | 2022-11-12 20:15 | 2022-11-13 20:15 | 24 | 2022-11-12 19:25 | 2022-11-12 21:20 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11625186 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU-A1110-419-FILTER DIRTY--MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-04-09 07:25 | 2023-04-09 08:25 | 2023-04-10 08:25 | 24 | 2023-04-09 07:35 | 2023-04-09 09:04 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12509963 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | SUPPLY BLOWER VERY NOISY -- (TAG NO:AHU-A1110-419)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-12-27 13:30 | 2023-12-27 14:30 | 2023-12-28 14:30 | 24 | 2023-12-27 13:40 | 2023-12-27 17:40 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 138627 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12689873 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED - AHU-A1110-419 – T4-10-03 |  | FM008 |  | 2024-02-28 22:18 | 2024-02-28 23:18 | 2024-02-29 23:18 | 24 | 2024-02-28 22:28 | 2024-02-29 01:12 | 164 | 328 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106973 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2022-10903516 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -T4-08-04 |  | FM008 |  | 2022-08-01 05:08 | 2022-08-01 06:08 | 2022-08-02 06:08 | 24 | 2022-08-01 05:18 | 2022-08-01 06:18 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12314027 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY AHU-A1110-419 - T4-09-04 |  | FM008 |  | 2023-10-24 15:34 | 2023-10-24 16:34 | 2023-10-25 16:34 | 24 | 2023-10-24 15:40 | 2023-10-24 18:40 | 180 | 175 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-11041109 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-10-03 |  | FM008 |  | 2022-09-23 22:50 | 2022-09-23 23:50 | 2022-09-24 23:50 | 24 | 2022-09-23 22:55 | 2022-09-23 23:55 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11361535 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | SUPPLY AND RETURN V BELT DAMAGED - AHU-A1110-419 – T4-08-04 |  | FM008 |  | 2023-01-08 23:21 | 2023-01-09 00:21 | 2023-01-10 00:21 | 24 | 2023-01-08 23:25 | 2023-01-09 01:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11550702 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU DRAIN LINE BLOCKED - AHU-A1110-419 – T4-08-04 |  | FM008 |  | 2023-03-10 20:37 | 2023-03-10 21:37 | 2023-03-11 21:37 | 24 | 2023-03-10 20:45 | 2023-03-10 22:30 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17573 | 87807 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2022-10044480 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY T4-08-04 TAG NO:AHU-A1110-419 |  | FM008 |  | 2022-01-13 00:11 | 2022-01-13 01:11 | 2022-01-14 01:11 | 24 | 2022-01-13 00:20 | 2022-01-13 06:45 | 385 | 135 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10128944 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU-A1110-419 – FILTER IS DIRTY – T4-08-04 |  | FM008 |  | 2022-02-11 19:15 | 2022-02-11 20:15 | 2022-02-12 20:15 | 24 | 2022-02-11 19:25 | 2022-02-11 21:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10308838 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU-A1110-419 DP3 FILTER ALARM |  | FM008 |  | 2022-03-30 11:50 | 2022-03-30 12:50 | 2022-03-31 12:50 | 24 | 2022-03-30 11:55 | 2022-03-30 13:20 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10660496 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU-A1110-419- DP3 FILTER ALAM-- |  | FM008 |  | 2022-05-14 12:22 | 2022-05-14 13:22 | 2022-05-15 13:22 | 24 | 2022-05-14 12:30 | 2022-05-14 14:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 94953 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10934670 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU FILTER IS IDRTY - AHU-A1110-419 - MECHANICAL ROOM T4-10-03 |  | FM008 |  | 2022-08-13 08:30 | 2022-08-13 09:30 | 2022-08-14 09:30 | 24 | 2022-08-13 08:35 | 2022-08-13 10:05 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10128957 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED-AHU-A1110-419)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-02-12 00:28 | 2022-02-12 01:28 | 2022-02-13 01:28 | 24 | 2022-02-12 00:30 | 2022-02-12 02:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 55709 |  |  | fm3093 | fm3093 | N - - - |  | Voice Communication
| CM-2022-10154613 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM SUPPLY DUCT ACCESS DOOR - AHU-A1110-419 – T4-08-04 |  | FM008 |  | 2022-02-22 02:45 | 2022-02-22 03:45 | 2022-02-23 03:45 | 24 | 2022-02-22 02:54 | 2022-02-22 04:20 | 86 | 172 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-11446511 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | AHU-A1110-419 DP1 FILTER DIRTY |  | FM008 |  | 2023-02-10 09:33 | 2023-02-10 10:33 | 2023-02-11 10:33 | 24 | 2023-02-10 09:40 | 2023-02-10 11:20 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11938153 | ASD-MTB-FOF010-AHU032 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY, AHU-A1110-419, T4-08-04 |  | FM008 |  | 2023-07-01 08:52 | 2023-07-01 09:52 | 2023-07-02 09:52 | 24 | 2023-07-01 09:00 | 2023-07-01 12:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10691947 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AHU-A1110-423 FILTER DIRTY T4-21-03 |  | FM008 |  | 2022-05-25 19:07 | 2022-05-25 20:07 | 2022-05-26 20:07 | 24 | 2022-05-25 19:17 | 2022-05-25 21:10 | 113 | 339 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10712720 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM AHU - (TAG NO:AHU-A1110-423) MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-06-02 09:34 | 2022-06-02 10:34 | 2022-06-03 10:34 | 24 | 2022-06-02 09:40 | 2022-06-02 10:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 17053 |  |  | 63817 | Ntale, Mr. Henry | N - - - |  | Voice Communication
| CM-2023-11396239 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | (A1110-423)-DP1-FILTER ALARM-T4-21-03 |  | FM008 |  | 2023-01-23 00:25 | 2023-01-23 01:25 | 2023-01-24 01:25 | 24 | 2023-01-23 00:30 | 2023-01-23 01:30 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11901761 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-08-04 |  | FM008 |  | 2023-06-21 21:00 | 2023-06-21 22:00 | 2023-06-22 22:00 | 24 | 2023-06-21 21:06 | 2023-06-21 23:50 | 164 | 201 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11028058 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AHU-A1110-423 - AHU INSIDE LAMP IS NOT WORKING – T4-21-03 |  | FM008 |  | 2022-09-16 21:48 | 2022-09-16 22:48 | 2022-09-17 22:48 | 24 | 2022-09-16 21:55 | 2022-09-16 23:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94954 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11805229 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-423 – T4-08-04 |  | FM008 |  | 2023-05-21 16:06 | 2023-05-21 17:06 | 2023-05-22 17:06 | 24 | 2023-05-21 16:12 | 2023-05-21 18:12 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11878121 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AHU-A1110-423/409/443/417 T4-08-04 HR WHEEL BELT IS DAMAGED |  | FM008 |  | 2023-06-15 09:11 | 2023-06-15 10:11 | 2023-06-16 10:11 | 24 | 2023-06-15 09:20 | 2023-06-15 16:20 | 420 | 965 | 5 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-11887492 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AIR FLOW MISMATCH |  | FM008 |  | 2023-06-17 10:08 | 2023-06-17 11:08 | 2023-06-18 11:08 | 24 | 2023-06-17 10:15 | 2023-06-17 13:40 | 205 | 335 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 95216 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12126157 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED |  | FM008 |  | 2023-08-28 11:06 | 2023-08-28 12:06 | 2023-08-29 12:06 | 24 | 2023-08-28 11:10 | 2023-08-28 12:10 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11061428 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-08-04 |  | FM008 |  | 2022-09-26 19:11 | 2022-09-26 20:11 | 2022-09-27 20:11 | 24 | 2022-09-26 19:15 | 2022-09-26 21:35 | 140 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM9671 | Karunagoda Mudalige, Mr. Kasun Lakmal | N - - - |  | Voice Communication
| CM-2023-11888214 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY-AIR HANDLING UNIT 036 (TAG NO:AHU-A1110-423)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-06-17 13:38 | 2023-06-17 14:38 | 2023-06-18 14:38 | 24 | 2023-06-17 13:45 | 2023-06-17 15:15 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-11901870 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-423 – T4-21-03 |  | FM008 |  | 2023-06-22 07:16 | 2023-06-22 08:16 | 2023-06-23 08:16 | 24 | 2023-06-22 07:20 | 2023-06-22 09:00 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12570984 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-423 – T4-08-04 |  | FM008 |  | 2024-01-18 10:38 | 2024-01-18 11:38 | 2024-01-19 11:38 | 24 | 2024-01-18 10:45 | 2024-01-18 13:15 | 150 | 230 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2023-12492730 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T4-08-04 |  | FM008 |  | 2023-12-21 13:09 | 2023-12-21 14:09 | 2023-12-22 14:09 | 24 | 2023-12-21 13:15 | 2023-12-21 15:30 | 135 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12645311 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | T4-08-04-RELIEF BELT DAMAGED-AIR HANDLING UNIT 036 (TAG NO:AHU-A1110-423)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2024-02-15 00:09 | 2024-02-15 01:09 | 2024-02-16 01:09 | 24 | 2024-02-15 00:15 | 2024-02-15 02:05 | 110 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 95217 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2022-9958714 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-423 |  | FM008 |  | 2022-01-04 07:20 | 2022-01-04 08:20 | 2022-01-05 08:20 | 24 | 2022-01-04 07:30 | 2022-01-04 10:39 | 189 | 277 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10080698 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AHU-A1110-423-COOLING COIL DIRTY-T4-08-04 |  | FM008 |  | 2022-01-29 00:16 | 2022-01-29 01:16 | 2022-01-30 01:16 | 24 | 2022-01-29 00:25 | 2022-01-29 03:00 | 155 | 310 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10080699 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | RELIEF SIDE V BLET DAMAGED-AHU-A1110-423-T4-08-04 |  | FM008 |  | 2022-01-29 00:17 | 2022-01-29 01:17 | 2022-01-30 01:17 | 24 | 2022-01-29 00:25 | 2022-01-29 04:40 | 255 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 95217 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-11182114 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-11-12 19:18 | 2022-11-12 20:18 | 2022-11-13 20:18 | 24 | 2022-11-12 19:25 | 2022-11-12 21:15 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10145951 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | SUPPLY BELT LOOSE |  | FM008 |  | 2022-02-16 00:12 | 2022-02-16 01:12 | 2022-02-17 01:12 | 24 | 2022-02-16 00:20 | 2022-02-16 02:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10141353 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-15 19:06 | 2022-02-15 20:06 | 2022-02-16 20:06 | 24 | 2022-02-15 19:16 | 2022-02-15 21:16 | 120 | 240 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10366397 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AC TOO COLD LUGGAGE SCREENING AREA |  | FM008 |  | 2022-04-15 11:27 | 2022-04-15 12:27 | 2022-04-16 12:27 | 24 | 2022-04-15 11:35 | 2022-04-15 14:15 | 160 | 70 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | CT13569 | FELIX | N - - - |  | Voice Communication
| CM-2022-10593544 | ASD-MTB-FOF010-AHU036 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – T4-08-04 |  | FM008 |  | 2022-04-25 19:20 | 2022-04-25 20:20 | 2022-04-26 20:20 | 24 | 2022-04-25 19:29 | 2022-04-25 21:00 | 91 | 182 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10079808 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AHU-A1110-427 BELT IS DAMAGED |  | FM008 |  | 2022-01-27 09:42 | 2022-01-27 10:42 | 2022-01-28 10:42 | 24 | 2022-01-27 09:50 | 2022-01-27 11:15 | 85 | 145 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | BMS
| CM-2022-10082576 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE IMMIGRATION |  | FM008 |  | 2022-01-28 17:38 | 2022-01-28 18:38 | 2022-01-29 18:38 | 24 | 2022-01-28 17:48 | 2022-01-28 20:50 | 182 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 55709 |  |  | 89935 | Casumpang, Ms. Errah Joy Viesca | N - - - |  | E-mail
| CM-2022-10235539 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE IMMIGRATION COUNTERS - AC TOO HOT |  | FM008 |  | 2022-03-11 14:27 | 2022-03-11 14:57 | 2022-03-11 18:57 | 4 | 2022-03-11 14:37 | 2022-03-11 15:45 | 68 | 41 | 2 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 99309 | Abbasi, Ms. Maryam Rehman | N - - - |  | Voice Communication
| CM-2022-10255218 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE IMMIGRATION SCREENING AREA |  | FM008 |  | 2022-03-14 22:27 | 2022-03-14 23:27 | 2022-03-15 23:27 | 24 | 2022-03-14 22:37 | 2022-03-14 23:35 | 58 | 58 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17053 | 87807 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-10861917 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC IS TOO HOT -MOI AREA- DEPARTURE IMMIGRATION –NEAR INFO DESK AREA |  | FM008 |  | 2022-07-20 13:45 | 2022-07-20 14:45 | 2022-07-21 14:45 | 24 | 2022-07-20 13:55 | 2022-07-20 17:30 | 215 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 95217 |  |  | 89431 | Uswatte Liyanage, Ms. Niromie Patricia Shalika Perera | N - - - |  | Voice Communication
| CM-2022-11030722 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | NEAR T2-10-40, DEPARTURE SCREENING – AC TEMPERATURE IS TOO HOT |  | FM008 |  | 2022-09-16 20:42 | 2022-09-16 21:42 | 2022-09-17 21:42 | 24 | 2022-09-16 20:50 | 2022-09-16 21:45 | 55 | 30 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94954 | 87807 |  |  | CT15021 | VITALIS | N - - - |  | Voice Communication
| CM-2022-11040620 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | T2-10-41 - SCREENING AREA – AC TOO HOT |  | FM008 |  | 2022-09-21 06:19 | 2022-09-21 07:19 | 2022-09-22 07:19 | 24 | 2022-09-21 06:28 | 2022-09-21 10:30 | 242 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-11059278 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-10-03 |  | FM008 |  | 2022-09-26 00:52 | 2022-09-26 01:52 | 2022-09-27 01:52 | 24 | 2022-09-26 00:55 | 2022-09-26 02:15 | 80 | 240 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11062594 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING AREA - AC TOO HOT |  | FM008 |  | 2022-09-27 14:23 | 2022-09-27 14:53 | 2022-09-27 18:53 | 4 | 2022-09-27 14:32 | 2022-09-27 15:00 | 28 | 28 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 87807 |  |  | CT14294 | PETER | N - - - |  | Voice Communication
| CM-2022-11277430 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE E-GATE LINE 16 & 18 AREA |  | FM008 |  | 2022-12-18 06:42 | 2022-12-18 07:42 | 2022-12-19 07:42 | 24 | 2022-12-18 06:49 | 2022-12-18 07:40 | 51 | 51 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | CT14736 | WIRCKIES | N - - - |  | Voice Communication
| CM-2023-11340423 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD BEFORE EMMIGRATION DEPARTURES |  | FM008 |  | 2023-01-02 09:13 | 2023-01-02 10:13 | 2023-01-03 10:13 | 24 | 2023-01-02 09:20 | 2023-01-02 14:05 | 285 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | CT13569 | FELIX | N - - - |  | Voice Communication
| CM-2023-11390686 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING -DEPARTURE SCREENING AREA |  | FM008 |  | 2023-01-22 13:44 | 2023-01-22 14:45 | 2023-01-23 14:45 | 24 | 2023-01-22 13:54 | 2023-01-22 18:50 | 296 | 26 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 95217 |  |  | CT13569 | FELIX | N - - - |  | Voice Communication
| CM-2023-11465222 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT-T2-10-41 |  | FM008 |  | 2023-02-17 03:10 | 2023-02-17 04:10 | 2023-02-18 04:10 | 24 | 2023-02-17 03:15 | 2023-02-17 05:10 | 115 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95217 | 87807 |  |  | CT15021 | VITALIS | N - - - |  | Voice Communication
| CM-2023-11546805 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING AREA AFTER IMMIGRATION - AC TOO HOT |  | FM008 |  | 2023-03-10 00:50 | 2023-03-10 01:50 | 2023-03-11 01:50 | 24 | 2023-03-10 00:55 | 2023-03-10 04:25 | 210 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 87807 |  |  | 88985 | Cascayan, Mr. Jay-Ar | N - - - |  | Voice Communication
| CM-2023-11887094 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-08-04 |  | FM008 |  | 2023-06-17 18:58 | 2023-06-17 19:58 | 2023-06-18 19:58 | 24 | 2023-06-17 19:03 | 2023-06-17 20:03 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12040785 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT – DEP,MOI SCREENING AREA NEAR T2-11-27 |  | FM008 |  | 2023-08-02 00:47 | 2023-08-02 01:47 | 2023-08-03 01:47 | 24 | 2023-08-02 00:50 | 2023-08-02 05:15 | 265 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | CT15999 | DEVILAL | N - - - |  | Voice Communication
| CM-2023-12064074 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE IMMIGRATION AREA |  | FM008 |  | 2023-08-09 00:09 | 2023-08-09 01:09 | 2023-08-10 01:09 | 24 | 2023-08-09 00:15 | 2023-08-09 01:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17053 | 87807 |  |  | 52856 | Oliveros, Mr. Jovito Jr. Panganiban | N - - - |  | Voice Communication
| CM-2023-12066019 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT, DEPARTURE SCREENING AREA,NEAR T2-10-41 |  | FM008 |  | 2023-08-11 23:48 | 2023-08-12 00:48 | 2023-08-13 00:48 | 24 | 2023-08-11 23:54 | 2023-08-12 01:05 | 71 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2023-12089653 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE IMMIGRATION AREA -AC TOO HOT |  | FM008 |  | 2023-08-14 21:18 | 2023-08-14 22:18 | 2023-08-15 22:18 | 24 | 2023-08-14 21:25 | 2023-08-14 22:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 82878 | Mbuyazi, Ms. Mbali Emelda | N - - - |  | Voice Communication
| CM-2023-12103213 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE EMIGRATION COUNTERS AREA |  | FM008 |  | 2023-08-21 10:53 | 2023-08-21 11:53 | 2023-08-22 11:53 | 24 | 2023-08-21 11:00 | 2023-08-21 12:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | MOI | ABSHAR | N - - - |  | Voice Communication
| CM-2023-12115076 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE IMMIGRATION A/C IS NOT WORKING |  | FM008 |  | 2023-08-25 14:10 | 2023-08-25 15:10 | 2023-08-26 15:10 | 24 | 2023-08-25 14:16 | 2023-08-25 18:10 | 234 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | T24866 | Akasbi, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2024-12537426 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - ROOM # T2-10-13 |  | FM008 |  | 2024-01-06 06:50 | 2024-01-06 07:50 | 2024-01-07 07:50 | 24 | 2024-01-06 07:00 | 2024-01-06 12:20 | 320 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 95217 |  |  | MOI | KHALIFA | N - - - |  | Voice Communication
| CM-2024-12570245 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE IMMIGRATION COUNTER 12 |  | FM008 |  | 2024-01-15 15:14 | 2024-01-15 16:14 | 2024-01-16 16:14 | 24 | 2024-01-15 15:20 | 2024-01-15 18:10 | 170 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 95217 |  |  | MOI | ROBAH | N - - - |  | Voice Communication
| CM-2024-12745299 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT T2-10-41 |  | FM008 |  | 2024-03-19 00:42 | 2024-03-19 01:42 | 2024-03-20 01:42 | 24 | 2024-03-19 00:50 | 2024-03-19 05:40 | 290 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 95217 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2024-12819836 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING NEAR T2-10-41 |  | FM008 |  | 2024-04-09 22:17 | 2024-04-09 23:17 | 2024-04-10 23:17 | 24 | 2024-04-09 22:25 | 2024-04-10 01:02 | 157 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2024-12823530 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TEMP VERY WARM-DEP SCREENING AREA-MTB |  | FM008 |  | 2024-04-13 19:09 | 2024-04-13 20:09 | 2024-04-14 20:09 | 24 | 2024-04-13 19:15 | 2024-04-14 00:20 | 305 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 77406 | 87807 |  |  | CT16428 | FRED | N - - - |  | Voice Communication
| CM-2024-12847595 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - NEAR T2-10-41 |  | FM008 |  | 2024-04-25 01:50 | 2024-04-25 02:50 | 2024-04-26 02:50 | 24 | 2024-04-25 01:55 | 2024-04-25 09:05 | 430 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2022-10910201 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT EMMIGRATION AREA COUNTER #20 DEPARTURE |  | FM008 |  | 2022-08-05 18:34 | 2022-08-05 19:34 | 2022-08-06 19:34 | 24 | 2022-08-05 18:40 | 2022-08-05 20:35 | 115 | 56 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 55709 |  |  | MOI | AAHIYA | N - - - |  | Voice Communication
| CM-2022-10934780 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE SCREENING |  | FM008 |  | 2022-08-13 21:45 | 2022-08-13 22:15 | 2022-08-14 02:15 | 4 | 2022-08-13 21:50 | 2022-08-13 23:00 | 70 | 45 | 2 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-11160040 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT IS NOT WORKING |  | FM008 |  | 2022-11-06 02:05 | 2022-11-06 03:05 | 2022-11-07 03:05 | 24 | 2022-11-06 02:10 | 2022-11-06 03:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 68060 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11208307 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD- DEPARTURE SCREENING AREA |  | FM008 |  | 2022-11-21 13:00 | 2022-11-21 14:00 | 2022-11-22 14:00 | 24 | 2022-11-21 13:08 | 2022-11-21 14:00 | 52 | 52 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 87807 |  |  | CT14114 | SPENCER | N - - - |  | Voice Communication
| CM-2022-11219853 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING -DEPARTURE SCREENING AREA |  | FM008 |  | 2022-11-27 12:54 | 2022-11-27 13:54 | 2022-11-28 13:54 | 24 | 2022-11-27 13:00 | 2022-11-27 13:48 | 48 | 48 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | MOI | KHALID | N - - - |  | Voice Communication
| CM-2022-11249754 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC IS NOT FUNCTIONNG IN DEPARTRE EMIGRATION E GATE AREA- - |  | FM008 |  | 2022-12-06 06:43 | 2022-12-06 07:43 | 2022-12-07 07:43 | 24 | 2022-12-06 06:50 | 2022-12-06 07:35 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94953 | 17053 |  |  | CT14706 | WILKIS | N - - - |  | Voice Communication
| CM-2022-11273427 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE EMMIGRATION AREA |  | FM008 |  | 2022-12-16 12:24 | 2022-12-16 13:24 | 2022-12-17 13:24 | 24 | 2022-12-16 12:30 | 2022-12-16 16:00 | 210 | 51 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 17053 |  |  | 85933 | Navoa, Ms. Keith Alexandra Chan | N - - - |  | Voice Communication
| CM-2023-11403516 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE IMMIGRATION AREA (CAPTAIN OFFICE) |  | FM008 |  | 2023-01-26 16:24 | 2023-01-26 17:24 | 2023-01-27 17:24 | 24 | 2023-01-26 16:30 | 2023-01-26 18:45 | 135 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 17053 |  |  | 112253 | Shahida, Mrs. Sajna | N - - - |  | Voice Communication
| CM-2023-11398600 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC IS TOO HOT-DEPARTURE SCREENING AREA-NEAR T2-10-41 (SEARCH ROOM))-AIRSIDE-MAIN TERMINAL BUILDING-SECOND FLOOR AREA 010 |  | FM008 |  | 2023-01-24 14:59 | 2023-01-24 15:59 | 2023-01-25 15:59 | 24 | 2023-01-24 15:05 | 2023-01-24 18:30 | 205 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 87807 |  |  | CT13569 | FELIX | N - - - |  | Voice Communication
| CM-2023-11587140 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER DIRTY - (AHU-A1110-427)- MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-03-23 00:22 | 2023-03-23 01:22 | 2023-03-24 01:22 | 24 | 2023-03-23 00:30 | 2023-03-23 02:15 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11651661 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TEMPERATURE TOO WARM-DEPARTURE SCREENING AREA ,-NEAR T2-10-41 |  | FM008 |  | 2023-04-11 23:51 | 2023-04-12 00:51 | 2023-04-13 00:51 | 24 | 2023-04-11 23:55 | 2023-04-12 00:32 | 37 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 77406 | 87807 |  |  | CT13735 | LAWRENCE | N - - - |  | Voice Communication
| CM-2023-11825046 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-08-04 |  | FM008 |  | 2023-05-28 06:56 | 2023-05-28 07:56 | 2023-05-29 07:56 | 24 | 2023-05-28 07:02 | 2023-05-28 09:02 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12014754 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AQ SENSOR DISCONNECTED - AHU-A1110-427 – T4-10-03 |  | FM008 |  | 2023-07-27 17:22 | 2023-07-27 18:22 | 2023-07-28 18:22 | 24 | 2023-07-27 17:27 | 2023-07-27 18:40 | 73 | 75 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 106973 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12056966 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT -DEPARTURE SCREENING AREA |  | FM008 |  | 2023-08-06 21:23 | 2023-08-06 22:23 | 2023-08-07 22:23 | 24 | 2023-08-06 21:30 | 2023-08-06 23:59 | 149 | 64 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | CT16000 | LOKENDRA | N - - - |  | Voice Communication
| CM-2023-12058840 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | T2-10-20 AC NOT WORKING |  | FM008 |  | 2023-08-08 02:41 | 2023-08-08 03:41 | 2023-08-09 03:41 | 24 | 2023-08-08 02:50 | 2023-08-08 06:00 | 190 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 89127 | 87807 |  |  | 51640 | Wanjiru, Ms. Anne Wairimu | N - - - |  | Voice Communication
| CM-2023-12067071 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURES AFTER MOI IMMIGRATION |  | FM008 |  | 2023-08-12 16:56 | 2023-08-12 17:56 | 2023-08-13 17:56 | 24 | 2023-08-12 17:05 | 2023-08-12 18:35 | 90 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | R15623 | Fatfat, Mr. Mhammad | N - - - |  | Voice Communication
| CM-2023-12075386 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE EMIGRATION COUNTERS |  | FM008 |  | 2023-08-13 10:49 | 2023-08-13 11:49 | 2023-08-14 11:49 | 24 | 2023-08-13 10:55 | 2023-08-13 15:10 | 255 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 121959 | 87807 |  |  | MOI | AISHA | N - - - |  | Voice Communication
| CM-2023-12085302 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEP MOI CHECK POINT & SCREENING AREA - AC TOO HOT |  | FM008 |  | 2023-08-15 11:27 | 2023-08-15 12:27 | 2023-08-16 12:27 | 24 | 2023-08-15 11:35 | 2023-08-15 18:30 | 415 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | MOI | AFSHAR | N - - - |  | Voice Communication
| CM-2023-12106255 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT IN -DEPARTURE IMMIGRATION AREA/ |  | FM008 |  | 2023-08-20 17:07 | 2023-08-20 18:07 | 2023-08-21 18:07 | 24 | 2023-08-20 17:15 | 2023-08-20 20:00 | 165 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 89629 | Hassan, Ms. Hind Zuhair Mohamed | N - - - |  | Voice Communication
| CM-2023-12198691 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE SCREENING |  | FM008 |  | 2023-09-17 21:52 | 2023-09-17 22:52 | 2023-09-18 22:52 | 24 | 2023-09-17 21:55 | 2023-09-17 23:05 | 70 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | CT16501 | ANTONY | N - - - |  | Voice Communication
| CM-2024-12558858 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD – T2-10-13 |  | FM008 |  | 2024-01-14 06:59 | 2024-01-14 07:59 | 2024-01-15 07:59 | 24 | 2024-01-14 07:05 | 2024-01-14 07:40 | 35 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 133396 | 95217 |  |  | MOI | KHALEEFA | N - - - |  | Voice Communication
| CM-2024-12574660 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT IN DEPARTURE SCREENING AREA – T2-10-41 |  | FM008 |  | 2024-01-17 18:04 | 2024-01-17 19:04 | 2024-01-18 19:04 | 24 | 2024-01-17 18:10 | 2024-01-17 23:45 | 335 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2024-12736003 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT PREMIUM CHECK-IN ROW NO 1 |  | FM008 |  | 2024-03-17 13:29 | 2024-03-17 14:29 | 2024-03-18 14:29 | 24 | 2024-03-17 13:35 | 2024-03-17 23:00 | 565 | 56 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 68350 | Elghazouani, Ms. Fatima Ezzahraa | N - - - |  | Voice Communication
| CM-2022-11008618 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-09-10 00:14 | 2022-09-10 01:14 | 2022-09-11 01:14 | 24 | 2022-09-10 00:20 | 2022-09-10 02:30 | 130 | 305 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11079644 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE SCREENING AREA |  | FM008 |  | 2022-10-08 07:15 | 2022-10-08 08:15 | 2022-10-09 08:15 | 24 | 2022-10-08 07:25 | 2022-10-08 08:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 76858 |  |  | CT14262 | KELVIN | N - - - |  | Voice Communication
| CM-2022-11208951 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE IMMIGRATION INFO DESK AC TOO COLD |  | FM008 |  | 2022-11-22 06:50 | 2022-11-22 07:50 | 2022-11-23 07:50 | 24 | 2022-11-22 07:00 | 2022-11-22 07:30 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | T25111 | Khattabi, Miss Imane | N - - - |  | Voice Communication
| CM-2022-11255884 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE INFORMATION COUNTER BEFOR IMMIGRATION |  | FM008 |  | 2022-12-10 08:03 | 2022-12-10 09:03 | 2022-12-11 09:03 | 24 | 2022-12-10 08:13 | 2022-12-10 13:00 | 287 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 51682 | Marquez, Ms. Carolyn Estil | N - - - |  | Voice Communication
| CM-2023-11439504 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO WARM - T2-10-27 |  | FM008 |  | 2023-02-06 22:17 | 2023-02-06 23:17 | 2023-02-07 23:17 | 24 | 2023-02-06 22:25 | 2023-02-06 23:30 | 65 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  |  | MOHAMED | N - - - |  | Voice Communication
| CM-2023-11530850 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING -DEPARTURE SCREENING AREA |  | FM008 |  | 2023-03-10 07:21 | 2023-03-10 08:21 | 2023-03-11 08:21 | 24 | 2023-03-10 07:30 | 2023-03-10 18:40 | 670 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 87807 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2023-11879187 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES IMMIGRATION AREA– |  | FM008 |  | 2023-06-12 00:46 | 2023-06-12 01:46 | 2023-06-13 01:46 | 24 | 2023-06-12 00:50 | 2023-06-12 03:00 | 130 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | CT14263 | RODGERS | N - - - |  | Voice Communication
| CM-2023-11969498 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | A/C IS TOO HOT AT IMMIGRATION DEPARTURE |  | FM008 |  | 2023-07-11 22:41 | 2023-07-11 23:41 | 2023-07-12 23:41 | 24 | 2023-07-11 22:45 | 2023-07-12 01:02 | 137 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 99309 | Abbasi, Ms. Maryam Rehman | N - - - |  | Voice Communication
| CM-2023-11995094 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-427 – T4-08-04 |  | FM008 |  | 2023-07-19 00:20 | 2023-07-19 01:20 | 2023-07-20 01:20 | 24 | 2023-07-19 00:26 | 2023-07-19 02:26 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12103395 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO WARM |  | FM008 |  | 2023-08-21 23:31 | 2023-08-22 00:31 | 2023-08-23 00:31 | 24 | 2023-08-21 23:40 | 2023-08-22 00:15 | 35 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | T24819 | Tamang, Mr. Samuel | N - - - |  | Voice Communication
| CM-2023-12111093 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD – MOI DEP SCREENING, BUSINESS CLASS AREA |  | FM008 |  | 2023-08-24 08:17 | 2023-08-24 09:17 | 2023-08-25 09:17 | 24 | 2023-08-24 08:25 | 2023-08-24 10:40 | 135 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2023-12133826 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TEMP VERY WARM-DEPT-SCREENING(T2-11-34B) AREA |  | FM008 |  | 2023-08-29 16:22 | 2023-08-29 17:22 | 2023-08-30 17:22 | 24 | 2023-08-29 16:30 | 2023-08-29 18:40 | 130 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 77406 | 17053 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2024-12570062 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | ARRIVAL MOI SCREENING AREA (PAST IMMIGRTAION ) - AC TOO COLD |  | FM008 |  | 2024-01-17 02:31 | 2024-01-17 03:31 | 2024-01-18 03:31 | 24 | 2024-01-17 02:40 | 2024-01-17 05:20 | 160 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | FM11261 | Ssessanga, Mr. Isaac | N - - - |  | Voice Communication
| CM-2024-12536609 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING NEAR TO T2-10-41 AC TOO HOT |  | FM008 |  | 2024-01-05 17:10 | 2024-01-05 18:10 | 2024-01-06 18:10 | 24 | 2024-01-05 17:15 | 2024-01-05 21:05 | 230 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2024-12673058 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE EMMIGRATION MOI COUNTER AREA AC TOO HOT |  | FM008 |  | 2024-02-24 18:20 | 2024-02-24 19:20 | 2024-02-25 19:20 | 24 | 2024-02-24 18:25 | 2024-02-24 23:59 | 334 | 32 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 53351 | Elouazzani, Ms. Halima | N - - - |  | Voice Communication
| CM-2024-12725901 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE IMMIGRATION COUNTERS AC TOO HOT |  | FM008 |  | 2024-03-10 22:28 | 2024-03-10 23:28 | 2024-03-11 23:28 | 24 | 2024-03-10 22:35 | 2024-03-10 23:35 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | 91583 | Castor, Ms. Leann Joy Dela Pena | N - - - |  | Voice Communication
| CM-2024-12826338 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) DEPARTURE SCREENING AREA NEAR T2-10-41 |  | FM008 |  | 2024-04-15 21:42 | 2024-04-15 22:42 | 2024-04-16 22:42 | 24 | 2024-04-15 21:50 | 2024-04-16 02:35 | 285 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2024-12858257 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - T2-10-41 BREAK ROOM |  | FM008 |  | 2024-04-28 21:13 | 2024-04-28 22:13 | 2024-04-29 22:13 | 24 | 2024-04-28 21:20 | 2024-04-28 23:58 | 158 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 87807 |  |  | CT16373 | ERIC | N - - - |  | Voice Communication
| CM-2024-12683739 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO WARM - IMMIGRATION AREA |  | FM008 |  | 2024-02-27 16:18 | 2024-02-27 17:18 | 2024-02-28 17:18 | 24 | 2024-02-27 16:25 | 2024-02-27 17:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 60639 | Lim, Mr. Ralph Ivan Espiritu | N - - - |  | Voice Communication
| CM-2024-12699957 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO WARM - NEAR PASSENGER SCREENING AREA |  | FM008 |  | 2024-03-04 22:01 | 2024-03-04 23:01 | 2024-03-05 23:01 | 24 | 2024-03-04 22:10 | 2024-03-05 00:30 | 140 | 145 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2024-12794533 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | ROW 7 COUNTER 10 AC TOO HOT |  | FM008 |  | 2024-04-03 18:26 | 2024-04-03 19:26 | 2024-04-04 19:26 | 24 | 2024-04-03 18:31 | 2024-04-03 23:58 | 327 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | 126526 | Paramel Wilfred, Mr. Joe Alfred | N - - - |  | E-mail
| CM-2024-12819323 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT, SECURITY CHECK IN AREA DEPARTURE IMMIGRATION |  | FM008 |  | 2024-04-07 20:17 | 2024-04-07 21:17 | 2024-04-08 21:17 | 24 | 2024-04-07 20:24 | 2024-04-08 02:05 | 341 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2022-9958715 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER DIRTY :AHU-A1110-427 |  | FM008 |  | 2022-01-04 07:22 | 2022-01-04 08:22 | 2022-01-05 08:22 | 24 | 2022-01-04 07:30 | 2022-01-04 09:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10045350 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT SECURITY CHECK POINT NEAR T2-10- 40 |  | FM008 |  | 2022-01-12 22:31 | 2022-01-12 23:31 | 2022-01-13 23:31 | 24 | 2022-01-12 22:40 | 2022-01-13 00:50 | 130 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 55709 |  |  | MOI | AAHIYA | N - - - |  | Voice Communication
| CM-2022-10048368 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE EMIGRATION COUNTER 11 TO 14 - AC IS TOO HOT |  | FM008 |  | 2022-01-13 07:07 | 2022-01-13 08:07 | 2022-01-14 08:07 | 24 | 2022-01-13 07:15 | 2022-01-13 09:10 | 115 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94953 | 55709 |  |  | 91582 | Paguirigan, Ms. Justine Yap | N - - - |  | Voice Communication
| CM-2022-10109825 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE IMMIGRATION |  | FM008 |  | 2022-02-05 13:56 | 2022-02-05 14:56 | 2022-02-06 14:56 | 24 | 2022-02-05 14:00 | 2022-02-05 15:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 55709 |  |  | 16884 | Gamare, Mr. Vikas Shankar | N - - - |  | Voice Communication
| CM-2022-10344020 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE IMMIGRATION NEAR T2-10-35A |  | FM008 |  | 2022-04-10 09:34 | 2022-04-10 10:34 | 2022-04-11 10:34 | 24 | 2022-04-10 09:40 | 2022-04-10 10:38 | 58 | 58 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 17053 |  |  | CT13551 | Oroko Reuben | N - - - |  | Voice Communication
| CM-2022-10032356 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TEMPERATURE IS TOO COLD – MTB, LEVEL 2, BEFORE IMMIGRATION, HIA INFORMATION COUNTER |  | FM008 |  | 2022-01-08 09:46 | 2022-01-08 10:46 | 2022-01-09 10:46 | 24 | 2022-01-08 09:55 | 2022-01-08 10:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94954 | 55709 |  |  | 91583 | Castor, Ms. Leann Joy Dela Pena | N - - - |  | Voice Communication
| CM-2022-10059913 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING AREA PAST IMMIGRATION - AC TOO HOT |  | FM008 |  | 2022-01-20 00:19 | 2022-01-20 01:19 | 2022-01-21 01:19 | 24 | 2022-01-20 00:25 | 2022-01-20 00:55 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 55709 |  |  | CT13537 | GITONGA | N - - - |  | Voice Communication
| CM-2022-10084465 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AHU COIL DIRTY |  | FM008 |  | 2022-01-28 09:16 | 2022-01-28 10:16 | 2022-01-29 10:16 | 24 | 2022-01-28 09:25 | 2022-01-28 14:30 | 305 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10142120 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AHU-A1110-427-SUPPLY BELT LOOSE |  | FM008 |  | 2022-02-14 04:07 | 2022-02-14 05:07 | 2022-02-15 05:07 | 24 | 2022-02-14 04:15 | 2022-02-14 05:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95217 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10276151 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT -DEPARTURE SCREENING AREA |  | FM008 |  | 2022-03-24 17:22 | 2022-03-24 18:22 | 2022-03-25 18:22 | 24 | 2022-03-24 17:30 | 2022-03-24 18:45 | 75 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 55709 |  |  | 17713 | Rebanal, Mr. Emmanuel Regorgo | N - - - |  | Voice Communication
| CM-2022-10350241 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | ACC TOO COLD –AT DEPARTURE IMIGRATIONS COUNTERS -AIRSIDE-MAIN TERMINAL BUILDING-SECOND FLOOR AREA 010 |  | FM008 |  | 2022-04-10 15:37 | 2022-04-10 16:37 | 2022-04-11 16:37 | 24 | 2022-04-10 15:45 | 2022-04-10 17:30 | 105 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 118650 | Sobirov, Mr. Durbek | N - - - |  | Voice Communication
| CM-2022-10696463 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-427 – T4-10-03 |  | FM008 |  | 2022-05-26 19:09 | 2022-05-26 20:09 | 2022-05-27 20:09 | 24 | 2022-05-26 19:15 | 2022-05-26 21:10 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10694013 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD - DEP IMMIGRATION ALL AREA - NEAR T2-12-17 |  | FM008 |  | 2022-05-29 01:26 | 2022-05-29 02:26 | 2022-05-30 02:26 | 24 | 2022-05-29 01:36 | 2022-05-29 05:00 | 204 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 55709 |  |  | 94544 | Stamenkovic, Ms. Miljana | N - - - |  | Voice Communication
| CM-2022-10752751 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AIR HANDLING UNIT 040 (TAG NO:AHU-A1110-427)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-06-17 19:21 | 2022-06-17 20:21 | 2022-06-18 20:21 | 24 | 2022-06-17 19:25 | 2022-06-17 20:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10912299 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) - DEPARTURE SCREENING AREA AFETR IMMIGRATION. |  | FM008 |  | 2022-08-06 23:54 | 2022-08-07 00:54 | 2022-08-08 00:54 | 24 | 2022-08-07 | 2022-08-07 00:35 | 35 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 55709 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-10950164 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING -DEPARTURE SCREENING AREA |  | FM008 |  | 2022-08-16 22:26 | 2022-08-16 23:26 | 2022-08-17 23:26 | 24 | 2022-08-16 22:30 | 2022-08-16 23:55 | 85 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 55709 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-11062636 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING AC TOO HOT NEAR T2-10-41 |  | FM008 |  | 2022-09-27 22:59 | 2022-09-27 23:59 | 2022-09-28 23:59 | 24 | 2022-09-27 23:05 | 2022-09-28 00:30 | 85 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 87807 | 87807 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-11103521 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE IMMIGRATION COUNTER AREA |  | FM008 |  | 2022-10-15 08:00 | 2022-10-15 09:00 | 2022-10-16 09:00 | 24 | 2022-10-15 08:05 | 2022-10-15 09:38 | 93 | 63 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | CT14263 | RODGERS | N - - - |  | Voice Communication
| CM-2022-11177174 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE IMMIGRATION BAGS SCREENING AREA |  | FM008 |  | 2022-11-08 23:45 | 2022-11-09 00:45 | 2022-11-10 00:45 | 24 | 2022-11-08 23:55 | 2022-11-09 01:00 | 65 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | CT15021 | VITALIS | N - - - |  | Voice Communication
| CM-2022-11199221 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE IMMIGRATION COUNTER AREA |  | FM008 |  | 2022-11-18 23:18 | 2022-11-19 00:18 | 2022-11-20 00:18 | 24 | 2022-11-18 23:25 | 2022-11-19 01:05 | 100 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 87807 |  |  | MOI | ALI | N - - - |  | Voice Communication
| CM-2022-10079813 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-01-27 09:45 | 2022-01-27 10:45 | 2022-01-28 10:45 | 24 | 2022-01-27 09:53 | 2022-01-27 18:00 | 487 | 207 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | BMS
| CM-2022-10142242 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -T4-10-03 |  | FM008 |  | 2022-02-14 19:07 | 2022-02-14 20:07 | 2022-02-15 20:07 | 24 | 2022-02-14 19:10 | 2022-02-14 23:00 | 230 | 225 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10237588 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | CHECK IN ROW 8 COUNTER 5 – AREA TOO HOT/AC NOT COOLING |  | FM008 |  | 2022-03-12 11:24 | 2022-03-12 12:24 | 2022-03-13 12:24 | 24 | 2022-03-12 11:34 | 2022-03-12 13:55 | 141 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106976 | 17053 |  |  | 67571 | Kalb-E-Haider, Mr. Syed | N - - - |  | Voice Communication
| CM-2022-10321994 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – T4-10-03 |  | FM008 |  | 2022-04-07 07:13 | 2022-04-07 08:13 | 2022-04-08 08:13 | 24 | 2022-04-07 07:20 | 2022-04-07 17:20 | 600 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 105233 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2022-10365603 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | ALL AREA AC TOO HOT T2-10-42 |  | FM008 |  | 2022-04-15 21:50 | 2022-04-15 22:50 | 2022-04-16 22:50 | 24 | 2022-04-15 22:00 | 2022-04-16 00:10 | 130 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 17053 |  |  |  | MUSA MUHAMMED | N - - - |  | Voice Communication
| CM-2022-10368548 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-427 - MECHANICAL ROOM T4-10-03 |  | FM008 |  | 2022-04-16 14:52 | 2022-04-16 15:52 | 2022-04-17 15:52 | 24 | 2022-04-16 15:00 | 2022-04-16 18:45 | 225 | 230 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10598313 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING DEPARTURE SCREENING AREA |  | FM008 |  | 2022-04-27 22:42 | 2022-04-27 23:42 | 2022-04-28 23:42 | 24 | 2022-04-27 22:50 | 2022-04-27 23:45 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | CT13537 | GITONGA | N - - - |  | Voice Communication
| CM-2022-10611753 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | DEPARTURE EMMIGRATION AREA AC IS TOO HOT |  | FM008 |  | 2022-05-01 21:57 | 2022-05-01 22:57 | 2022-05-02 22:57 | 24 | 2022-05-01 22:07 | 2022-05-01 23:55 | 108 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94953 | 17053 |  |  | CT13537 | GITONGA | N - - - |  | Voice Communication
| CM-2022-10772148 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER DIRTY T4-08-04 |  | FM008 |  | 2022-06-22 07:30 | 2022-06-22 08:30 | 2022-06-23 08:30 | 24 | 2022-06-22 07:35 | 2022-06-22 09:00 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM7396 | Chowdhury, Mr. Biswajit | N - - - |  | Voice Communication
| CM-2022-10909563 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE SCREENING AREA T2-10-41 |  | FM008 |  | 2022-08-01 22:22 | 2022-08-01 23:22 | 2022-08-02 23:22 | 24 | 2022-08-01 22:27 | 2022-08-01 23:59 | 92 | 39 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 76858 |  |  | CT13572 | PHILEMON | N - - - |  | Voice Communication
| CM-2023-11398458 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2023-01-24 00:35 | 2023-01-24 01:35 | 2023-01-25 01:35 | 24 | 2023-01-24 00:40 | 2023-01-24 02:00 | 80 | 240 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12281005 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AC NOT WORKING -DEPARTURE SCREENING AREA |  | FM008 |  | 2023-10-13 17:02 | 2023-10-13 18:02 | 2023-10-14 18:02 | 24 | 2023-10-13 17:10 | 2023-10-13 18:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 17333 | 87807 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2023-12281438 | ASD-MTB-FOF010-AHU040 | AIR HANDLING UNIT-05 | AHU-A1110-427-LIGHTING SWITCH NOT WORKING-T4-01-03 |  | FM008 |  | 2023-10-14 21:54 | 2023-10-14 22:54 | 2023-10-15 22:54 | 24 | 2023-10-14 22:00 | 2023-10-14 23:59 | 119 | 223 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95217 | 87807 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2022-10193318 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ROW 8 COUNTER 10 AC TOO HOT - T2-12-01 (CHECK IN HALL) - CM-2022-01-1347 |  | FM008 |  | 2022-02-27 02:45 | 2022-02-27 03:45 | 2022-02-28 03:45 | 24 | 2022-02-27 02:55 | 2022-02-27 06:45 | 230 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 55709 |  |  | 112233 | Ranasinghe Arachchige, Mr. Rahul Sachin Ranasinghe | N - - - |  | Voice Communication
| CM-2022-10214369 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE CHECK IN ROW # 6 AREA |  | FM008 |  | 2022-03-04 12:38 | 2022-03-04 13:38 | 2022-03-05 13:38 | 24 | 2022-03-04 12:45 | 2022-03-04 13:35 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 17053 |  |  | 88557 | Allang, Ms. Endra Freehana | N - - - |  | Voice Communication
| CM-2022-10305794 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD T2-12-10 |  | FM008 |  | 2022-03-28 22:16 | 2022-03-28 23:16 | 2022-03-29 23:16 | 24 | 2022-03-28 22:25 | 2022-03-28 23:50 | 85 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 85125 | 55709 |  |  | 27172 | Rajan, Mr. Ranjithbabu | N - - - |  | Voice Communication
| CM-2022-10312425 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC VENT PAINT FADED T2-12-17 |  | FM008 |  | 2022-04-03 07:41 | 2022-04-03 08:41 | 2022-04-04 08:41 | 24 | 2022-04-03 07:50 | 2022-04-03 13:00 | 310 | 75 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 85125 | 17053 |  |  | FM7797 | Adalla, Mr. Alex Otieno | N - - - |  | Voice Communication
| CM-2022-10567772 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD IN DEPARTURE AREA - NEAR CHECK-IN ROW 7&8 |  | FM008 |  | 2022-04-21 03:29 | 2022-04-21 04:29 | 2022-04-22 04:29 | 24 | 2022-04-21 03:39 | 2022-04-21 04:39 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 17241 | Azadi, Ms. Ayeshe Mirak | N - - - |  | Voice Communication
| CM-2022-10821726 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE IMMIGRATION COUNTER AREA |  | FM008 |  | 2022-07-06 16:36 | 2022-07-06 17:36 | 2022-07-07 17:36 | 24 | 2022-07-06 16:45 | 2022-07-06 17:50 | 65 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 95217 |  |  | MOI | ALI | N - - - |  | Voice Communication
| CM-2022-11138500 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD – T2-12-10 |  | FM008 |  | 2022-10-29 05:36 | 2022-10-29 06:36 | 2022-10-30 06:36 | 24 | 2022-10-29 05:45 | 2022-10-29 06:30 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 17053 |  |  | 27172 | Rajan, Mr. Ranjithbabu | N - - - |  | Voice Communication
| CM-2023-11499953 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU-A1110-429 – FILTER ALARM |  | FM008 |  | 2023-02-28 00:26 | 2023-02-28 01:26 | 2023-03-01 01:26 | 24 | 2023-02-28 00:35 | 2023-02-28 02:00 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 94954 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11699183 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | MT-2007 LE PETIT CAMION THE AC IN FRONT OF THE SHOP IS TOO COLD |  | FM008 |  | 2023-04-26 18:30 | 2023-04-26 19:30 | 2023-04-27 19:30 | 24 | 2023-04-26 18:36 | 2023-04-26 23:10 | 274 | 67 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | 132071 | Nabbuto, Ms. Josephine | N - - - |  | Voice Communication
| CM-2023-11801636 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - INFO DESK NEAR ROW 7 DEPARTURE HALL |  | FM008 |  | 2023-05-17 15:53 | 2023-05-17 16:53 | 2023-05-18 16:53 | 24 | 2023-05-17 16:00 | 2023-05-17 17:40 | 100 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 73265 | Paudel, Mr. Jeevan | N - - - |  | Voice Communication
| CM-2023-11898932 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD INFRONT OF ROW 7 INFORMATION DESK CHECK IN AREA DEPARTURE |  | FM008 |  | 2023-06-21 01:24 | 2023-06-21 02:24 | 2023-06-22 02:24 | 24 | 2023-06-21 01:30 | 2023-06-21 06:20 | 290 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106972 | 133396 |  |  | 91640 | Sevilla, Ms. Sharleen Gealone | N - - - |  | Voice Communication
| CM-2023-12066898 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT, CHECK IN ROW- 5& 6 SEATING AREA , DEPARTURE HALL |  | FM008 |  | 2023-08-11 21:56 | 2023-08-11 22:56 | 2023-08-12 22:56 | 24 | 2023-08-11 22:06 | 2023-08-11 23:06 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | 17216 | Tolkar, Mr. Kabir Abdul Sattar | N - - - |  | Voice Communication
| CM-2023-12114230 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | WEEE BELT DAMAGED & FILETR DIRTY -- AHU-A1110-429 - MECHANICAL ROOM T4-10-03 |  | FM008 |  | 2023-08-26 00:26 | 2023-08-26 01:26 | 2023-08-27 01:26 | 24 | 2023-08-26 00:35 | 2023-08-26 03:30 | 175 | 525 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12116527 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-429 – T4-10-03 |  | FM008 |  | 2023-08-25 19:31 | 2023-08-25 20:31 | 2023-08-26 20:31 | 24 | 2023-08-25 19:40 | 2023-08-25 23:40 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | BMS
| CM-2023-12127798 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE HALL IN BETWEEN ROW -4 &5 NEAR T2-12-26 |  | FM008 |  | 2023-08-28 17:44 | 2023-08-28 18:44 | 2023-08-29 18:44 | 24 | 2023-08-28 17:50 | 2023-08-28 22:40 | 290 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 124475 | 17053 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2023-12152062 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | BLOWER PAINT FADED |  | FM008 |  | 2023-09-05 07:37 | 2023-09-05 08:37 | 2023-09-06 08:37 | 24 | 2023-09-05 07:45 | 2023-09-05 11:45 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12217802 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT - CHECK IN ROW 6, 7 & 8 - CM-2023-01-1557 |  | FM008 |  | 2023-09-24 22:03 | 2023-09-24 23:03 | 2023-09-25 23:03 | 24 | 2023-09-24 22:10 | 2023-09-24 23:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17053 | 87807 |  |  | T24883 | Mohammed | - - -
| CM-2023-12390521 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECKIN ROW 5 ALL THE COUNTERS |  | FM008 |  | 2023-11-20 02:54 | 2023-11-20 03:54 | 2023-11-21 03:54 | 24 | 2023-11-20 03:00 | 2023-11-20 07:30 | 270 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 108142 | Moussaoui, Ms. Rafika | N - - - |  | Voice Communication
| CM-2023-12452089 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD ROW 7 COUNTER 1 |  | FM008 |  | 2023-12-06 22:10 | 2023-12-06 23:10 | 2023-12-07 23:10 | 24 | 2023-12-06 22:15 | 2023-12-07 00:30 | 135 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | R10331 | Naserian, Ms. Linda | N - - - |  | Voice Communication
| CM-2023-12448884 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOISY IN DEPARTURE IMMIGRATION AREA NEAR T2-11-17 |  | FM008 |  | 2023-12-09 11:50 | 2023-12-09 12:50 | 2023-12-10 12:50 | 24 | 2023-12-09 12:00 | 2023-12-09 18:50 | 410 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 17053 |  |  | 125847 | Saha, Mr. Somnath | N - - - |  | Voice Communication
| CM-2023-12485208 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | FILTER DIRTY - AIR HANDLING UNIT 042 (TAG NO:AHU-A1110-429)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-12-19 00:03 | 2023-12-19 01:03 | 2023-12-20 01:03 | 24 | 2023-12-19 00:10 | 2023-12-19 04:15 | 245 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12575330 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING -T2-12-10 |  | FM008 |  | 2024-01-18 06:26 | 2024-01-18 07:26 | 2024-01-19 07:26 | 24 | 2024-01-18 06:35 | 2024-01-18 11:40 | 305 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 52135 | Jayasinghe Arachchige, Ms. Ramesha Niranjala Perera | N - - - |  | Voice Communication
| CM-2024-12588220 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TEMP VERY WARM- CHECK IN ROW 7,DEPARTURE -TERMINAL |  | FM008 |  | 2024-01-24 23:10 | 2024-01-25 00:10 | 2024-01-26 00:10 | 24 | 2024-01-24 23:15 | 2024-01-25 00:10 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 77406 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12587671 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT - ENTIRE CHECKIN ROW 7 |  | FM008 |  | 2024-01-22 23:34 | 2024-01-23 00:34 | 2024-01-24 00:34 | 24 | 2024-01-22 23:40 | 2024-01-23 02:00 | 140 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 121959 | 94954 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12670157 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC IS TOO HOT/WARM-QR SALES OFFICE DEPARTURE NEAR JAMOCHA ROW NO.6 |  | FM008 |  | 2024-02-21 22:36 | 2024-02-21 23:36 | 2024-02-22 23:36 | 24 | 2024-02-21 22:40 | 2024-02-21 23:30 | 50 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 17053 |  |  | 59517 | Reyes, Mr. Ojieson Castro | N - - - |  | Voice Communication
| CM-2024-12797272 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE CHECK IN ROW 5 ALL THE COUNTERS |  | FM008 |  | 2024-04-05 22:08 | 2024-04-05 23:08 | 2024-04-06 23:08 | 24 | 2024-04-05 22:15 | 2024-04-05 23:55 | 100 | 56 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 17053 |  |  | 139195 | Dahech, Mr. Mahdi | N - - - |  | Voice Communication
| CM-2024-12825810 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) – INFORMATION DESK NEAR ROW 7 & 8 |  | FM008 |  | 2024-04-14 15:45 | 2024-04-14 16:45 | 2024-04-15 16:45 | 24 | 2024-04-14 15:50 | 2024-04-14 22:10 | 380 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | T28776 | Abdallah Zoabi, Ms. Nermine Bakkar | N - - - |  | Voice Communication
| CM-2022-10917125 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – T4-10-03 |  | FM008 |  | 2022-08-07 21:20 | 2022-08-07 22:20 | 2022-08-08 22:20 | 24 | 2022-08-07 21:25 | 2022-08-07 23:00 | 95 | 175 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10989142 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT COOLING – ROW 3 TO ROW 9 (PASSENGERS COMPLAINING) |  | FM008 |  | 2022-08-31 13:45 | 2022-08-31 14:15 | 2022-08-31 18:15 | 4 | 2022-08-31 13:50 | 2022-08-31 15:40 | 110 | 30 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 55709 |  |  | 81713 | Rodrigues, Mr. Savio Xavier | N - - - |  | Voice Communication
| CM-2022-11222708 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING - AHU-A1110-429 – T4-10-03 |  | FM008 |  | 2022-11-27 13:09 | 2022-11-27 14:09 | 2022-11-28 14:09 | 24 | 2022-11-27 13:15 | 2022-11-27 14:40 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2023-12254198 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECKIN ROW 1 FROM COUNTERS 1 TO 6 |  | FM008 |  | 2023-10-04 04:09 | 2023-10-04 05:09 | 2023-10-05 05:09 | 24 | 2023-10-04 04:15 | 2023-10-04 04:45 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 111249 | Zarrouk, Mr. Ismail | N - - - |  | Voice Communication
| CM-2023-12387042 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD -- DEPARTURE CHECKIN ROW 4 COUNTER 8 |  | FM008 |  | 2023-11-18 09:11 | 2023-11-18 10:11 | 2023-11-19 10:11 | 24 | 2023-11-18 09:20 | 2023-11-18 10:40 | 80 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 137204 | Sahrane, Ms. Doha | N - - - |  | Voice Communication
| CM-2023-12451212 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU ABNORMAL NOISE -T4-08-04 |  | FM008 |  | 2023-12-07 09:09 | 2023-12-07 10:09 | 2023-12-08 10:09 | 24 | 2023-12-07 09:15 | 2023-12-07 14:05 | 290 | 725 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12557366 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | CHECK IN ROW NO 7 AC TOO HOT |  | FM008 |  | 2024-01-12 23:57 | 2024-01-13 00:57 | 2024-01-14 00:57 | 24 | 2024-01-13 00:05 | 2024-01-13 01:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12797082 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ROW # 5 AC TOO HOT CHECK IN HALL |  | FM008 |  | 2024-04-04 22:12 | 2024-04-04 23:12 | 2024-04-05 23:12 | 24 | 2024-04-04 22:15 | 2024-04-05 02:00 | 225 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12818050 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT AND NOISY -T2-12-10 |  | FM008 |  | 2024-04-08 07:47 | 2024-04-08 08:47 | 2024-04-09 08:47 | 24 | 2024-04-08 07:55 | 2024-04-08 08:55 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 82345 | Lari, Mr. Abdulla Nasser G A | N - - - |  | Voice Communication
| CM-2024-12828991 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC IS TOO HOT -T2-12-26 -BTWN ROW 4 AND ROW 5 -QR CUSTOMER SERVICE DESK |  | FM008 |  | 2024-04-16 13:37 | 2024-04-16 14:37 | 2024-04-17 14:37 | 24 | 2024-04-16 13:45 | 2024-04-16 16:40 | 175 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2022-11064526 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU-A1110-429- DP1 FILTER DIRTY -T4-10-03 |  | FM008 |  | 2022-09-29 00:04 | 2022-09-29 01:04 | 2022-09-30 01:04 | 24 | 2022-09-29 00:10 | 2022-09-29 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11177179 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT QR DND COUNTER ROW 5 NEXT TO JAMOCHA |  | FM008 |  | 2022-11-09 00:27 | 2022-11-09 01:27 | 2022-11-10 01:27 | 24 | 2022-11-09 00:35 | 2022-11-09 01:20 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 68672 | Kande Appuhamilage, Mr. Chathuranga Senarathna | N - - - |  | Voice Communication
| CM-2023-11342011 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE ROW #5 COUNTER AREA |  | FM008 |  | 2023-01-03 08:48 | 2023-01-03 09:48 | 2023-01-04 09:48 | 24 | 2023-01-03 08:55 | 2023-01-03 09:40 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | R10219 | Borsali, Ms. Dorsaf | N - - - |  | Voice Communication
| CM-2023-11459134 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU-A1110-429 DP1 FILTER ALARM T4-10-03 |  | FM008 |  | 2023-02-13 19:07 | 2023-02-13 20:07 | 2023-02-14 20:07 | 24 | 2023-02-13 19:10 | 2023-02-13 20:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17573 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-11841399 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM - AIR HANDLING UNIT 042 (TAG NO:AHU-A1110-429)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-05-31 14:24 | 2023-05-31 15:24 | 2023-06-01 15:24 | 24 | 2023-05-31 14:30 | 2023-05-31 16:55 | 145 | 186 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 87807 |  |  | 10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12127893 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY |  | FM008 |  | 2023-08-29 02:53 | 2023-08-29 03:53 | 2023-08-30 03:53 | 24 | 2023-08-29 03:00 | 2023-08-29 06:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12211095 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO WARM -CHECK IN ROW # 8 |  | FM008 |  | 2023-09-23 19:03 | 2023-09-23 20:03 | 2023-09-24 20:03 | 24 | 2023-09-23 19:05 | 2023-09-23 23:10 | 245 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 63789 | Ravidas, Ms. Silpa | N - - - |  | Voice Communication
| CM-2024-12553727 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO WARM -T2-12-10 |  | FM008 |  | 2024-01-11 08:33 | 2024-01-11 09:33 | 2024-01-12 09:33 | 24 | 2024-01-11 08:40 | 2024-01-11 09:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 8322 | Shabbir, Mr. Qadri Mubashir | N - - - |  | Voice Communication
| CM-2024-12570085 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING -T2-12-10 |  | FM008 |  | 2024-01-17 07:08 | 2024-01-17 08:08 | 2024-01-18 08:08 | 24 | 2024-01-17 07:15 | 2024-01-17 11:10 | 235 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | 52135 | Jayasinghe Arachchige, Ms. Ramesha Niranjala Perera | N - - - |  | Voice Communication
| CM-2024-12585884 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TEMP- WARM -T2-12-10 |  | FM008 |  | 2024-01-23 14:19 | 2024-01-23 15:19 | 2024-01-24 15:19 | 24 | 2024-01-23 14:25 | 2024-01-23 18:40 | 255 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 77406 | 95217 |  |  | 25135 | Hamdare, Mr. Nabil Mushtaque A. | N - - - |  | Voice Communication
| CM-2024-12628784 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING - T2-12-10 TROLLEY MANAGMENT OFFICE |  | FM008 |  | 2024-02-05 13:05 | 2024-02-05 14:05 | 2024-02-06 14:05 | 24 | 2024-02-05 13:10 | 2024-02-05 16:15 | 185 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 17053 | 17053 |  |  | 12871 | Pant, Mr. Birendra Prasad | N - - - |  | Voice Communication
| CM-2024-12650673 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | T2-12-10 AC TOO HOT |  | FM008 |  | 2024-02-14 13:44 | 2024-02-14 14:44 | 2024-02-15 14:44 | 24 | 2024-02-14 13:50 | 2024-02-14 15:40 | 110 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | 8322 | Shabbir, Mr. Qadri Mubashir | N - - - |  | Voice Communication
| CM-2024-12690896 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | RETURN MOTOR AND BLOWER NOISY - T4-08-04 |  | FM008 |  | 2024-02-29 08:22 | 2024-02-29 09:22 | 2024-03-01 09:22 | 24 | 2024-02-29 08:30 | 2024-02-29 12:30 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM12459 | Dhanabalan, Mr. Devaraj | N - - - |  | Voice Communication
| CM-2024-12704529 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO WARM - DEPARTURE CHECK-IN ROW #7 AREA |  | FM008 |  | 2024-03-04 23:36 | 2024-03-05 00:36 | 2024-03-06 00:36 | 24 | 2024-03-04 23:40 | 2024-03-05 02:30 | 170 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12770144 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT – SH0-0035 - AMERICAN TOURIST LANDSIDE DEPARTURES |  | FM008 |  | 2024-03-26 00:03 | 2024-03-26 01:03 | 2024-03-27 01:03 | 24 | 2024-03-26 00:08 | 2024-03-26 02:45 | 157 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 95217 |  |  | 140560 | Elomari, Mr. Moussa | N - - - |  | Voice Communication
| CM-2024-12822500 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE CHECK ROW 5 ALL COUNTERS |  | FM008 |  | 2024-04-12 15:12 | 2024-04-12 16:12 | 2024-04-13 16:12 | 24 | 2024-04-12 15:25 | 2024-04-12 17:00 | 95 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 87807 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12821569 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ROW 4 COUNTER 11 AC TOO HOT |  | FM008 |  | 2024-04-10 16:05 | 2024-04-10 17:05 | 2024-04-11 17:05 | 24 | 2024-04-10 16:10 | 2024-04-10 18:35 | 145 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 136727 | Dalil, Ms. Fatima Zahra | N - - - |  | Voice Communication
| CM-2023-12343348 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN ROW 6 COUNTER 5 AREA |  | FM008 |  | 2023-10-30 19:37 | 2023-10-30 20:37 | 2023-10-31 20:37 | 24 | 2023-10-30 19:45 | 2023-10-30 23:55 | 250 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 110866 | Mehri, Ms. Sahar | N - - - |  | Voice Communication
| CM-2023-12378248 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC DIFFUSER DIRTY - INSIDE T2-12-17 |  | FM008 |  | 2023-11-15 12:34 | 2023-11-15 13:34 | 2023-11-16 13:34 | 24 | 2023-11-15 12:40 | 2023-11-15 16:45 | 245 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | 134092 | Almario, Mr. Neftali Tinao | N - - - |  | E-mail
| CM-2023-12428337 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED -T4-10-03 |  | FM008 |  | 2023-11-30 14:20 | 2023-11-30 15:20 | 2023-12-01 15:20 | 24 | 2023-11-30 14:25 | 2023-11-30 18:25 | 240 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | COPEX CABLE DETARCHED/DAMAGED | RECTIFIED/REPLACED | 17333 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12451261 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE ROW # 4 |  | FM008 |  | 2023-12-07 11:25 | 2023-12-07 12:25 | 2023-12-08 12:25 | 24 | 2023-12-07 11:35 | 2023-12-07 13:20 | 105 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 119320 | 17053 |  |  | 138037 | Rida, Ms. Chaima | N - - - |  | Voice Communication
| CM-2023-12491760 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE ROW 6 COUNTER 7 |  | FM008 |  | 2023-12-21 21:31 | 2023-12-21 22:31 | 2023-12-22 22:31 | 24 | 2023-12-21 21:36 | 2023-12-22 01:00 | 204 | 64 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 138627 | 87807 |  |  | 132545 | Wahyuni, Ms. Dwi | N - - - |  | Voice Communication
| CM-2024-12689179 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING -T2-12-10 |  | FM008 |  | 2024-02-26 08:30 | 2024-02-26 09:30 | 2024-02-27 09:30 | 24 | 2024-02-26 08:35 | 2024-02-26 12:15 | 220 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | MOI | AAHIYA | N - - - |  | Voice Communication
| CM-2024-12694537 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT - CHECK IN ROW 7 |  | FM008 |  | 2024-03-02 23:00 | 2024-03-03 | 2024-03-04 | 24 | 2024-03-02 23:05 | 2024-03-03 01:40 | 155 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12705156 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | DP2 FINAL FILTER STATUS - AHU-A1110-429 - FOURTH FLOOR AREA 010 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP3.MTB429.AHU429.SYSALM.DP2 / |  | FM008 |  | 2024-03-08 02:42 | 2024-03-08 03:42 | 2024-03-09 03:42 | 24 | 2024-03-08 02:50 | 2024-03-08 04:15 | 85 | 145 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12712781 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) – ROW 7 |  | FM008 |  | 2024-03-07 22:39 | 2024-03-07 23:39 | 2024-03-08 23:39 | 24 | 2024-03-07 22:45 | 2024-03-08 01:05 | 140 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12768653 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT ROW 7 # 7 TO 14 |  | FM008 |  | 2024-03-26 15:54 | 2024-03-26 16:54 | 2024-03-27 16:54 | 24 | 2024-03-26 16:00 | 2024-03-26 17:10 | 70 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 95217 |  |  | 113586 | Shaik , Mr. Rameezuddin Ahamed | N - - - |  | Voice Communication
| CM-2024-12793122 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) - DEPARTURE CHECK-IN ROW # 7 AREA |  | FM008 |  | 2024-04-01 22:48 | 2024-04-01 23:48 | 2024-04-02 23:48 | 24 | 2024-04-01 22:54 | 2024-04-02 03:12 | 258 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12820386 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 6 COUNTER 1 TO 6 |  | FM008 |  | 2024-04-09 21:37 | 2024-04-09 22:37 | 2024-04-10 22:37 | 24 | 2024-04-09 21:45 | 2024-04-10 02:04 | 259 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 111000 | Gatheru, Ms. Esther Nyaruai | N - - - |  | Voice Communication
| CM-2023-12325306 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | CHECK IN ROW 07 AREA - AC TOO COLD |  | FM008 |  | 2023-10-27 06:48 | 2023-10-27 07:48 | 2023-10-28 07:48 | 24 | 2023-10-27 06:55 | 2023-10-27 08:00 | 65 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | R10331 | Naserian, Ms. Linda | N - - - |  | Voice Communication
| CM-2023-12362326 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 6 |  | FM008 |  | 2023-11-09 04:00 | 2023-11-09 05:00 | 2023-11-10 05:00 | 24 | 2023-11-09 04:05 | 2023-11-09 05:05 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | R14514 | El Malki, Ms. Salma | N - - - |  | Voice Communication
| CM-2023-12377671 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD ROW # 7 COUNTER 1 TO 3 CHECK IN HALL DEPARTURE |  | FM008 |  | 2023-11-12 22:15 | 2023-11-12 23:15 | 2023-11-13 23:15 | 24 | 2023-11-12 22:20 | 2023-11-12 23:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | R10331 | Naserian, Ms. Linda | N - - - |  | Voice Communication
| CM-2023-12379106 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ROW-4 COUNTER-10 AC TOO COLD |  | FM008 |  | 2023-11-14 11:45 | 2023-11-14 12:45 | 2023-11-15 12:45 | 24 | 2023-11-14 11:50 | 2023-11-14 17:45 | 355 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 87807 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2023-12462031 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ELR FAULT – |  | FM008 |  | 2023-12-11 19:01 | 2023-12-11 20:01 | 2023-12-12 20:01 | 24 | 2023-12-11 19:05 | 2023-12-11 23:40 | 275 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2024-12708194 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | MTB, LEVEL 2, CHECK-IN ROW 7 COUNTER 11 – AC TEMPERATURE IS TOO HOT |  | FM008 |  | 2024-03-05 23:31 | 2024-03-06 00:31 | 2024-03-07 00:31 | 24 | 2024-03-05 23:36 | 2024-03-05 23:59 | 23 | 23 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94954 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12713339 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | CHECK IN ROW NO 07 AC TOO COLD |  | FM008 |  | 2024-03-09 22:58 | 2024-03-09 23:58 | 2024-03-10 23:58 | 24 | 2024-03-09 23:05 | 2024-03-09 23:59 | 54 | 54 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12821414 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT T2-12-25 INFORMATION DESK ROW 5 |  | FM008 |  | 2024-04-09 15:20 | 2024-04-09 16:20 | 2024-04-10 16:20 | 24 | 2024-04-09 15:25 | 2024-04-09 18:30 | 185 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 115778 | Jbarek, Ms. Meryem | N - - - |  | Voice Communication
| CM-2024-12832726 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC HOT AMERICAN TOURIST FRONT OF DAY TO DAY CLOSE TO CHECK-IN ROW 8 DEPARTURE |  | FM008 |  | 2024-04-20 14:40 | 2024-04-20 15:40 | 2024-04-21 15:40 | 24 | 2024-04-20 14:45 | 2024-04-20 17:40 | 175 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 134373 | Abdul Hakeem, Mr. Mohamed Sharf | N - - - |  | Voice Communication
| CM-2022-10145736 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING AROUND ROW 6 (PASSENGERS COMPLAINING) – NEAR T2-12-17 |  | FM008 |  | 2022-02-14 22:43 | 2022-02-14 23:13 | 2022-02-15 03:13 | 4 | 2022-02-14 22:50 | 2022-02-14 23:58 | 68 | 28 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 55709 |  |  | 112233 | Ranasinghe Arachchige, Mr. Rahul Sachin Ranasinghe | N - - - |  | Voice Communication
| CM-2022-10171191 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE ROW 7 COUNTER 14 |  | FM008 |  | 2022-02-24 00:11 | 2022-02-24 01:11 | 2022-02-25 01:11 | 24 | 2022-02-24 00:20 | 2022-02-24 00:50 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 85125 | 55709 |  |  | 112233 | Ranasinghe Arachchige, Mr. Rahul Sachin Ranasinghe | N - - - |  | Voice Communication
| CM-2022-10032372 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | FILTER DIRTY; AHU-A1110-429 – T4-08-04 |  | FM008 |  | 2022-01-08 10:19 | 2022-01-08 11:19 | 2022-01-09 11:19 | 24 | 2022-01-08 10:29 | 2022-01-08 12:00 | 91 | 182 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10124719 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED-T4-08-04 -AHU-A1110-429)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-02-12 03:09 | 2022-02-12 04:09 | 2022-02-13 04:09 | 24 | 2022-02-12 03:15 | 2022-02-12 05:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 55709 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10145744 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU-A1110-429-FILTER DIRTY-T4-10-03 |  | FM008 |  | 2022-02-15 00:17 | 2022-02-15 01:17 | 2022-02-16 01:17 | 24 | 2022-02-15 00:26 | 2022-02-15 03:40 | 194 | 280 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10361438 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ROW 6 OFFICE T2-12-17 AC VENT PAINT FADED |  | FM008 |  | 2022-04-12 12:31 | 2022-04-12 13:31 | 2022-04-13 13:31 | 24 | 2022-04-12 12:40 | 2022-04-12 15:00 | 140 | 155 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM7797 | Adalla, Mr. Alex Otieno | N - - - |  | Voice Communication
| CM-2022-10770929 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-06-21 09:51 | 2022-06-21 10:51 | 2022-06-22 10:51 | 24 | 2022-06-21 10:00 | 2022-06-21 11:15 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10928513 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) – ROW 6 COUNTER 07 |  | FM008 |  | 2022-08-09 21:22 | 2022-08-09 22:22 | 2022-08-10 22:22 | 24 | 2022-08-09 21:30 | 2022-08-09 23:50 | 140 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 55709 |  |  | 84448 | Marata, Ms. Michelle De Los Angeles | N - - - |  | Voice Communication
| CM-2022-10971004 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | A/C IS TOO HOT IN ROW 6 |  | FM008 |  | 2022-08-25 21:46 | 2022-08-25 22:46 | 2022-08-26 22:46 | 24 | 2022-08-25 21:54 | 2022-08-25 23:40 | 106 | 43 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 55709 |  |  | 84448 | Marata, Ms. Michelle De Los Angeles | N - - - |  | Voice Communication
| CM-2022-11024615 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN HALL ROW 7, COUNTER 2 |  | FM008 |  | 2022-09-13 22:37 | 2022-09-13 23:37 | 2022-09-14 23:37 | 24 | 2022-09-13 22:47 | 2022-09-13 23:47 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 17053 |  |  | 107576 | Hichri, Ms. Amira | N - - - |  | Voice Communication
| CM-2023-11657894 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | ROW 6 COUNTERS AC TOO HOT |  | FM008 |  | 2023-04-13 17:07 | 2023-04-13 18:07 | 2023-04-14 18:07 | 24 | 2023-04-13 17:10 | 2023-04-13 20:00 | 170 | 70 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 101167 | Gunawardena, Ms. Dulwala Gedara Shashika Prasadini | N - - - |  | Voice Communication
| CM-2022-10958025 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TOO HOT ROW6-COUNTER 6 |  | FM008 |  | 2022-08-19 21:58 | 2022-08-19 22:58 | 2022-08-20 22:58 | 24 | 2022-08-19 22:10 | 2022-08-19 22:50 | 40 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 87807 | 55709 |  |  | 84448 | Marata, Ms. Michelle De Los Angeles | N - - - |  | Voice Communication
| CM-2023-11486535 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC VENT DUSTY ACCUMULATED -DEPARTURE ROW 7 - T2-12-10 (OFFICE)) |  | FM008 |  | 2023-02-24 16:39 | 2023-02-24 17:39 | 2023-02-25 17:39 | 24 | 2023-02-24 16:45 | 2023-02-24 18:30 | 105 | 85 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 87807 |  |  | 17967 | Manzon, Ms. Meriam Salazar | N - - - |  | Voice Communication
| CM-2023-11932831 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AHU-A1110-429 FILTER DIRTY |  | FM008 |  | 2023-06-28 18:53 | 2023-06-28 19:53 | 2023-06-29 19:53 | 24 | 2023-06-28 19:00 | 2023-06-28 20:30 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12740952 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | T2-12-26 – AC TOO HOT |  | FM008 |  | 2024-03-18 14:53 | 2024-03-18 15:53 | 2024-03-19 15:53 | 24 | 2024-03-18 15:00 | 2024-03-18 18:40 | 220 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2024-12772421 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC TEMP VERY WARM -DEPT-CHECK IN ROW 7-MTB |  | FM008 |  | 2024-03-27 17:53 | 2024-03-27 18:53 | 2024-03-28 18:53 | 24 | 2024-03-27 18:00 | 2024-03-27 19:35 | 95 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 77406 | 95217 |  |  | 115686 | Pa-Obnak, Ms. Sopittha | N - - - |  | Voice Communication
| CM-2024-12772690 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO HOT) - DEPARTURE CHECK-IN ROW #8 AREA |  | FM008 |  | 2024-03-29 01:19 | 2024-03-29 02:19 | 2024-03-30 02:19 | 24 | 2024-03-29 01:25 | 2024-03-29 06:25 | 300 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 113622 | Kotwal, Mr. Safwan Shabbir | N - - - |  | Voice Communication
| CM-2024-12798362 | ASD-MTB-FOF010-AHU042 | AIR HANDLING UNIT-05 | A/C IS TOO HOT DEPARTURES HALL |  | FM008 |  | 2024-04-06 16:52 | 2024-04-06 17:52 | 2024-04-07 17:52 | 24 | 2024-04-06 17:00 | 2024-04-06 21:03 | 243 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | 80930 | Papa, Ms. Donna Deanne Gill | N - - - |  | Voice Communication
| CM-2022-10779871 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 – DP 1 FILTER ALARM – T4-10-03 |  | FM008 |  | 2022-06-26 07:06 | 2022-06-26 08:06 | 2022-06-27 08:06 | 24 | 2022-06-26 07:15 | 2022-06-26 08:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11263280 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | FRESH AIR DUCT INSULATION DAMAGED - AHU-A1110-431 – T4-08-21 |  | FM008 |  | 2022-12-11 10:10 | 2022-12-11 11:10 | 2022-12-12 11:10 | 24 | 2022-12-11 10:15 | 2022-12-11 14:30 | 255 | 285 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10913830 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | SUPPLY MOTOT BELT DAMAGED :AHU-A1110-431) |  | FM008 |  | 2022-08-05 03:04 | 2022-08-05 04:04 | 2022-08-06 04:04 | 24 | 2022-08-05 03:10 | 2022-08-05 04:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 55709 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2022-11005657 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | SUPPLY FAN MOTOR BELT DAMAGED – T4-10-03 |  | FM008 |  | 2022-09-08 00:27 | 2022-09-08 01:27 | 2022-09-09 01:27 | 24 | 2022-09-08 00:37 | 2022-09-08 02:27 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11114423 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY DP3-T4-08-21 |  | FM008 |  | 2022-10-18 16:03 | 2022-10-18 17:03 | 2022-10-19 17:03 | 24 | 2022-10-18 16:10 | 2022-10-18 17:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12036897 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431-DP-FILTER ALARM-T4-10-03 |  | FM008 |  | 2023-08-02 19:15 | 2023-08-02 20:15 | 2023-08-03 20:15 | 24 | 2023-08-02 19:20 | 2023-08-02 20:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12631433 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2024-02-07 00:30 | 2024-02-07 01:30 | 2024-02-08 01:30 | 24 | 2024-02-07 00:35 | 2024-02-07 04:45 | 250 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 95217 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2022-10914568 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 DP1 ALARM T4-08-04 |  | FM008 |  | 2022-08-04 18:58 | 2022-08-04 19:58 | 2022-08-05 19:58 | 24 | 2022-08-04 19:05 | 2022-08-04 20:00 | 55 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 55709 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-10998548 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | FILTER ALARM – T4-10-03 |  | FM008 |  | 2022-09-07 22:33 | 2022-09-07 23:33 | 2022-09-08 23:33 | 24 | 2022-09-07 22:43 | 2022-09-07 23:58 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 105233 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11062622 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 DP1 FILTER DIRTY |  | FM008 |  | 2022-09-27 19:21 | 2022-09-27 20:21 | 2022-09-28 20:21 | 24 | 2022-09-27 19:30 | 2022-09-27 22:15 | 165 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11162308 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING -AHU-A1110-431 |  | FM008 |  | 2022-11-06 00:16 | 2022-11-06 01:16 | 2022-11-07 01:16 | 24 | 2022-11-06 00:25 | 2022-11-06 02:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 124475 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11177224 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | T2-12-25 – AC NOT WORKING |  | FM008 |  | 2022-11-09 08:22 | 2022-11-09 09:22 | 2022-11-10 09:22 | 24 | 2022-11-09 08:30 | 2022-11-09 09:15 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | THE CONTROL PANEL IS FAULTY | PANEL REPAIRED | 17573 | 87807 |  |  | 111243 | Nguma, Ms. Margaret Munyiva | N - - - |  | Voice Communication
| CM-2022-11270994 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-431 – T4-10-03 |  | FM008 |  | 2022-12-15 00:09 | 2022-12-15 01:09 | 2022-12-16 01:09 | 24 | 2022-12-15 00:15 | 2022-12-15 03:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2023-11624213 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 FILTER DIRTY T4-10-03 |  | FM008 |  | 2023-04-08 11:39 | 2023-04-08 12:39 | 2023-04-09 12:39 | 24 | 2023-04-08 11:45 | 2023-04-08 13:15 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-11877365 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 FILTER DIRTY T4-08-04 |  | FM008 |  | 2023-06-12 19:03 | 2023-06-12 20:03 | 2023-06-13 20:03 | 24 | 2023-06-12 19:07 | 2023-06-12 20:37 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11883880 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431- FILTER DIRTY- |  | FM008 |  | 2023-06-16 07:32 | 2023-06-16 08:32 | 2023-06-17 08:32 | 24 | 2023-06-16 07:40 | 2023-06-16 10:10 | 150 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 87807 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2024-12574403 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2024-01-17 09:02 | 2024-01-17 10:02 | 2024-01-18 10:02 | 24 | 2024-01-17 09:10 | 2024-01-17 13:00 | 230 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12777384 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AC NOT WORKING -QR NEAR ROW 6 |  | FM008 |  | 2024-03-30 22:50 | 2024-03-30 23:50 | 2024-03-31 23:50 | 24 | 2024-03-30 22:55 | 2024-03-31 00:15 | 80 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | 59517 | Reyes, Mr. Ojieson Castro | N - - - |  | Voice Communication
| CM-2023-12252524 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-04 00:11 | 2023-10-04 01:11 | 2023-10-05 01:11 | 24 | 2023-10-04 00:15 | 2023-10-04 01:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12252525 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU SUPPLY FAN BELT DAMAGED |  | FM008 |  | 2023-10-04 00:12 | 2023-10-04 01:12 | 2023-10-05 01:12 | 24 | 2023-10-04 00:18 | 2023-10-04 02:20 | 122 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 121959 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10634519 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 FILTER DIRTY |  | FM008 |  | 2022-05-09 22:12 | 2022-05-09 23:12 | 2022-05-10 23:12 | 24 | 2022-05-09 22:22 | 2022-05-09 23:52 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10816904 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 – DP2 FILTER ALARM – T4-10-03 |  | FM008 |  | 2022-07-05 19:04 | 2022-07-05 20:04 | 2022-07-06 20:04 | 24 | 2022-07-05 19:10 | 2022-07-05 22:45 | 215 | 205 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94954 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11969556 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED, AHU-A1110-431, T4-08-04 |  | FM008 |  | 2023-07-12 02:23 | 2023-07-12 03:23 | 2023-07-13 03:23 | 24 | 2023-07-12 02:30 | 2023-07-12 04:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10044366 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-01-12 11:56 | 2022-01-12 12:56 | 2022-01-13 12:56 | 24 | 2022-01-12 12:05 | 2022-01-12 16:10 | 245 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10119516 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU044 FILTER BLOCKED/DIRTY – T4-10-03 |  | FM008 |  | 2022-02-07 19:13 | 2022-02-07 20:13 | 2022-02-08 20:13 | 24 | 2022-02-07 19:22 | 2022-02-07 23:15 | 233 | 280 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106976 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10570343 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | AHU-A1110-431 – FILTER IS DIRTY – T4-08-04 |  | FM008 |  | 2022-04-17 19:12 | 2022-04-17 20:12 | 2022-04-18 20:12 | 24 | 2022-04-17 19:21 | 2022-04-17 21:11 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11630546 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2023-04-07 16:41 | 2023-04-07 17:41 | 2023-04-08 17:41 | 24 | 2023-04-07 16:51 | 2023-04-07 18:20 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 121959 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12257481 | ASD-MTB-FOF010-AHU044 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED - AHU-A1110-431 – T4-08-04 |  | FM008 |  | 2023-10-08 00:03 | 2023-10-08 01:03 | 2023-10-09 01:03 | 24 | 2023-10-08 00:08 | 2023-10-08 03:08 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | FAN BLOWER IS DIRTY | CLEANED THE BLOWER | 106973 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11024060 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHU-A1110-433 AHU LAMP NOT WORKING T4-10-03 |  | FM008 |  | 2022-09-14 20:44 | 2022-09-14 21:44 | 2022-09-15 21:44 | 24 | 2022-09-14 20:50 | 2022-09-14 22:40 | 110 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11059279 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-10-03 |  | FM008 |  | 2022-09-26 00:53 | 2022-09-26 01:53 | 2022-09-27 01:53 | 24 | 2022-09-26 00:59 | 2022-09-26 04:20 | 201 | 206 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11403181 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | DP3 FILTER DIRTY - AHU-A1110-433 - T4-10-03 |  | FM008 |  | 2023-01-25 01:12 | 2023-01-25 02:12 | 2023-01-26 02:12 | 24 | 2023-01-25 01:15 | 2023-01-25 02:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-11824182 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-26 10:38 | 2023-05-26 11:38 | 2023-05-27 11:38 | 24 | 2023-05-26 10:45 | 2023-05-26 15:30 | 285 | 337 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12585979 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED |  | FM008 |  | 2024-01-24 01:40 | 2024-01-24 02:40 | 2024-01-25 02:40 | 24 | 2024-01-24 01:45 | 2024-01-24 04:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | FAN BLOWER IS DIRTY | CLEANED THE BLOWER | 121959 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11697050 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHU RETURN MOTOR FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2023-04-23 15:29 | 2023-04-23 16:29 | 2023-04-24 16:29 | 24 | 2023-04-23 15:39 | 2023-04-23 17:07 | 88 | 176 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 121959 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12511480 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - MECHANICAL ROOM T4-10-03, EXTRA REMARKS-: PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP3.MTB433.AHU433.SYSALM.DP1 / |  | FM008 |  | 2023-12-27 15:32 | 2023-12-27 16:32 | 2023-12-28 16:32 | 24 | 2023-12-27 15:38 | 2023-12-27 23:59 | 501 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 138627 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | Y - - - |  | BMS
| CM-2022-9950909 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHUT INSIDE LIGHT NOT WORKING |  | FM008 |  | 2022-01-02 00:08 | 2022-01-02 01:08 | 2022-01-03 01:08 | 24 | 2022-01-02 00:15 | 2022-01-02 01:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17053 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10142121 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHU-A1110-433-DRAIN LINE BLOCKED |  | FM008 |  | 2022-02-14 04:08 | 2022-02-14 05:08 | 2022-02-15 05:08 | 24 | 2022-02-14 04:15 | 2022-02-14 05:40 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 95217 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10049858 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AIR DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-01-15 03:17 | 2022-01-15 04:17 | 2022-01-16 04:17 | 24 | 2022-01-15 03:25 | 2022-01-15 04:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | BMS
| CM-2022-10142241 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -T4-10-03 |  | FM008 |  | 2022-02-14 19:05 | 2022-02-14 20:05 | 2022-02-15 20:05 | 24 | 2022-02-14 19:10 | 2022-02-14 21:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-11495244 | ASD-MTB-FOF010-AHU046 | AIR HANDLING UNIT-05 | AHU DRAIN LINE BLOCKED - T4-08-04 |  | FM008 |  | 2023-03-01 22:15 | 2023-03-01 23:15 | 2023-03-02 23:15 | 24 | 2023-03-01 22:25 | 2023-03-01 23:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17053 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10209350 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT ILLUMINATING INSIDE AHU RETURN AIRSIDE - AHU-A1110-445 – T4-08-04 |  | FM008 |  | 2022-03-02 22:18 | 2022-03-02 23:18 | 2022-03-03 23:18 | 24 | 2022-03-02 22:25 | 2022-03-02 23:35 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 106973 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10573703 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445- DP1 FILTER ALARM -T4-10-03 |  | FM008 |  | 2022-04-18 13:43 | 2022-04-18 14:43 | 2022-04-19 14:43 | 24 | 2022-04-18 13:50 | 2022-04-18 15:25 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10770768 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM –T4-10-03 |  | FM008 |  | 2022-06-20 13:50 | 2022-06-20 14:50 | 2022-06-21 14:50 | 24 | 2022-06-20 14:00 | 2022-06-20 15:15 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11158738 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AHU-A1110-445 - MECHANICAL ROOM T4-10-03 |  | FM008 |  | 2022-11-03 20:02 | 2022-11-03 21:02 | 2022-11-04 21:02 | 24 | 2022-11-03 20:05 | 2022-11-03 21:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12062554 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445-FILTER DIRTY MTB -FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-08-08 07:40 | 2023-08-08 08:40 | 2023-08-09 08:40 | 24 | 2023-08-08 07:45 | 2023-08-08 15:00 | 435 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11248044 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – T4-08-04 |  | FM008 |  | 2022-12-06 08:15 | 2022-12-06 09:15 | 2022-12-07 09:15 | 24 | 2022-12-06 08:20 | 2022-12-06 12:30 | 250 | 750 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 17053 |  |  | FM9671 | Karunagoda Mudalige, Mr. Kasun Lakmal | N - - - |  | Voice Communication
| CM-2022-11260111 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445 SUPPLY MOTOR CABLE FAULTY |  | FM008 |  | 2022-12-11 00:05 | 2022-12-11 01:05 | 2022-12-12 01:05 | 24 | 2022-12-11 00:10 | 2022-12-11 03:30 | 200 | 400 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | FAULTY CONTROL THERMOSTAT | REPLACED THE THERMOSTAT | 68485 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11499882 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY |  | FM008 |  | 2023-02-27 14:37 | 2023-02-27 15:37 | 2023-02-28 15:37 | 24 | 2023-02-27 14:43 | 2023-02-27 18:10 | 207 | 124 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12282584 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING |  | FM008 |  | 2023-10-15 16:21 | 2023-10-15 17:21 | 2023-10-16 17:21 | 24 | 2023-10-15 16:30 | 2023-10-15 18:45 | 135 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95216 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12366802 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | FILTER DIRTY:- AIR HANDLING UNIT 058 (TAG NO:AHU-A1110-445)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-11-10 07:17 | 2023-11-10 08:17 | 2023-11-11 08:17 | 24 | 2023-11-10 07:25 | 2023-11-10 10:30 | 185 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11041110 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-10-03 |  | FM008 |  | 2022-09-23 22:51 | 2022-09-23 23:51 | 2022-09-24 23:51 | 24 | 2022-09-23 22:55 | 2022-09-23 23:55 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11818400 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1110-445 - MECHANICAL ROOM T4-10-03 |  | FM008 |  | 2023-05-22 10:46 | 2023-05-22 11:46 | 2023-05-23 11:46 | 24 | 2023-05-22 10:53 | 2023-05-22 17:00 | 367 | 352 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM9991 | Eymer Gomez, Mr. Joseph Hementh Gomez | N - - - |  | Voice Communication
| CM-2023-12463397 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445 RETURN BLOWER BELT DAMAGED |  | FM008 |  | 2023-12-11 12:47 | 2023-12-11 13:47 | 2023-12-12 13:47 | 24 | 2023-12-11 12:55 | 2023-12-11 14:10 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12488678 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445 FILTER DIRTY C4-10-05 |  | FM008 |  | 2023-12-20 13:49 | 2023-12-20 14:49 | 2023-12-21 14:49 | 24 | 2023-12-20 13:55 | 2023-12-20 15:00 | 65 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12403212 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | SUPPLY MOTOR CABLE FAULTY - AIR HANDLING UNIT 058 (TAG NO:AHU-A1110-445)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2023-11-21 07:41 | 2023-11-21 08:41 | 2023-11-22 08:41 | 24 | 2023-11-21 07:50 | 2023-11-21 11:00 | 190 | 380 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 119320 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10128942 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445 – FILTER IS DIRTY – T4-08-04 |  | FM008 |  | 2022-02-11 19:12 | 2022-02-11 20:12 | 2022-02-12 20:12 | 24 | 2022-02-11 19:22 | 2022-02-11 21:22 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10125270 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED -T4-08-04-AHU-A1110-445)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-02-13 02:32 | 2022-02-13 03:32 | 2022-02-14 03:32 | 24 | 2022-02-13 02:40 | 2022-02-13 04:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17336 | 55709 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10124642 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | BELT LOOSE -AHU- A1110-445)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-02-11 22:11 | 2022-02-11 23:11 | 2022-02-12 23:11 | 24 | 2022-02-11 22:20 | 2022-02-11 23:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 55709 |  |  | fm3093 | fm3093 | N - - - |  | Voice Communication
| CM-2022-10593139 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | FILTER DIRTY- T4-08-04 |  | FM008 |  | 2022-04-29 00:13 | 2022-04-29 01:13 | 2022-04-30 01:13 | 24 | 2022-04-29 00:20 | 2022-04-29 01:35 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10793645 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - (TAG NO:AHU-A1110-445)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 010 |  | FM008 |  | 2022-07-04 01:30 | 2022-07-04 02:30 | 2022-07-05 02:30 | 24 | 2022-07-04 01:40 | 2022-07-04 03:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 95217 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11933336 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | FILTER DIRTY - T4-08-04 |  | FM008 |  | 2023-06-27 18:59 | 2023-06-27 19:59 | 2023-06-28 19:59 | 24 | 2023-06-27 19:05 | 2023-06-27 23:45 | 280 | 187 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | E-mail
| CM-2023-11932832 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | AHU-A1110-445 BELT DAMAGED |  | FM008 |  | 2023-06-28 18:54 | 2023-06-28 19:54 | 2023-06-29 19:54 | 24 | 2023-06-28 19:00 | 2023-06-28 22:05 | 185 | 280 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12285786 | ASD-MTB-FOF010-AHU058 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PULLEY IS WORN OUT |  | FM008 |  | 2023-10-15 12:42 | 2023-10-15 13:42 | 2023-10-16 13:42 | 24 | 2023-10-15 12:50 | 2023-10-15 16:10 | 200 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 010 | N | DAMAGED | PULLEY DAMAGE | REPLACED THE PULLEY | 95216 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-11762474 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU-A1110-410 DP2 FILTER ALARM |  | FM008 |  | 2023-05-04 04:24 | 2023-05-04 05:24 | 2023-05-05 05:24 | 24 | 2023-05-04 04:35 | 2023-05-04 05:35 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11959371 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-410) |  | FM008 |  | 2023-07-08 00:12 | 2023-07-08 01:12 | 2023-07-09 01:12 | 24 | 2023-07-08 00:20 | 2023-07-08 02:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12230272 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED - AHU-A1110-410 – T4-09-04 |  | FM008 |  | 2023-09-28 00:03 | 2023-09-28 01:03 | 2023-09-29 01:03 | 24 | 2023-09-28 00:10 | 2023-09-28 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12230273 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | RELIEF V BELT DAMAGED - AHU-A1110-410 – T4-09-04 |  | FM008 |  | 2023-09-28 00:04 | 2023-09-28 01:04 | 2023-09-29 01:04 | 24 | 2023-09-28 00:10 | 2023-09-28 03:40 | 210 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10917130 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | SUPPLY WWE BELT IS DAMAGED - AHU-A1110-410 - T4-09-04 |  | FM008 |  | 2022-08-08 00:02 | 2022-08-08 01:02 | 2022-08-09 01:02 | 24 | 2022-08-08 00:10 | 2022-08-08 01:30 | 80 | 240 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 55709 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2022-10958458 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM T4-09-04 |  | FM008 |  | 2022-08-22 07:50 | 2022-08-22 08:50 | 2022-08-23 08:50 | 24 | 2022-08-22 07:58 | 2022-08-22 09:00 | 62 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10997811 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T4-09-04 |  | FM008 |  | 2022-09-04 11:39 | 2022-09-04 12:39 | 2022-09-05 12:39 | 24 | 2022-09-04 11:45 | 2022-09-04 13:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17053 | 17053 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2023-11613157 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU-A1110-410-LIGHTING FLEXIBLE CONNECT DAMAGE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-04-02 09:06 | 2023-04-02 10:06 | 2023-04-03 10:06 | 24 | 2023-04-02 09:10 | 2023-04-02 13:50 | 280 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11621657 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-09-04 |  | FM008 |  | 2023-04-04 10:07 | 2023-04-04 11:07 | 2023-04-05 11:07 | 24 | 2023-04-04 10:15 | 2023-04-04 12:30 | 135 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11621058 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU-A1110-410 RELEASE FAN MOTOR CABLE FLEXIBLE DAMAGED – T4-09-04 |  | FM008 |  | 2023-04-05 13:10 | 2023-04-05 14:10 | 2023-04-06 14:10 | 24 | 2023-04-05 13:20 | 2023-04-05 16:18 | 178 | 181 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 106914 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12016453 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | EXHAUST GRILL DIRTY - EF-A1110-410- CH1 KITCHEN |  | FM008 |  | 2023-07-28 19:54 | 2023-07-28 20:54 | 2023-07-29 20:54 | 24 | 2023-07-28 20:04 | 2023-07-28 22:04 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12016454 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | EXHAUST GRILL DIRTY - EF-A1110-410- CH1 FIRST MALE/FEMALE WASHROOM |  | FM008 |  | 2023-07-28 19:55 | 2023-07-28 20:55 | 2023-07-29 20:55 | 24 | 2023-07-28 20:00 | 2023-07-28 23:40 | 220 | 368 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11060323 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | FILTER ALARM- T4-09-04 |  | FM008 |  | 2022-09-26 07:52 | 2022-09-26 08:52 | 2022-09-27 08:52 | 24 | 2022-09-26 08:00 | 2022-09-26 12:10 | 250 | 156 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11113677 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-10-19 21:23 | 2022-10-19 22:23 | 2022-10-20 22:23 | 24 | 2022-10-19 21:30 | 2022-10-19 22:46 | 76 | 152 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11868301 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU-A1110-410- FILTER DIRTY |  | FM008 |  | 2023-06-10 18:57 | 2023-06-10 19:57 | 2023-06-11 19:57 | 24 | 2023-06-10 19:03 | 2023-06-10 21:03 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12231296 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU FILTER DIRTY - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-09-28 01:03 | 2023-09-28 02:03 | 2023-09-29 02:03 | 24 | 2023-09-28 01:10 | 2023-09-28 05:45 | 275 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12232975 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED - AIR HANDLING UNIT 023 (TAG NO:AHU-A1110-410)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-09-30 00:03 | 2023-09-30 01:03 | 2023-10-01 01:03 | 24 | 2023-09-30 00:08 | 2023-09-30 03:08 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 119320 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12672484 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2024-02-22 00:21 | 2024-02-22 01:21 | 2024-02-23 01:21 | 24 | 2024-02-22 00:25 | 2024-02-22 02:30 | 125 | 375 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95216 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10100039 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU DP2 FILTER ALARM - T4-09-04 |  | FM008 |  | 2022-02-02 20:26 | 2022-02-02 21:26 | 2022-02-03 21:26 | 24 | 2022-02-02 20:35 | 2022-02-02 23:45 | 190 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17053 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10634520 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU-A1110-410 FILTER DIRTY |  | FM008 |  | 2022-05-09 22:15 | 2022-05-09 23:15 | 2022-05-10 23:15 | 24 | 2022-05-09 22:20 | 2022-05-09 23:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10995339 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | DRAIN LINE INSULATION DAMAGED - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-09-05 16:16 | 2022-09-05 17:16 | 2022-09-06 17:16 | 24 | 2022-09-05 16:20 | 2022-09-05 18:30 | 130 | 260 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 94954 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-10118032 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-02-07 09:47 | 2022-02-07 10:47 | 2022-02-08 10:47 | 24 | 2022-02-07 09:50 | 2022-02-07 11:15 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-10570344 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU-A1110-410 – FILTER IS DIRTY – T4-09-04 |  | FM008 |  | 2022-04-17 19:13 | 2022-04-17 20:13 | 2022-04-18 20:13 | 24 | 2022-04-17 19:23 | 2022-04-17 23:20 | 237 | 227 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10723574 | ASD-MTB-FOF011-AHU023 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AIR HANDLING UNIT 023 (TAG NO:AHU-A1110-410)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-06-07 08:45 | 2022-06-07 09:45 | 2022-06-08 09:45 | 24 | 2022-06-07 08:50 | 2022-06-07 10:35 | 105 | 315 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10652555 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | RELIEF SIDE BELT DAMAGED -AHU-A1110-412)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-05-12 00:15 | 2022-05-12 01:15 | 2022-05-13 01:15 | 24 | 2022-05-12 00:20 | 2022-05-12 02:00 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12206495 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-412 – T4-09-04 |  | FM008 |  | 2023-09-21 11:13 | 2023-09-21 12:13 | 2023-09-22 12:13 | 24 | 2023-09-21 11:20 | 2023-09-21 17:30 | 370 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12233296 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED - AHU-A1110-412) – T4 09 04 |  | FM008 |  | 2023-10-01 00:05 | 2023-10-01 01:05 | 2023-10-02 01:05 | 24 | 2023-10-01 00:10 | 2023-10-01 03:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 132112 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11046259 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | AHU-A1110-412- FILTER ALARM-- |  | FM008 |  | 2022-09-25 11:30 | 2022-09-25 12:30 | 2022-09-26 12:30 | 24 | 2022-09-25 11:40 | 2022-09-25 15:15 | 215 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11350316 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | RELIEF FAN WEE BELT DAMAGED - AHU-A1110-412 - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-01-05 22:18 | 2023-01-05 23:18 | 2023-01-06 23:18 | 24 | 2023-01-05 22:25 | 2023-01-05 23:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | E-mail
| CM-2023-11524383 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1110-412 |  | FM008 |  | 2023-03-07 09:56 | 2023-03-07 10:56 | 2023-03-08 10:56 | 24 | 2023-03-07 10:05 | 2023-03-07 14:30 | 265 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11615770 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | DOOR INTER LOCK HANDLE DAMAGE-AHU-A1110-412 |  | FM008 |  | 2023-04-03 10:05 | 2023-04-03 11:05 | 2023-04-04 11:05 | 24 | 2023-04-03 10:11 | 2023-04-03 11:40 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | DOOR HANDLE LOOSE/DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12252001 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING – (AHU-A1110-412) -T4 11 03 |  | FM008 |  | 2023-10-01 20:44 | 2023-10-01 21:44 | 2023-10-02 21:44 | 24 | 2023-10-01 20:54 | 2023-10-01 23:24 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 132112 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-11351105 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM- AHU-A1110-421-T4-09-04 |  | FM008 |  | 2023-01-06 00:31 | 2023-01-06 01:31 | 2023-01-07 01:31 | 24 | 2023-01-06 00:35 | 2023-01-06 03:30 | 175 | 175 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 133396 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12232977 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED - AIR HANDLING UNIT 025 (TAG NO:AHU-A1110-412)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-09-30 00:05 | 2023-09-30 01:05 | 2023-10-01 01:05 | 24 | 2023-09-30 00:10 | 2023-09-30 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 119320 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12232981 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | RELIEF FAN BELT DAMAGED - AHU-A1110-412 – T4-09-04 |  | FM008 |  | 2023-09-30 01:00 | 2023-09-30 02:00 | 2023-10-01 02:00 | 24 | 2023-09-30 01:05 | 2023-09-30 04:15 | 190 | 247 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10044367 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | AHU-A1110-412 – FILTER DIRTY – T4-09-04 |  | FM008 |  | 2022-01-12 11:57 | 2022-01-12 12:57 | 2022-01-13 12:57 | 24 | 2022-01-12 12:06 | 2022-01-12 14:30 | 144 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-11005184 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 025 (TAG NO:AHU-A1110-412)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 FILTER ALARM |  | FM008 |  | 2022-09-09 00:16 | 2022-09-09 01:16 | 2022-09-10 01:16 | 24 | 2022-09-09 00:25 | 2022-09-09 03:50 | 205 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11658146 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | DDC-A1110-412+424 - RAD FEEDBACK MISMATCH |  | FM008 |  | 2023-04-14 16:41 | 2023-04-14 17:41 | 2023-04-15 17:41 | 24 | 2023-04-14 16:45 | 2023-04-14 17:42 | 57 | 114 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10118026 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | FILTER DIRTY T4-09-04 |  | FM008 |  | 2022-02-07 09:44 | 2022-02-07 10:44 | 2022-02-08 10:44 | 24 | 2022-02-07 09:50 | 2022-02-07 17:00 | 430 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-10118029 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | RELIEF V BELT DAMAGED T4-09-04 |  | FM008 |  | 2022-02-07 09:46 | 2022-02-07 10:46 | 2022-02-08 10:46 | 24 | 2022-02-07 09:50 | 2022-02-07 15:20 | 330 | 115 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 55709 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-10917337 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY T4-09-07 |  | FM008 |  | 2022-08-09 00:15 | 2022-08-09 01:15 | 2022-08-10 01:15 | 24 | 2022-08-09 00:25 | 2022-08-09 02:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | BMS
| CM-2023-11617830 | ASD-MTB-FOF011-AHU025 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - T4-09-04 |  | FM008 |  | 2023-04-02 15:08 | 2023-04-02 16:08 | 2023-04-03 16:08 | 24 | 2023-04-02 15:15 | 2023-04-02 16:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM7343 | Azad Hussain Ansari, | N - - - |  | Voice Communication
| CM-2022-10313697 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | RELIEF FLEXIBLE HOSE CONNECTOR DAMAGED |  | FM008 |  | 2022-04-04 07:36 | 2022-04-04 08:36 | 2022-04-05 08:36 | 24 | 2022-04-04 07:46 | 2022-04-04 11:05 | 199 | 241 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 106972 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12343825 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AHU-A1110-414- DRAINAGE LINE BLOCKED |  | FM008 |  | 2023-11-01 21:00 | 2023-11-01 22:00 | 2023-11-02 22:00 | 24 | 2023-11-01 21:05 | 2023-11-01 22:05 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 87807 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2024-12557585 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AC TOO HOT ARRIVALS HALL MEET AND GREET AREA |  | FM008 |  | 2024-01-13 17:48 | 2024-01-13 18:48 | 2024-01-14 18:48 | 24 | 2024-01-13 17:55 | 2024-01-13 21:05 | 190 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | T26780 | Laila, Ms. Lahlimi | N - - - |  | Voice Communication
| CM-2024-12882349 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -T4-09-04 |  | FM008 |  | 2024-04-30 17:10 | 2024-04-30 18:10 | 2024-05-01 18:10 | 24 | 2024-04-30 17:16 | 2024-04-30 20:30 | 194 | 276 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2022-10902584 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AHU-A1110-414 FILTER DIRTY T4-9-09-04 |  | FM008 |  | 2022-08-01 07:29 | 2022-08-01 08:29 | 2022-08-02 08:29 | 24 | 2022-08-01 07:35 | 2022-08-01 09:00 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 87807 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11304226 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -T4-09-04 |  | FM008 |  | 2022-12-26 00:11 | 2022-12-26 01:11 | 2022-12-27 01:11 | 24 | 2022-12-26 00:20 | 2022-12-28 07:51 | 3331.117 | 480 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2024-12534729 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | ARRIVAL MEET AND GREET AREA AC TOO HOT |  | FM008 |  | 2024-01-05 16:23 | 2024-01-05 17:23 | 2024-01-06 17:23 | 24 | 2024-01-05 16:30 | 2024-01-05 18:30 | 120 | 70 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | T28773 | Nuraeni, Ms. Neni | N - - - |  | Voice Communication
| CM-2022-11040231 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-09-24 11:31 | 2022-09-24 12:31 | 2022-09-25 12:31 | 24 | 2022-09-24 11:40 | 2022-09-24 14:00 | 140 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-11929917 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AHU-A1110-414 AHU CABIN LIGHTING SWITCH DAMAGED T4-09-04 |  | FM008 |  | 2023-06-26 10:46 | 2023-06-26 11:46 | 2023-06-27 11:46 | 24 | 2023-06-26 10:56 | 2023-06-26 14:30 | 214 | 246 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 89127 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-12205360 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-414 – T4-09-04 |  | FM008 |  | 2023-09-21 11:18 | 2023-09-21 12:18 | 2023-09-22 12:18 | 24 | 2023-09-21 11:25 | 2023-09-21 15:55 | 270 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12364191 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AHU BEARING NOISY |  | FM008 |  | 2023-11-09 08:40 | 2023-11-09 09:40 | 2023-11-10 09:40 | 24 | 2023-11-09 08:45 | 2023-11-09 11:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 17053 |  |  | FM6971 | Perez Rendon Albaladejo, Ms. Eulalia | N - - - |  | Voice Communication
| CM-2024-12557288 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AC TOO HOT MEET AND GREET |  | FM008 |  | 2024-01-12 14:45 | 2024-01-12 15:45 | 2024-01-13 15:45 | 24 | 2024-01-12 14:50 | 2024-01-12 17:50 | 180 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | T28748 | Kamonye, Ms. Janet Faith Njeri | N - - - |  | Voice Communication
| CM-2022-10025590 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AHU-A1110-414 LIGHTING FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2022-01-05 11:04 | 2022-01-05 12:04 | 2022-01-06 12:04 | 24 | 2022-01-05 11:14 | 2022-01-05 12:43 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 106972 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-9967083 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGE AHU-A1110-414 |  | FM008 |  | 2022-01-03 00:58 | 2022-01-03 01:58 | 2022-01-04 01:58 | 24 | 2022-01-03 01:05 | 2022-01-03 03:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | SUPPLY FAN FAULTY | REPAIRED THE FAN | 85125 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-9967112 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | RELIEF FAN BELT DAMAGED - T4-09-04 |  | FM008 |  | 2022-01-03 02:59 | 2022-01-03 03:59 | 2022-01-04 03:59 | 24 | 2022-01-03 03:05 | 2022-01-03 04:45 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-9957808 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | DRAINAGE LINE SUMP RUSTED - AHU-A1110-414 – T4-09-04 |  | FM008 |  | 2022-01-05 03:02 | 2022-01-05 04:02 | 2022-01-06 04:02 | 24 | 2022-01-05 03:10 | 2022-01-05 04:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106973 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10273745 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AHU-A1110-414- FILTER DIRTY |  | FM008 |  | 2022-03-22 09:37 | 2022-03-22 10:37 | 2022-03-23 10:37 | 24 | 2022-03-22 09:45 | 2022-03-22 13:00 | 195 | 215 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11329957 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP4.MTB434.AHU414.SYSALM.DP1 / |  | FM008 |  | 2022-12-30 14:47 | 2022-12-30 15:47 | 2022-12-31 15:47 | 24 | 2022-12-30 14:55 | 2022-12-30 17:00 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-9967074 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY; AHU-A1110-414 – T4-09-04 |  | FM008 |  | 2022-01-03 00:28 | 2022-01-03 01:28 | 2022-01-04 01:28 | 24 | 2022-01-03 00:35 | 2022-01-03 02:00 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10929555 | ASD-MTB-FOF011-AHU027 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1110-414 – T4-09-04 |  | FM008 |  | 2022-08-10 00:08 | 2022-08-10 01:08 | 2022-08-11 01:08 | 24 | 2022-08-10 00:15 | 2022-08-10 03:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10262526 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | FILTER DIRTY- T4-09-04 |  | FM008 |  | 2022-03-19 19:04 | 2022-03-19 20:04 | 2022-03-20 20:04 | 24 | 2022-03-19 19:10 | 2022-03-19 20:25 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2022-10777565 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AHU-A1110-420 – DP1 FILTER ALARM – T4-09-04 |  | FM008 |  | 2022-06-26 07:11 | 2022-06-26 08:11 | 2022-06-27 08:11 | 24 | 2022-06-26 07:20 | 2022-06-26 11:30 | 250 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11157631 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AHU-A1110-420-DUCT INSULATION DAMAGED-T4-09-04 |  | FM008 |  | 2022-11-02 10:04 | 2022-11-02 11:04 | 2022-11-03 11:04 | 24 | 2022-11-02 10:10 | 2022-11-02 12:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 87807 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11230601 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | SUPPLY CHILLED WATER LINE INSULATION DAMAGED -T4-09-04 |  | FM008 |  | 2022-11-29 19:18 | 2022-11-29 20:18 | 2022-11-30 20:18 | 24 | 2022-11-29 19:30 | 2022-11-29 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11298232 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT (A1110-420) -COOLING COIL DIRTY - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011.T4-09-04 |  | FM008 |  | 2022-12-21 22:16 | 2022-12-21 23:16 | 2022-12-22 23:16 | 24 | 2022-12-21 22:20 | 2022-12-22 01:30 | 190 | 570 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-11625189 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AHU-A1110-420-FILTER DIRTY--MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-04-09 07:28 | 2023-04-09 08:28 | 2023-04-10 08:28 | 24 | 2023-04-09 07:35 | 2023-04-09 10:38 | 183 | 181 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12495635 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | SUPPLY BLOWER BEARING NOISY |  | FM008 |  | 2023-12-24 10:10 | 2023-12-24 11:10 | 2023-12-25 11:10 | 24 | 2023-12-24 10:15 | 2023-12-24 14:15 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68060 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11041467 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-09-04 |  | FM008 |  | 2022-09-24 06:59 | 2022-09-24 07:59 | 2022-09-25 07:59 | 24 | 2022-09-24 07:05 | 2022-09-24 08:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11259953 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AHU-A1110-420 -DP1- FILTER ALARM – T4-09-04 |  | FM008 |  | 2022-12-11 13:38 | 2022-12-11 14:38 | 2022-12-12 14:38 | 24 | 2022-12-11 13:47 | 2022-12-11 16:30 | 163 | 321 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11480018 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARM , AHU-A1110-420 , T4-09-04 |  | FM008 |  | 2023-02-24 07:07 | 2023-02-24 08:07 | 2023-02-25 08:07 | 24 | 2023-02-24 07:15 | 2023-02-24 08:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11935198 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AC NOT WORKING KFC SN1030 |  | FM008 |  | 2023-06-30 03:12 | 2023-06-30 04:12 | 2023-07-01 04:12 | 24 | 2023-06-30 03:20 | 2023-06-30 06:00 | 160 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | SP0029 | Pilakal, Sathyanarayanan | N - - - |  | Voice Communication
| CM-2023-11950301 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-09-04 |  | FM008 |  | 2023-07-05 18:55 | 2023-07-05 19:55 | 2023-07-06 19:55 | 24 | 2023-07-05 19:02 | 2023-07-05 22:35 | 213 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12088616 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS-PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP4.MTB446.AHU420.SYSALM.DP3 / MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-08-14 10:19 | 2023-08-14 11:19 | 2023-08-15 11:19 | 24 | 2023-08-14 10:25 | 2023-08-14 15:35 | 310 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12209857 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | FILTER DIRTY– (AHU-A1110-420) – T4 08 04 |  | FM008 |  | 2023-09-22 19:50 | 2023-09-22 20:50 | 2023-09-23 20:50 | 24 | 2023-09-22 19:55 | 2023-09-22 23:40 | 225 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11842170 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AC IS TOO COLD -SN-1030- BOH KITCHEN AREA --RETAIL SOUTH NODE |  | FM008 |  | 2023-06-03 21:31 | 2023-06-03 22:31 | 2023-06-04 22:31 | 24 | 2023-06-03 21:40 | 2023-06-03 23:40 | 120 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 89127 |  |  | SP0029 | Pilakal, Sathyanarayanan | N - - - |  | Voice Communication
| CM-2023-11932883 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AC TOO HOT SN1030 FOOD MARKET KFC |  | FM008 |  | 2023-06-29 00:21 | 2023-06-29 01:21 | 2023-06-30 01:21 | 24 | 2023-06-29 00:30 | 2023-06-29 04:30 | 240 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | SP0029 | Pilakal, Sathyanarayanan | N - - - |  | Voice Communication
| CM-2023-12303878 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AHU MOTOR TEMPERATURE HIGH - AIR HANDLING UNIT 045 (TAG NO:AHU-A1110-432)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-10-21 13:20 | 2023-10-21 14:20 | 2023-10-22 14:20 | 24 | 2023-10-21 13:30 | 2023-10-21 18:35 | 305 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMPERATURE GAUGE FAULTY | RECTIFIED/REPLACED | 119320 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2022-10653720 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-05-13 14:55 | 2022-05-13 15:55 | 2022-05-14 15:55 | 24 | 2022-05-13 15:00 | 2022-05-13 17:40 | 160 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11289707 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 033-SUPPLY AND RETURN FAN-V-BELT DAMAGE-AHU-A1110-420,-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-12-22 02:20 | 2022-12-22 03:20 | 2022-12-23 03:20 | 24 | 2022-12-22 02:30 | 2022-12-22 05:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-9963316 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | FILTER IS DIRTY IN T4-09-04 |  | FM008 |  | 2022-01-02 12:10 | 2022-01-02 13:10 | 2022-01-03 13:10 | 24 | 2022-01-02 12:15 | 2022-01-02 13:30 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | BMS
| CM-2022-10910608 | ASD-MTB-FOF011-AHU033 | AIR HANDLING UNIT-05 | AHU-A1110-420 T4-09-04 SUPPLY & RETURN V BELT DAMAGED |  | FM008 |  | 2022-08-02 10:06 | 2022-08-02 11:06 | 2022-08-03 11:06 | 24 | 2022-08-02 10:15 | 2022-08-02 12:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 76858 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10726800 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – T4-09-04 AIR HANDLING UNIT 037 (TAG NO:AHU-A1110-424)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-06-05 20:44 | 2022-06-05 21:44 | 2022-06-06 21:44 | 24 | 2022-06-05 20:50 | 2022-06-05 22:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 17154 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11353177 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP2 & DP3 – FILTER ALARM - AHU-A1110-424 – T4-09-04 |  | FM008 |  | 2023-01-07 02:22 | 2023-01-07 03:22 | 2023-01-08 03:22 | 24 | 2023-01-07 02:30 | 2023-01-07 04:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11406347 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU-A1110-424- DP1 FILTER ALARM |  | FM008 |  | 2023-01-28 12:46 | 2023-01-28 13:46 | 2023-01-29 13:46 | 24 | 2023-01-28 12:55 | 2023-01-28 14:45 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 94954 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11772554 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-05-07 13:41 | 2023-05-07 14:41 | 2023-05-08 14:41 | 24 | 2023-05-07 13:47 | 2023-05-07 16:30 | 163 | 366 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12275527 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | COOLING FAN FAULT - LCC A1110-424 – T4 11 03 |  | FM008 |  | 2023-10-09 18:58 | 2023-10-09 19:58 | 2023-10-10 19:58 | 24 | 2023-10-09 19:05 | 2023-10-10 01:00 | 355 | 355 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 132112 | 87807 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2022-11045056 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-09-25 11:06 | 2022-09-25 12:06 | 2022-09-26 12:06 | 24 | 2022-09-25 11:15 | 2022-09-25 17:00 | 345 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11093915 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU-A1110-424 – AHU INSIDE LIGHT NOT WORKING – T4-09-04 |  | FM008 |  | 2022-10-09 20:50 | 2022-10-09 21:50 | 2022-10-10 21:50 | 24 | 2022-10-09 21:00 | 2022-10-09 22:30 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11263798 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-424 – T4-09-04 |  | FM008 |  | 2022-12-14 00:17 | 2022-12-14 01:17 | 2022-12-15 01:17 | 24 | 2022-12-14 00:25 | 2022-12-14 02:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12044108 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-424 – T4-09-04 |  | FM008 |  | 2023-08-03 22:10 | 2023-08-03 23:10 | 2023-08-04 23:10 | 24 | 2023-08-03 22:20 | 2023-08-03 23:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106973 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-12232839 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS T4-09-04 (AHU-A1110-424) |  | FM008 |  | 2023-09-30 11:53 | 2023-09-30 12:53 | 2023-10-01 12:53 | 24 | 2023-09-30 12:00 | 2023-09-30 18:05 | 365 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12255322 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | BELT DAMAGED |  | FM008 |  | 2023-10-06 08:59 | 2023-10-06 09:59 | 2023-10-07 09:59 | 24 | 2023-10-06 09:05 | 2023-10-06 17:25 | 500 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11624229 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU-A1110-424 RELIEF MOTOR FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2023-04-08 12:30 | 2023-04-08 13:30 | 2023-04-09 13:30 | 24 | 2023-04-08 12:39 | 2023-04-08 14:07 | 88 | 176 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68485 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11901873 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-424 – T4-09-04 |  | FM008 |  | 2023-06-22 07:21 | 2023-06-22 08:21 | 2023-06-23 08:21 | 24 | 2023-06-22 07:30 | 2023-06-22 10:40 | 190 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12088638 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU-A1110-424--FILTER DIRTY- T4-09-04- |  | FM008 |  | 2023-08-14 11:11 | 2023-08-14 12:11 | 2023-08-15 12:11 | 24 | 2023-08-14 11:15 | 2023-08-14 14:30 | 195 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12649825 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2024-02-13 09:56 | 2024-02-13 10:56 | 2024-02-14 10:56 | 24 | 2024-02-13 10:01 | 2024-02-13 13:45 | 224 | 275 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2023-12280235 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED - AHU-A1110-424) - |  | FM008 |  | 2023-10-14 09:00 | 2023-10-14 10:00 | 2023-10-15 10:00 | 24 | 2023-10-14 09:05 | 2023-10-14 18:05 | 540 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12452794 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ASD-MTB-FOF011-AHU037(AHU-A1110-424) MECHANICAL ROOM T4-09-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP4.MTB424.AHU424.SYSALM.DP1 / |  | FM008 |  | 2023-12-09 14:46 | 2023-12-09 15:46 | 2023-12-10 15:46 | 24 | 2023-12-09 14:50 | 2023-12-09 22:45 | 475 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2022-10044530 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-424 |  | FM008 |  | 2022-01-13 11:43 | 2022-01-13 12:43 | 2022-01-14 12:43 | 24 | 2022-01-13 11:53 | 2022-01-13 12:53 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | E-mail
| CM-2022-10120704 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-424 T4-09-04 |  | FM008 |  | 2022-02-08 10:24 | 2022-02-08 11:24 | 2022-02-09 11:24 | 24 | 2022-02-08 10:33 | 2022-02-08 12:30 | 117 | 234 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 55709 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2022-10044697 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION IS DAMAGED |  | FM008 |  | 2022-01-14 05:01 | 2022-01-14 06:01 | 2022-01-15 06:01 | 24 | 2022-01-14 05:10 | 2022-01-14 06:15 | 65 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | BMS
| CM-2022-10917336 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY T4-09-04 |  | FM008 |  | 2022-08-09 00:14 | 2022-08-09 01:14 | 2022-08-10 01:14 | 24 | 2022-08-09 00:20 | 2022-08-09 03:35 | 195 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | BMS
| CM-2022-10929910 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU-A1110-424 - DUCT INSULATION DAMAGED T4-07-31 |  | FM008 |  | 2022-08-11 19:15 | 2022-08-11 20:15 | 2022-08-12 20:15 | 24 | 2022-08-11 19:20 | 2022-08-11 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 55709 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-11526085 | ASD-MTB-FOF011-AHU037 | AIR HANDLING UNIT-05 | AHU-A1110-424- DP 1 FILTER ALARM – T4-09-04 |  | FM008 |  | 2023-03-08 08:53 | 2023-03-08 09:53 | 2023-03-09 09:53 | 24 | 2023-03-08 09:00 | 2023-03-08 10:35 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 94954 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10106551 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM T4-09-04 AHU-A1110-428 |  | FM008 |  | 2022-02-02 20:01 | 2022-02-02 21:01 | 2022-02-03 21:01 | 24 | 2022-02-02 20:10 | 2022-02-02 22:10 | 120 | 265 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10124970 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AIR FILTER IS DIRTY - :AHU-A1110-428 - T4-09-04 |  | FM008 |  | 2022-02-12 13:55 | 2022-02-12 14:55 | 2022-02-13 14:55 | 24 | 2022-02-12 14:00 | 2022-02-12 15:30 | 90 | 270 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | E-mail
| CM-2022-10573780 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428-FILTER DIRTY |  | FM008 |  | 2022-04-19 00:18 | 2022-04-19 01:18 | 2022-04-20 01:18 | 24 | 2022-04-19 00:25 | 2022-04-19 02:20 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10669943 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428- DP 1 FILTER ALARM- |  | FM008 |  | 2022-05-19 10:44 | 2022-05-19 11:44 | 2022-05-20 11:44 | 24 | 2022-05-19 10:54 | 2022-05-19 14:15 | 201 | 156 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17154 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10728036 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428 – DP 3 FILTER ALARM – T4-09-04 |  | FM008 |  | 2022-06-06 19:01 | 2022-06-06 20:01 | 2022-06-07 20:01 | 24 | 2022-06-06 19:10 | 2022-06-06 20:20 | 70 | 210 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17154 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10924545 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428-V BELT DAMAGED-T4-09-04 |  | FM008 |  | 2022-08-09 00:22 | 2022-08-09 01:22 | 2022-08-10 01:22 | 24 | 2022-08-09 00:30 | 2022-08-09 05:10 | 280 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95217 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-11004733 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-09-07 11:12 | 2022-09-07 12:12 | 2022-09-08 12:12 | 24 | 2022-09-07 11:20 | 2022-09-07 13:00 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11037655 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO WARM - SECURITY SCREENING AREA AFTER IMMIGRATION |  | FM008 |  | 2022-09-21 00:01 | 2022-09-21 01:01 | 2022-09-22 01:01 | 24 | 2022-09-21 00:11 | 2022-09-21 01:01 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  |  | BASHEER MOI | N - - - |  | Voice Communication
| CM-2023-11404297 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE EMIGRATION PASSPORT CONTROL AREA |  | FM008 |  | 2023-01-28 00:25 | 2023-01-28 01:25 | 2023-01-29 01:25 | 24 | 2023-01-28 00:30 | 2023-01-28 03:40 | 190 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 94954 |  |  | 101305 | Taalaibekova, Ms. Baktygul | N - - - |  | Voice Communication
| CM-2023-11735577 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | T2-11-41- AC IS TOO COLD- - |  | FM008 |  | 2023-04-29 08:37 | 2023-04-29 09:37 | 2023-04-30 09:37 | 24 | 2023-04-29 08:45 | 2023-04-29 12:10 | 205 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94953 | 87807 |  |  | CT15022 | MUJAHID | N - - - |  | Voice Communication
| CM-2023-11930874 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING AREA NEAR EMMIGRATION AC TOO HOT |  | FM008 |  | 2023-06-26 14:48 | 2023-06-26 15:48 | 2023-06-27 15:48 | 24 | 2023-06-26 14:55 | 2023-06-26 18:35 | 220 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | CT15022 | MUJAHID | N - - - |  | Voice Communication
| CM-2023-12127993 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING BUSINESS CLASS AC TOO COLD |  | FM008 |  | 2023-08-29 09:33 | 2023-08-29 10:33 | 2023-08-30 10:33 | 24 | 2023-08-29 09:40 | 2023-08-29 15:40 | 360 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2023-12158880 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE SCREENING CHECK POINT NEAR T2-11-24 |  | FM008 |  | 2023-09-07 07:08 | 2023-09-07 08:08 | 2023-09-08 08:08 | 24 | 2023-09-07 07:15 | 2023-09-07 11:15 | 240 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 106972 | 17053 |  |  | CT14362 | Isaac | N - - - |  | Voice Communication
| CM-2023-12423755 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | -AC TOO WARM NEAR DEPARTURE T2-10-41 SCREENING AREA |  | FM008 |  | 2023-12-01 00:38 | 2023-12-01 01:38 | 2023-12-02 01:38 | 24 | 2023-12-01 00:45 | 2023-12-01 04:45 | 240 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 77406 | 87807 |  |  | CT13297 | KAMOGA | N - - - |  | Voice Communication
| CM-2024-12540914 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -T4-09-04 |  | FM008 |  | 2024-01-07 10:41 | 2024-01-07 11:41 | 2024-01-08 11:41 | 24 | 2024-01-07 10:45 | 2024-01-07 14:55 | 250 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2024-12670352 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT MOI SCREENING AREA NEAR T2-11-40 |  | FM008 |  | 2024-02-22 15:10 | 2024-02-22 16:10 | 2024-02-23 16:10 | 24 | 2024-02-22 15:15 | 2024-02-22 21:00 | 345 | 33 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 138627 | 17053 |  |  |  | DEYA | N - - - |  | Voice Communication
| CM-2024-12692166 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC NOT WORKING(TOO HOT) IN DEPARTURE SCREENING AREA |  | FM008 |  | 2024-03-01 03:53 | 2024-03-01 04:53 | 2024-03-02 04:53 | 24 | 2024-03-01 04:00 | 2024-03-01 05:15 | 75 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 105536 | Ameer, Mr. Abdul | N - - - |  | Voice Communication
| CM-2022-11040784 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE IMMIGRATION SCREENING AREA |  | FM008 |  | 2022-09-21 23:19 | 2022-09-22 00:19 | 2022-09-23 00:19 | 24 | 2022-09-21 23:25 | 2022-09-21 23:55 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | MOI | BASHIR | N - - - |  | Voice Communication
| CM-2022-11104695 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE PASSENGER SCREENING |  | FM008 |  | 2022-10-15 10:57 | 2022-10-15 11:57 | 2022-10-16 11:57 | 24 | 2022-10-15 11:05 | 2022-10-15 12:49 | 104 | 64 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | GSS8985 | ANIEST | N - - - |  | Voice Communication
| CM-2023-11763650 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DEPARTURE EMMIGRATION AREA AC TOO COLD |  | FM008 |  | 2023-05-05 02:08 | 2023-05-05 03:08 | 2023-05-06 03:08 | 24 | 2023-05-05 02:15 | 2023-05-05 04:15 | 120 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | COOLING COIL DAMAGE | REPLACED/REPAIRED THE COOLING COIL | 106972 | 87807 |  |  | 51682 | Marquez, Ms. Carolyn Estil | N - - - |  | Voice Communication
| CM-2023-11779737 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DEPARTURE IMMIGRATION E-GATE AREA - AC IS TOO HOT |  | FM008 |  | 2023-05-10 23:13 | 2023-05-11 00:13 | 2023-05-12 00:13 | 24 | 2023-05-10 23:20 | 2023-05-11 01:00 | 100 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N |  |  |  | 94953 | 106972 |  |  | CT13734 | JOSEPH | N - - - |  | Voice Communication
| CM-2023-11885503 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2023-06-16 09:14 | 2023-06-16 10:14 | 2023-06-17 10:14 | 24 | 2023-06-16 09:20 | 2023-06-16 16:10 | 410 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11886015 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC NOT WORKING -DEPARTURE SCREENING AREA |  | FM008 |  | 2023-06-17 23:01 | 2023-06-18 00:01 | 2023-06-19 00:01 | 24 | 2023-06-17 23:10 | 2023-06-18 02:40 | 210 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 87807 |  |  | CT13734 | JOSEPH | N - - - |  | Voice Communication
| CM-2023-11936325 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE IMMIGRATION AREA, SCREENING AREA |  | FM008 |  | 2023-06-30 23:17 | 2023-07-01 00:17 | 2023-07-02 00:17 | 24 | 2023-06-30 23:25 | 2023-07-01 01:02 | 97 | 67 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 94954 | 17053 |  |  | CT14263 | ROGERS NGETICH | N - - - |  | Voice Communication
| CM-2023-11998155 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | NEAR T2-11-24 – DEPARTURE IMMIGRATION AREA – LANE 15 & 16 AREA – AC TOO HOT |  | FM008 |  | 2023-07-22 07:09 | 2023-07-22 08:09 | 2023-07-23 08:09 | 24 | 2023-07-22 07:15 | 2023-07-22 13:30 | 375 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | CT13735 | LAWRENCE | N - - - |  | Voice Communication
| CM-2023-12013881 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT- IN DEPARTURE IMMIGRATION AREA |  | FM008 |  | 2023-07-27 07:10 | 2023-07-27 08:10 | 2023-07-28 08:10 | 24 | 2023-07-27 07:15 | 2023-07-27 12:35 | 320 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  |  | SAOUD-MOI | N - - - |  | Voice Communication
| CM-2023-12064214 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-428 – T4-09-04 |  | FM008 |  | 2023-08-09 13:52 | 2023-08-09 14:52 | 2023-08-10 14:52 | 24 | 2023-08-09 14:00 | 2023-08-09 17:15 | 195 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-12067850 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT IN IMMIGRATION DEPARTURE AREA |  | FM008 |  | 2023-08-12 17:05 | 2023-08-12 18:05 | 2023-08-13 18:05 | 24 | 2023-08-12 17:10 | 2023-08-12 20:00 | 170 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 87807 |  |  |  | MOHAMAD-MOI | N - - - |  | Voice Communication
| CM-2023-12085465 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT -DEPARTURE SCREENING (CM-2023-04-2073) |  | FM008 |  | 2023-08-14 02:10 | 2023-08-14 03:10 | 2023-08-15 03:10 | 24 | 2023-08-14 02:20 | 2023-08-14 06:05 | 225 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 87807 | 17053 |  |  | CT13698 | BENON | - - - |  | Voice Communication
| CM-2023-12134599 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1110-428 – T4 09 04 |  | FM008 |  | 2023-08-31 05:32 | 2023-08-31 06:32 | 2023-09-01 06:32 | 24 | 2023-08-31 05:40 | 2023-08-31 06:45 | 65 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2023-12231413 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED -T4-09-04 |  | FM008 |  | 2023-09-28 08:12 | 2023-09-28 09:12 | 2023-09-29 09:12 | 24 | 2023-09-28 08:20 | 2023-09-28 10:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106914 | 87807 |  |  | FM7396 | Chowdhury, Mr. Biswajit | N - - - |  | Voice Communication
| CM-2023-12495419 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT NEAR DOOR # T2-11-41 DEPARTURE SCREENING |  | FM008 |  | 2023-12-23 17:29 | 2023-12-23 18:29 | 2023-12-24 18:29 | 24 | 2023-12-23 17:35 | 2023-12-23 22:10 | 275 | 51 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | CT13698 | BENON | N - - - |  | Voice Communication
| CM-2023-12511709 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN ROW 4 COUNTER 11 |  | FM008 |  | 2023-12-28 09:51 | 2023-12-28 10:51 | 2023-12-29 10:51 | 24 | 2023-12-28 09:55 | 2023-12-28 13:40 | 225 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 121959 | 17053 |  |  | 119707 | Akhmet, Ms. Tangsholpan | N - - - |  | Voice Communication
| CM-2022-10917290 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | FILTER ALARM - AHU-A1110-428 – T4-09-04 |  | FM008 |  | 2022-08-08 19:07 | 2022-08-08 20:07 | 2022-08-09 20:07 | 24 | 2022-08-08 19:15 | 2022-08-08 22:00 | 165 | 260 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | BMS
| CM-2022-10951404 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | T2-10-20 & AROUND IMMIGRATION AREA – AC NOT WORKING |  | FM008 |  | 2022-08-15 14:07 | 2022-08-15 15:07 | 2022-08-16 15:07 | 24 | 2022-08-15 14:10 | 2022-08-15 15:25 | 75 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 55709 |  |  | 119741 | Firouse, Ms. Shanuli Ridhwana | N - - - |  | Voice Communication
| CM-2022-11040748 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE IMMIGRATION COUNTER AREA |  | FM008 |  | 2022-09-21 16:34 | 2022-09-21 17:34 | 2022-09-22 17:34 | 24 | 2022-09-21 16:40 | 2022-09-21 18:00 | 80 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  |  | NAWAD | N - - - |  | Voice Communication
| CM-2022-11043389 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-09-25 10:06 | 2022-09-25 11:06 | 2022-09-26 11:06 | 24 | 2022-09-25 10:10 | 2022-09-25 13:45 | 215 | 215 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11188930 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM AHU-A1110-428) |  | FM008 |  | 2022-11-14 11:28 | 2022-11-14 12:28 | 2022-11-15 12:28 | 24 | 2022-11-14 11:38 | 2022-11-14 13:05 | 87 | 174 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11230634 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -AHU-A1110-428 |  | FM008 |  | 2022-11-30 00:06 | 2022-11-30 01:06 | 2022-12-01 01:06 | 24 | 2022-11-30 00:15 | 2022-11-30 03:45 | 210 | 420 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 124475 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11511964 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428 – DP1 FILTER ALARM-- |  | FM008 |  | 2023-03-05 10:07 | 2023-03-05 11:07 | 2023-03-06 11:07 | 24 | 2023-03-05 10:15 | 2023-03-05 11:15 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11514439 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | T2-11-41 AC NOT WORKING/HOT |  | FM008 |  | 2023-03-07 06:58 | 2023-03-07 07:58 | 2023-03-08 07:58 | 24 | 2023-03-07 07:05 | 2023-03-07 08:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  |  | MOI SALMAN | N - - - |  | Voice Communication
| CM-2023-11630712 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING |  | FM008 |  | 2023-04-08 14:01 | 2023-04-08 15:01 | 2023-04-09 15:01 | 24 | 2023-04-08 14:11 | 2023-04-08 15:40 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106972 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11763155 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-05-03 00:08 | 2023-05-03 01:08 | 2023-05-04 01:08 | 24 | 2023-05-03 00:15 | 2023-05-03 01:43 | 88 | 176 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11804640 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE EMIGRATION, INFO DESK AREA |  | FM008 |  | 2023-05-20 03:29 | 2023-05-20 04:29 | 2023-05-21 04:29 | 24 | 2023-05-20 03:35 | 2023-05-20 05:45 | 130 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | T26780 | Laila, Ms. Lahlimi | N - - - |  | Voice Communication
| CM-2023-11841223 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-06-01 09:17 | 2023-06-01 10:17 | 2023-06-02 10:17 | 24 | 2023-06-01 09:20 | 2023-06-01 12:50 | 210 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12097677 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT IN DEPARTURE SCREENING CHECK POINT, NEAR T2-10-41 |  | FM008 |  | 2023-08-17 17:15 | 2023-08-17 18:15 | 2023-08-18 18:15 | 24 | 2023-08-17 17:20 | 2023-08-17 18:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | CT14362 | Isaac | N - - - |  | Voice Communication
| CM-2023-12189479 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | MTB, LEVEL 2, DEPARTURE IMMIGRATION COUNTER AREA - AC TEMPERATURE IS TOO HOT |  | FM008 |  | 2023-09-16 13:28 | 2023-09-16 14:28 | 2023-09-17 14:28 | 24 | 2023-09-16 13:35 | 2023-09-16 16:40 | 185 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 94954 | 87807 |  |  | 17274 | Partonezhad, Ms. Zahra Abbas | N - - - |  | Voice Communication
| CM-2023-12232769 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT (NOT WORKING) - MOI EXIT AREA NEAR T2-S27 |  | FM008 |  | 2023-09-30 08:19 | 2023-09-30 09:19 | 2023-10-01 09:19 | 24 | 2023-09-30 08:25 | 2023-09-30 09:35 | 70 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 87807 |  |  | CT18484 | NELSON | N - - - |  | Voice Communication
| CM-2023-12245877 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | ABNORMAL SOUND COMING FROM SUPPLY SIDE BEARING - AHU-A1110-428 – T4-09-04 |  | FM008 |  | 2023-10-02 13:28 | 2023-10-02 14:28 | 2023-10-03 14:28 | 24 | 2023-10-02 13:35 | 2023-10-02 16:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2024-12748961 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DEPARTURE SCREENING AFTER PASSPORT CONTROL AC TOO HOT |  | FM008 |  | 2024-03-18 21:24 | 2024-03-18 22:24 | 2024-03-19 22:24 | 24 | 2024-03-18 21:30 | 2024-03-18 23:05 | 95 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 95217 |  |  | CT16373 | ERIC | N - - - |  | Voice Communication
| CM-2024-12705154 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1110-428 - MECHANICAL ROOM T4-09-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP4.MTB428.AHU428.SYSALM.DP1 / |  | FM008 |  | 2024-03-08 02:41 | 2024-03-08 03:41 | 2024-03-09 03:41 | 24 | 2024-03-08 02:50 | 2024-03-08 05:50 | 180 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12825801 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP2 FINAL FILTER STATUS, AHU-A1110-428, MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2024-04-14 15:21 | 2024-04-14 16:21 | 2024-04-15 16:21 | 24 | 2024-04-14 15:25 | 2024-04-14 18:15 | 170 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12379377 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD |  | FM008 |  | 2023-11-15 14:49 | 2023-11-15 15:49 | 2023-11-16 15:49 | 24 | 2023-11-15 14:55 | 2023-11-15 16:45 | 110 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 95216 | 87807 |  |  | CT13907 | DOUGLAS | N - - - |  | Voice Communication
| CM-2024-12683491 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT , T2-10-13 |  | FM008 |  | 2024-02-26 13:44 | 2024-02-26 14:44 | 2024-02-27 14:44 | 24 | 2024-02-26 13:50 | 2024-02-26 18:40 | 290 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | MOI CAPTAIN | NASSER | N - - - |  | Voice Communication
| CM-2022-10044365 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428 – FILTER DIRTY – T4-09-04 |  | FM008 |  | 2022-01-12 11:56 | 2022-01-12 12:56 | 2022-01-13 12:56 | 24 | 2022-01-12 12:05 | 2022-01-12 17:50 | 345 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10251785 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TEMPERATURE IS TOO HOT – MTB, LEVEL 2, AFTER DEPARTURE IMMIGRATION, MOI SCREENING AREA |  | FM008 |  | 2022-03-15 22:38 | 2022-03-15 23:38 | 2022-03-16 23:38 | 24 | 2022-03-15 22:45 | 2022-03-15 23:35 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 94954 | 87807 |  |  | CT13752 | PHILEMON | N - - - |  | Voice Communication
| CM-2022-10307509 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE IMMIGRATION COUNTER |  | FM008 |  | 2022-03-29 08:38 | 2022-03-29 09:38 | 2022-03-30 09:38 | 24 | 2022-03-29 08:45 | 2022-03-29 10:10 | 85 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | 63976 | Escobido, Mr. Earl Joseph Chiong | N - - - |  | Voice Communication
| CM-2022-10351776 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428 DP1 FILTER ALARM-T4-09-04-- |  | FM008 |  | 2022-04-12 10:06 | 2022-04-12 11:06 | 2022-04-13 11:06 | 24 | 2022-04-12 10:15 | 2022-04-12 16:15 | 360 | 230 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10611329 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD – DEPARTURE SCREENING (BUSINESS CLASS AREA) |  | FM008 |  | 2022-04-30 09:23 | 2022-04-30 10:23 | 2022-05-01 10:23 | 24 | 2022-04-30 09:30 | 2022-04-30 10:15 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | CT13551 | Oroko Reuben | N - - - |  | Voice Communication
| CM-2022-10627609 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE SCREENING BEHIND IMMIGRATION COUNTER NEAR T2-10-40 |  | FM008 |  | 2022-05-08 23:01 | 2022-05-09 00:01 | 2022-05-10 00:01 | 24 | 2022-05-08 23:10 | 2022-05-08 23:55 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | CT13537 | GITONGA | N - - - |  | Voice Communication
| CM-2022-10696464 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FILER ALARM - AHU-A1110-428 - T4-09-04 |  | FM008 |  | 2022-05-26 19:11 | 2022-05-26 20:11 | 2022-05-27 20:11 | 24 | 2022-05-26 19:20 | 2022-05-26 21:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11159210 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO COLD |  | FM008 |  | 2022-11-02 00:21 | 2022-11-02 01:21 | 2022-11-03 01:21 | 24 | 2022-11-02 00:25 | 2022-11-02 01:10 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | MOI | MOHAMMED | N - - - |  | Voice Communication
| CM-2022-11190515 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED - AHU-A1110-428)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-11-14 12:01 | 2022-11-14 13:01 | 2022-11-15 13:01 | 24 | 2022-11-14 12:10 | 2022-11-14 16:00 | 230 | 460 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17336 | 87807 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2022-11270409 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | CHILL WATER LINE INSULATION DAMAGED – T4-09-04 |  | FM008 |  | 2022-12-13 01:13 | 2022-12-13 02:13 | 2022-12-14 02:13 | 24 | 2022-12-13 01:20 | 2022-12-13 04:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-11681547 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-04-18 00:06 | 2023-04-18 01:06 | 2023-04-19 01:06 | 24 | 2023-04-18 00:12 | 2023-04-18 05:50 | 338 | 278 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-10258856 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AC TOO WARM - DEPARTURE SCREEN AREA NEAR IMMIGRATION |  | FM008 |  | 2022-03-18 15:51 | 2022-03-18 16:51 | 2022-03-19 16:51 | 24 | 2022-03-18 16:00 | 2022-03-18 19:45 | 225 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 87807 |  |  | 114134 | Mascarenhas, Mr. Rekesh John | N - - - |  | Voice Communication
| CM-2023-11406348 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428- DP1 FILTER ALARM |  | FM008 |  | 2023-01-28 12:48 | 2023-01-28 13:48 | 2023-01-29 13:48 | 24 | 2023-01-28 12:58 | 2023-01-28 16:45 | 227 | 352 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 94954 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11545623 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU-A1110-428 – DP 2 FILTER ALARM – T4-09-04 |  | FM008 |  | 2023-03-09 08:53 | 2023-03-09 09:53 | 2023-03-10 09:53 | 24 | 2023-03-09 09:00 | 2023-03-09 11:00 | 120 | 165 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12166494 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | DP2 RELIEF FILTER STATUS |  | FM008 |  | 2023-09-09 22:39 | 2023-09-09 23:39 | 2023-09-10 23:39 | 24 | 2023-09-09 22:45 | 2023-09-10 02:02 | 197 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12231169 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | ABNORMAL NOISE FROM RELIEF SIDE |  | FM008 |  | 2023-09-27 13:01 | 2023-09-27 14:01 | 2023-09-28 14:01 | 24 | 2023-09-27 13:10 | 2023-09-27 16:10 | 180 | 485 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68060 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12250627 | ASD-MTB-FOF011-AHU041 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - AHU-A1110-428 – T4-11-03 |  | FM008 |  | 2023-10-03 13:46 | 2023-10-03 14:46 | 2023-10-04 14:46 | 24 | 2023-10-03 13:50 | 2023-10-03 18:00 | 250 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 133396 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10674411 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD-CHECK IN ROW#04 & 05 |  | FM008 |  | 2022-05-18 08:37 | 2022-05-18 09:37 | 2022-05-19 09:37 | 24 | 2022-05-18 08:45 | 2022-05-18 11:30 | 165 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95217 | 55709 |  |  | 62147 | Chopra, Mr. Sunil | N - - - |  | Voice Communication
| CM-2022-10723339 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -DEPARTURE ROW 3 AND 4 |  | FM008 |  | 2022-06-05 23:13 | 2022-06-06 00:13 | 2022-06-07 00:13 | 24 | 2022-06-05 23:20 | 2022-06-06 01:30 | 130 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | 91213 | Begum, Ms. Khatija | N - - - |  | Voice Communication
| CM-2022-10744640 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -DEPARTURE ROW 3 AND 4 |  | FM008 |  | 2022-06-12 22:00 | 2022-06-12 23:00 | 2022-06-13 23:00 | 24 | 2022-06-12 22:05 | 2022-06-12 23:00 | 55 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 87807 |  |  | 91213 | Begum, Ms. Khatija | N - - - |  | Voice Communication
| CM-2022-10931805 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED- T4-09-04 |  | FM008 |  | 2022-08-12 00:06 | 2022-08-12 01:06 | 2022-08-13 01:06 | 24 | 2022-08-12 00:15 | 2022-08-12 03:30 | 195 | 390 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11274669 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN HALL ROW 5 AC TOO COLD |  | FM008 |  | 2022-12-17 06:34 | 2022-12-17 07:34 | 2022-12-18 07:34 | 24 | 2022-12-17 06:43 | 2022-12-17 09:50 | 187 | 42 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | R11244 | Sassioui, Mr. Ayoub | N - - - |  | Voice Communication
| CM-2022-11304208 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -ROW 5 DEPARTURE AREA |  | FM008 |  | 2022-12-25 19:44 | 2022-12-25 20:44 | 2022-12-26 20:44 | 24 | 2022-12-25 19:50 | 2022-12-25 22:15 | 145 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | 119785 | Saidani, Ms. Emna | N - - - |  | Voice Communication
| CM-2022-11304239 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – IN ROW NO 5 (URGENT) |  | FM008 |  | 2022-12-26 01:03 | 2022-12-26 02:03 | 2022-12-27 02:03 | 24 | 2022-12-26 01:10 | 2022-12-26 01:55 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 106914 | 17053 |  |  | R15466 | Naithani, Mr. Vivek | N - - - |  | Voice Communication
| CM-2023-11699196 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | DEPARTURE ROW # 3 AND 4 AC TOO COLD |  | FM008 |  | 2023-04-26 19:11 | 2023-04-26 20:11 | 2023-04-27 20:11 | 24 | 2023-04-26 19:18 | 2023-04-26 23:10 | 232 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106972 | 87807 |  |  | 123356 | Bouya, Ms. Oumayma | N - - - |  | Voice Communication
| CM-2023-11801401 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW NO 4 AC TOO COLD |  | FM008 |  | 2023-05-16 15:37 | 2023-05-16 16:37 | 2023-05-17 16:37 | 24 | 2023-05-16 15:43 | 2023-05-16 18:00 | 137 | 62 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | R13759 | El Ouasif, Ms. Safaa | N - - - |  | Voice Communication
| CM-2023-11801649 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4 COUNTER 3 AC TOO COLD |  | FM008 |  | 2023-05-17 17:17 | 2023-05-17 18:17 | 2023-05-18 18:17 | 24 | 2023-05-17 17:25 | 2023-05-17 20:00 | 155 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11818580 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | MTB, LEVEL 2, CHECK-IN ROW 4 COUNTER 13 – AC TEMPERATURE IS TOO COLD |  | FM008 |  | 2023-05-23 03:52 | 2023-05-23 04:52 | 2023-05-24 04:52 | 24 | 2023-05-23 04:00 | 2023-05-23 06:40 | 160 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 94954 | 17053 |  |  | 123356 | Bouya, Ms. Oumayma | N - - - |  | Voice Communication
| CM-2023-11884501 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN COUNTER 4 ROW 4 |  | FM008 |  | 2023-06-13 19:41 | 2023-06-13 20:41 | 2023-06-14 20:41 | 24 | 2023-06-13 19:50 | 2023-06-13 23:55 | 245 | 37 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 68485 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11898905 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – CHECK IN ROW NO 4 COUNTER 2 AREA |  | FM008 |  | 2023-06-20 22:21 | 2023-06-20 23:21 | 2023-06-21 23:21 | 24 | 2023-06-20 22:25 | 2023-06-20 23:55 | 90 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 133396 |  |  | 113748 | Mennany, Ms. Khawla | N - - - |  | Voice Communication
| CM-2023-11910675 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – DEPARTURE COUNTER ROW NO 4 |  | FM008 |  | 2023-06-22 04:17 | 2023-06-22 05:17 | 2023-06-23 05:17 | 24 | 2023-06-22 04:20 | 2023-06-22 06:30 | 130 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | E-mail
| CM-2023-11917375 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC IS TOO COLD -DEPARTIRE ROW 4 -COUNTER 4 -T2-14-01 (DEPARTURES HALL) |  | FM008 |  | 2023-06-24 08:39 | 2023-06-24 09:39 | 2023-06-25 09:39 | 24 | 2023-06-24 08:45 | 2023-06-24 14:00 | 315 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CHILLED WATER VALVE NOT WORKING | REPAIR/REPLACE | 17336 | 17053 |  |  | 119777 | Sfar, Ms. Rihab | N - - - |  | Voice Communication
| CM-2023-11934257 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD GATE NO 1 INFORM DESK DEP NEAR ROW NO 4 INFOR |  | FM008 |  | 2023-06-28 01:13 | 2023-06-28 02:13 | 2023-06-29 02:13 | 24 | 2023-06-28 01:20 | 2023-06-28 03:35 | 135 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | R10753 | Abdouli, Ms. Hiba | N - - - |  | Voice Communication
| CM-2023-12198793 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 4 COUNTER 4 AND 5 |  | FM008 |  | 2023-09-18 02:17 | 2023-09-18 03:17 | 2023-09-19 03:17 | 24 | 2023-09-18 02:25 | 2023-09-18 06:40 | 255 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | R10527 | Ishraq, Mr. Mohsin | N - - - |  | Voice Communication
| CM-2023-12341230 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AHU -A1110-430 T4-09-04 AIR RELEASE UNION CRACKED |  | FM008 |  | 2023-11-01 12:50 | 2023-11-01 13:50 | 2023-11-02 13:50 | 24 | 2023-11-01 12:59 | 2023-11-01 14:30 | 91 | 273 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 89127 | 87807 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-12345617 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 4 1ST COUNTER AC TOO COLD |  | FM008 |  | 2023-11-04 02:02 | 2023-11-04 03:02 | 2023-11-05 03:02 | 24 | 2023-11-04 02:07 | 2023-11-04 04:45 | 158 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | 105281 | Dombe, Ms. Diana Natasha Ndaiziveyi | N - - - |  | Voice Communication
| CM-2023-12361851 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #4 COUNTER AREA |  | FM008 |  | 2023-11-07 02:04 | 2023-11-07 03:04 | 2023-11-08 03:04 | 24 | 2023-11-07 02:10 | 2023-11-07 06:10 | 240 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | R13424 | Moumen, Mr. Abdelaziz | N - - - |  | Voice Communication
| CM-2023-12363846 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 4 COUNTER 13 |  | FM008 |  | 2023-11-07 18:40 | 2023-11-07 19:40 | 2023-11-08 19:40 | 24 | 2023-11-07 18:45 | 2023-11-07 22:40 | 235 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | R12455 | Adil, Mr. Ouass | N - - - |  | Voice Communication
| CM-2023-12385933 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK-IN ROW 4 COUNTER 1 |  | FM008 |  | 2023-11-18 08:19 | 2023-11-18 09:19 | 2023-11-19 09:19 | 24 | 2023-11-18 08:25 | 2023-11-18 09:35 | 70 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2023-12407292 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC IS TOO COLD -DEPARTURE CHECK IN ROW 4 -COUNTER 5-12 |  | FM008 |  | 2023-11-24 11:10 | 2023-11-24 12:10 | 2023-11-25 12:10 | 24 | 2023-11-24 11:15 | 2023-11-24 16:20 | 305 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | R13759 | El Ouasif, Ms. Safaa | N - - - |  | Voice Communication
| CM-2023-12456244 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD , ROW-4, COUNTER- 6 , DEPARTURE LVL |  | FM008 |  | 2023-12-09 09:21 | 2023-12-09 10:21 | 2023-12-10 10:21 | 24 | 2023-12-09 09:30 | 2023-12-09 12:50 | 200 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 137955 | Ghedifi, Ms. Ikram | N - - - |  | Voice Communication
| CM-2023-12485455 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECK IN ROW NO 4 |  | FM008 |  | 2023-12-17 11:36 | 2023-12-17 12:36 | 2023-12-18 12:36 | 24 | 2023-12-17 11:45 | 2023-12-17 14:45 | 180 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | R13773 | Firouchane, Ms. Salma | N - - - |  | Voice Communication
| CM-2023-12488545 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECK IN COUNTER ROW NO 4 |  | FM008 |  | 2023-12-19 23:38 | 2023-12-20 00:38 | 2023-12-21 00:38 | 24 | 2023-12-19 23:45 | 2023-12-20 02:00 | 135 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 106914 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12552907 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT IN ROW-4, COUNTER-8 |  | FM008 |  | 2024-01-10 23:07 | 2024-01-11 00:07 | 2024-01-12 00:07 | 24 | 2024-01-10 23:10 | 2024-01-11 01:02 | 112 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 136942 | Kharbouche, Mr. Mohamed Yassir | N - - - |  | Voice Communication
| CM-2024-12575920 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE ROW 4 COUNTER 5 |  | FM008 |  | 2024-01-20 11:42 | 2024-01-20 12:42 | 2024-01-21 12:42 | 24 | 2024-01-20 11:50 | 2024-01-20 16:00 | 250 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 138627 | 17053 |  |  | 138242 | Boucena, Ms. Narimane | N - - - |  | Voice Communication
| CM-2024-12592423 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | A/C IS TOO HOT AT ROW 04 |  | FM008 |  | 2024-01-25 16:42 | 2024-01-25 17:42 | 2024-01-26 17:42 | 24 | 2024-01-25 16:50 | 2024-01-25 21:00 | 250 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12652624 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE CHECK IN ROW 4 ALL AREA |  | FM008 |  | 2024-02-16 12:25 | 2024-02-16 13:25 | 2024-02-17 13:25 | 24 | 2024-02-16 12:30 | 2024-02-16 16:35 | 245 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12655144 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING ROW 5 DEPARTURE AREA |  | FM008 |  | 2024-02-17 15:51 | 2024-02-17 16:51 | 2024-02-18 16:51 | 24 | 2024-02-17 16:00 | 2024-02-17 17:50 | 110 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 87807 |  |  | 68060 | Ndiinu, Mr. George Njoroge | N - - - |  | Voice Communication
| CM-2024-12672566 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO WARM = CHECK IN ROW # 4 COUNTER # 1 |  | FM008 |  | 2024-02-22 05:37 | 2024-02-22 06:37 | 2024-02-23 06:37 | 24 | 2024-02-22 05:45 | 2024-02-22 06:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12712512 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT - MOST CHECK IN COUNTERS IN ROW 5 |  | FM008 |  | 2024-03-06 22:14 | 2024-03-06 23:14 | 2024-03-07 23:14 | 24 | 2024-03-06 22:19 | 2024-03-07 00:36 | 137 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12729553 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING AT ROW 05 |  | FM008 |  | 2024-03-12 15:34 | 2024-03-12 16:34 | 2024-03-13 16:34 | 24 | 2024-03-12 15:40 | 2024-03-12 18:30 | 170 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12727807 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURES ENTIRE ROW 4 |  | FM008 |  | 2024-03-14 16:19 | 2024-03-14 17:19 | 2024-03-15 17:19 | 24 | 2024-03-14 16:25 | 2024-03-14 23:59 | 454 | 37 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12770165 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – ROW 5 COUNTER 10 (DEPARTURES) |  | FM008 |  | 2024-03-26 05:51 | 2024-03-26 06:51 | 2024-03-27 06:51 | 24 | 2024-03-26 06:00 | 2024-03-26 06:40 | 40 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 95217 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12799306 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW # 4 AREA |  | FM008 |  | 2024-04-06 21:55 | 2024-04-06 22:55 | 2024-04-07 22:55 | 24 | 2024-04-06 22:00 | 2024-04-06 23:15 | 75 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 137201 | Benhadi, Ms. Abla | N - - - |  | Voice Communication
| CM-2024-12797279 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT (NOT WORKING) DEPARTURE CHECK-IN COUNTER ROW #5 AREA |  | FM008 |  | 2024-04-05 22:26 | 2024-04-05 23:26 | 2024-04-06 23:26 | 24 | 2024-04-05 22:32 | 2024-04-05 23:58 | 86 | 52 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 37722 | Phumiphak, Ms. Narukamol | N - - - |  | Voice Communication
| CM-2024-12810785 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 5 ALL COUNTERS - AC TOO HOT |  | FM008 |  | 2024-04-10 16:22 | 2024-04-10 17:22 | 2024-04-11 17:22 | 24 | 2024-04-10 16:30 | 2024-04-10 18:35 | 125 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 139655 | Calica, Ms. April Joy Apilado | N - - - |  | Voice Communication
| CM-2024-12825422 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT - ROW 4 & COUNTER NO 05 |  | FM008 |  | 2024-04-13 16:57 | 2024-04-13 17:57 | 2024-04-14 17:57 | 24 | 2024-04-13 17:03 | 2024-04-13 20:00 | 177 | 67 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 87807 |  |  | 140204 | Gnaoui, Mr. Hichem | N - - - |  | Voice Communication
| CM-2024-12824327 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING – ROW 5 COUNTER 2 |  | FM008 |  | 2024-04-13 16:39 | 2024-04-13 17:39 | 2024-04-14 17:39 | 24 | 2024-04-13 16:45 | 2024-04-13 18:35 | 110 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 139195 | Dahech, Mr. Mahdi | N - - - |  | Voice Communication
| CM-2024-12824564 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #4 COUNTER #9 AREA |  | FM008 |  | 2024-04-14 19:30 | 2024-04-14 20:30 | 2024-04-15 20:30 | 24 | 2024-04-14 19:35 | 2024-04-15 01:00 | 325 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 140202 | Borsali, Ms. Dorsaf | N - - - |  | Voice Communication
| CM-2022-11045055 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-09-25 11:02 | 2022-09-25 12:02 | 2022-09-26 12:02 | 24 | 2022-09-25 11:10 | 2022-09-25 15:15 | 245 | 165 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11156458 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-10-31 21:08 | 2022-10-31 22:08 | 2022-11-01 22:08 | 24 | 2022-10-31 21:15 | 2022-10-31 22:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11232669 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | RETURN DUCT CANVAS DAMAGED-AHU-A1110-430)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-11-30 21:42 | 2022-11-30 22:42 | 2022-12-01 22:42 | 24 | 2022-11-30 21:50 | 2022-11-30 23:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11657790 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW 4 COUNTER 9 |  | FM008 |  | 2023-04-13 10:39 | 2023-04-13 11:39 | 2023-04-14 11:39 | 24 | 2023-04-13 10:45 | 2023-04-13 12:10 | 85 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11698656 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC IS TOO COLD- ROW 4 COUNTER 13 |  | FM008 |  | 2023-04-23 23:40 | 2023-04-24 00:40 | 2023-04-25 00:40 | 24 | 2023-04-23 23:45 | 2023-04-24 00:42 | 57 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 87807 | 87807 |  |  | R13779 | Zahir, Ms. Majda | N - - - |  | Voice Communication
| CM-2023-11697295 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4-COUNTER 7- AC IS TOO COLD |  | FM008 |  | 2023-04-24 23:06 | 2023-04-25 00:06 | 2023-04-26 00:06 | 24 | 2023-04-24 23:12 | 2023-04-24 23:58 | 46 | 34 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 87807 | 87807 |  |  | R13759 | El Ouasif, Ms. Safaa | N - - - |  | Voice Communication
| CM-2023-11693712 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC IS TOO COLD-DEPARTURE -ROW 4 COUNTER 10 |  | FM008 |  | 2023-04-21 08:33 | 2023-04-21 09:33 | 2023-04-22 09:33 | 24 | 2023-04-21 08:37 | 2023-04-21 14:40 | 363 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17336 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11801895 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | DEPARTURE ROW NO 4 COUNTER 14,12&13 – AC TOO COLD |  | FM008 |  | 2023-05-18 15:16 | 2023-05-18 16:16 | 2023-05-19 16:16 | 24 | 2023-05-18 15:21 | 2023-05-18 16:21 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11810780 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW 4 COUNTER 8 |  | FM008 |  | 2023-05-22 07:04 | 2023-05-22 08:04 | 2023-05-23 08:04 | 24 | 2023-05-22 07:10 | 2023-05-22 09:40 | 150 | 38 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 106973 | 17053 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11843378 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – DEPARTURE CHECK IN HALL ROW 4 COUNTER 12 |  | FM008 |  | 2023-06-02 02:38 | 2023-06-02 03:38 | 2023-06-03 03:38 | 24 | 2023-06-02 02:45 | 2023-06-02 05:50 | 185 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11836755 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE ROW 4 COUNTER 12 AREA |  | FM008 |  | 2023-05-31 02:02 | 2023-05-31 03:02 | 2023-06-01 03:02 | 24 | 2023-05-31 02:10 | 2023-05-31 06:30 | 260 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11863104 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC IS TOO COLD-DEPARTURE ROW 4 COUNTER 14 |  | FM008 |  | 2023-06-08 16:16 | 2023-06-08 17:16 | 2023-06-09 17:16 | 24 | 2023-06-08 16:25 | 2023-06-08 20:00 | 215 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17336 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11883507 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT , ENTIRE ROW#3, DEPARTURE AREA |  | FM008 |  | 2023-06-14 16:38 | 2023-06-14 17:38 | 2023-06-15 17:38 | 24 | 2023-06-14 16:47 | 2023-06-14 18:00 | 73 | 70 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | 50621 | Mohammed, Mr. Mohsin Hasham | N - - - |  | Voice Communication
| CM-2023-11893440 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 4 COUNTER 6 |  | FM008 |  | 2023-06-18 10:49 | 2023-06-18 11:49 | 2023-06-19 11:49 | 24 | 2023-06-18 10:55 | 2023-06-18 14:00 | 185 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 105740 | Maxwell, Ms. Tanya Mwayera Pensha | N - - - |  | Voice Communication
| CM-2023-11888437 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4 COUNTER # 5 AC TOO COLD |  | FM008 |  | 2023-06-18 10:00 | 2023-06-18 11:00 | 2023-06-19 11:00 | 24 | 2023-06-18 10:05 | 2023-06-18 13:05 | 180 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11941864 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD, INFORMATION DESK NEAR CHECK IN ROW-3 & 4 |  | FM008 |  | 2023-07-03 18:49 | 2023-07-03 19:49 | 2023-07-04 19:49 | 24 | 2023-07-03 18:58 | 2023-07-03 20:00 | 62 | 62 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | T26780 | Laila, Ms. Lahlimi | N - - - |  | Voice Communication
| CM-2023-12097569 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING -ROW 2 DEPARTURE |  | FM008 |  | 2023-08-17 06:43 | 2023-08-17 07:43 | 2023-08-18 07:43 | 24 | 2023-08-17 06:50 | 2023-08-17 09:35 | 165 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | 92549 | Soman, Ms. Sony | N - - - |  | Voice Communication
| CM-2023-12126156 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-08-28 11:04 | 2023-08-28 12:04 | 2023-08-29 12:04 | 24 | 2023-08-28 11:10 | 2023-08-28 15:00 | 230 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-12141070 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD IN ROW-4, COUNTER 7,8 & 9 DEAPRTURE HALL |  | FM008 |  | 2023-09-03 09:39 | 2023-09-03 10:39 | 2023-09-04 10:39 | 24 | 2023-09-03 09:45 | 2023-09-03 11:30 | 105 | 39 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 87807 |  |  | R10331 | Naserian, Ms. Linda | N - - - |  | Voice Communication
| CM-2023-12280037 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #4 COUNTER AREA |  | FM008 |  | 2023-10-13 00:32 | 2023-10-13 01:32 | 2023-10-14 01:32 | 24 | 2023-10-13 00:40 | 2023-10-13 05:20 | 280 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2023-12378615 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN COUNTERS ROW NO 4 DEPARTURES |  | FM008 |  | 2023-11-17 02:47 | 2023-11-17 03:47 | 2023-11-18 03:47 | 24 | 2023-11-17 02:52 | 2023-11-17 04:20 | 88 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 135028 | Bhatti, Ms. Muneeba | N - - - |  | Voice Communication
| CM-2023-12420170 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | SUPPLY SIDE BEARING NOISY – T4-01-04 |  | FM008 |  | 2023-11-28 09:06 | 2023-11-28 10:06 | 2023-11-29 10:06 | 24 | 2023-11-28 09:10 | 2023-11-28 13:10 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12575253 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING - ROW 4 COUNTER 7 |  | FM008 |  | 2024-01-17 16:34 | 2024-01-17 17:34 | 2024-01-18 17:34 | 24 | 2024-01-17 16:40 | 2024-01-17 21:35 | 295 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12592242 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO WARM - DEPARTURE CHECK-IN ROW #4 COUNTER #1 AREA |  | FM008 |  | 2024-01-25 01:12 | 2024-01-25 02:12 | 2024-01-26 02:12 | 24 | 2024-01-25 01:20 | 2024-01-25 06:00 | 280 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 17573 | 17053 |  |  | 142195 | Ishraq, Mr. Mohsin | N - - - |  | Voice Communication
| CM-2024-12597422 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING ROW 4 -DEPARTURE |  | FM008 |  | 2024-01-28 05:18 | 2024-01-28 06:18 | 2024-01-29 06:18 | 24 | 2024-01-28 05:25 | 2024-01-28 06:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12831198 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 5 ALL COUNTERS |  | FM008 |  | 2024-04-17 03:45 | 2024-04-17 04:45 | 2024-04-18 04:45 | 24 | 2024-04-17 03:50 | 2024-04-17 05:30 | 100 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 17053 |  |  | 137355 | Mansouri, Ms. El Yakoute | N - - - |  | Voice Communication
| CM-2024-12833213 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECK-IN ROW 3-4 INFO DESK AREA |  | FM008 |  | 2024-04-20 17:24 | 2024-04-20 18:24 | 2024-04-21 18:24 | 24 | 2024-04-20 17:30 | 2024-04-20 18:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | T25151 | Were, Ms. Hanifa Ajiambo | N - - - |  | Voice Communication
| CM-2024-12849731 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK-IN ROW NO 5 AC TOO HOT |  | FM008 |  | 2024-04-24 06:34 | 2024-04-24 07:34 | 2024-04-25 07:34 | 24 | 2024-04-24 06:40 | 2024-04-24 14:00 | 440 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12847603 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW NO 04 & COUNTER NO 13 |  | FM008 |  | 2024-04-25 03:49 | 2024-04-25 04:49 | 2024-04-26 04:49 | 24 | 2024-04-25 03:55 | 2024-04-25 08:00 | 245 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12854106 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE ROW 3 INFORMATION DESK |  | FM008 |  | 2024-04-28 10:00 | 2024-04-28 11:00 | 2024-04-29 11:00 | 24 | 2024-04-28 10:05 | 2024-04-28 16:00 | 355 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | T28851 | Saafi, Mr. Kevin | N - - - |  | Voice Communication
| CM-2022-10988784 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE CHECK IN HALL ROW#3 INFORMATION COUNTER AREA |  | FM008 |  | 2022-08-29 18:43 | 2022-08-29 19:43 | 2022-08-30 19:43 | 24 | 2022-08-29 18:50 | 2022-08-29 23:00 | 250 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17053 | 55709 |  |  | 55126 | Khadka, Mr. Dilip | N - - - |  | Voice Communication
| CM-2022-11080447 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1110-430 |  | FM008 |  | 2022-10-08 00:09 | 2022-10-08 01:09 | 2022-10-09 01:09 | 24 | 2022-10-08 00:15 | 2022-10-08 01:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 76858 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11295818 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #5 AREA |  | FM008 |  | 2022-12-20 13:57 | 2022-12-20 14:57 | 2022-12-21 14:57 | 24 | 2022-12-20 14:05 | 2022-12-20 16:45 | 160 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 74906 | Zaveri, Mr. Nuruddin Asgar | N - - - |  | Voice Communication
| CM-2023-11351106 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM- AHU-A1110-430- T4-09-04 |  | FM008 |  | 2023-01-06 00:32 | 2023-01-06 01:32 | 2023-01-07 01:32 | 24 | 2023-01-06 00:35 | 2023-01-06 02:00 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11546776 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | QR SALES COUNTER NEAR JAMOCHA - AC TOO HOT |  | FM008 |  | 2023-03-09 21:52 | 2023-03-09 22:52 | 2023-03-10 22:52 | 24 | 2023-03-09 22:00 | 2023-03-09 23:35 | 95 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | 59517 | Reyes, Mr. Ojieson Castro | N - - - |  | Voice Communication
| CM-2023-11697478 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4 COUNTER 1 - AC TOO COLD |  | FM008 |  | 2023-04-25 20:18 | 2023-04-25 21:18 | 2023-04-26 21:18 | 24 | 2023-04-25 20:23 | 2023-04-25 23:55 | 212 | 42 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 89127 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11698506 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 5 COUNTER 5 AC TOO COLD |  | FM008 |  | 2023-04-26 19:35 | 2023-04-26 20:35 | 2023-04-27 20:35 | 24 | 2023-04-26 19:41 | 2023-04-26 23:55 | 254 | 47 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | 12065 | Mohammadi, Ms. Masoumeh Hassan | N - - - |  | Voice Communication
| CM-2023-11799700 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW 4 COUNTER 1 |  | FM008 |  | 2023-05-16 04:03 | 2023-05-16 05:03 | 2023-05-17 05:03 | 24 | 2023-05-16 04:10 | 2023-05-16 06:25 | 135 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2023-11800124 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4 COUNTER 12 AC TOO COLD |  | FM008 |  | 2023-05-17 14:05 | 2023-05-17 15:05 | 2023-05-18 15:05 | 24 | 2023-05-17 14:10 | 2023-05-17 17:40 | 210 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11808396 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 4 COUNTER 10 |  | FM008 |  | 2023-05-21 08:50 | 2023-05-21 09:50 | 2023-05-22 09:50 | 24 | 2023-05-21 08:55 | 2023-05-21 15:40 | 405 | 67 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 17053 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11818256 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW 4 AREA |  | FM008 |  | 2023-05-22 07:04 | 2023-05-22 08:04 | 2023-05-23 08:04 | 24 | 2023-05-22 07:10 | 2023-05-22 09:40 | 150 | 38 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17573 | 17053 |  |  | 83571 | Abdimalit Uulu, Mr. Omurzak | N - - - |  | Voice Communication
| CM-2023-11883587 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK IN ROW 4 ALL COUNTERS |  | FM008 |  | 2023-06-15 02:54 | 2023-06-15 03:54 | 2023-06-16 03:54 | 24 | 2023-06-15 03:00 | 2023-06-15 04:40 | 100 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 133396 | 87807 |  |  | 105740 | Maxwell, Ms. Tanya Mwayera Pensha | N - - - |  | Voice Communication
| CM-2023-11884629 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4 COUNTER 12-13 AC TOO COLD |  | FM008 |  | 2023-06-14 04:04 | 2023-06-14 05:04 | 2023-06-15 05:04 | 24 | 2023-06-14 04:10 | 2023-06-14 04:50 | 40 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11917647 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT, ROW-4 CHECK IN COUNTER |  | FM008 |  | 2023-06-24 23:20 | 2023-06-25 00:20 | 2023-06-26 00:20 | 24 | 2023-06-24 23:25 | 2023-06-24 23:55 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2023-11976399 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT T2-12-26 |  | FM008 |  | 2023-07-15 19:50 | 2023-07-15 20:50 | 2023-07-16 20:50 | 24 | 2023-07-15 19:56 | 2023-07-16 01:02 | 306 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | 17910 | Mouatad, Mr. Brahim | N - - - |  | Voice Communication
| CM-2023-12202470 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE CHECK IN ROW 4 ALL THE COUNTERS |  | FM008 |  | 2023-09-20 03:35 | 2023-09-20 04:35 | 2023-09-21 04:35 | 24 | 2023-09-20 03:40 | 2023-09-20 05:25 | 105 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2023-12209376 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD IN CHECK IN COUNTER NO 2 ROW 4 AREA |  | FM008 |  | 2023-09-23 22:51 | 2023-09-23 23:51 | 2023-09-24 23:51 | 24 | 2023-09-23 23:00 | 2023-09-24 01:25 | 145 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 95217 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | E-mail
| CM-2024-12562229 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 4 - AC TOO HOT |  | FM008 |  | 2024-01-15 17:15 | 2024-01-15 18:15 | 2024-01-16 18:15 | 24 | 2024-01-15 17:20 | 2024-01-15 18:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 95217 |  |  | 136727 | Dalil, Ms. Fatima Zahra | N - - - |  | Voice Communication
| CM-2024-12590160 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING – ROW 4 LAST 3 PREMIUM COUNTERS (PASSENGERS COMPLAINING) |  | FM008 |  | 2024-01-24 13:01 | 2024-01-24 13:31 | 2024-01-24 17:31 | 4 | 2024-01-24 13:10 | 2024-01-24 18:35 | 325 | 65 | 2 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106973 | 95217 |  |  | 97236 | Gusain, Mr. Aman Singh | N - - - |  | Voice Communication
| CM-2024-12611917 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT, ROW-4 ALL COUNTERS AND PASSENGER QUEUING AREA |  | FM008 |  | 2024-02-02 13:25 | 2024-02-02 14:25 | 2024-02-03 14:25 | 24 | 2024-02-02 13:35 | 2024-02-02 15:30 | 115 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 124475 | 17053 |  |  | 97236 | Gusain, Mr. Aman Singh | N - - - |  | Voice Communication
| CM-2024-12651540 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE ALL AREA ALL CHECK IN COUNTER |  | FM008 |  | 2024-02-15 08:30 | 2024-02-15 09:30 | 2024-02-16 09:30 | 24 | 2024-02-15 08:35 | 2024-02-15 12:10 | 215 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 95217 |  |  | T25503 | Khan, Mr. Shahroz Jamil | N - - - |  | Voice Communication
| CM-2024-12648294 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | T4-09-04-FILTER DIRTY -AIR HANDLING UNIT 043 (TAG NO:AHU-A1110-430)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2024-02-15 00:07 | 2024-02-15 01:07 | 2024-02-16 01:07 | 24 | 2024-02-15 00:15 | 2024-02-15 04:10 | 235 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 95217 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2024-12650107 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT ROW 4 COUNTER 6 |  | FM008 |  | 2024-02-14 11:03 | 2024-02-14 12:03 | 2024-02-15 12:03 | 24 | 2024-02-14 11:10 | 2024-02-14 14:00 | 170 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12713833 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC IS TOO WARM/ HOT-ALL DEPARTURE ROW NO.5 CHECK IN AREA |  | FM008 |  | 2024-03-08 23:06 | 2024-03-09 00:06 | 2024-03-10 00:06 | 24 | 2024-03-08 23:11 | 2024-03-08 23:59 | 48 | 30 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 17053 |  |  | 97236 | Gusain, Mr. Aman Singh | N - - - |  | Voice Communication
| CM-2024-12756982 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 4 COUNTER 3 AC TOO COLD |  | FM008 |  | 2024-03-24 09:26 | 2024-03-24 10:26 | 2024-03-25 10:26 | 24 | 2024-03-24 09:35 | 2024-03-24 10:30 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | 115081 | Karlina, Ms. Ninik | N - - - |  | Voice Communication
| CM-2024-12825192 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW 3 COUNTER 13 AND 14 AC TOO HOT |  | FM008 |  | 2024-04-13 00:55 | 2024-04-13 01:55 | 2024-04-14 01:55 | 24 | 2024-04-13 01:00 | 2024-04-13 02:20 | 80 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 87807 |  |  | 105083 | Thakur, Mr. Zain Khalil | N - - - |  | Voice Communication
| CM-2024-12828194 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING ROW 5 |  | FM008 |  | 2024-04-16 11:06 | 2024-04-16 12:06 | 2024-04-17 12:06 | 24 | 2024-04-16 11:15 | 2024-04-16 12:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12829264 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK-IN ROW 3 AC TOO HOT |  | FM008 |  | 2024-04-17 17:47 | 2024-04-17 18:47 | 2024-04-18 18:47 | 24 | 2024-04-17 17:55 | 2024-04-17 18:40 | 45 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12828579 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -CHECK COUNTER N2 IN ROW 4 |  | FM008 |  | 2024-04-18 05:15 | 2024-04-18 06:15 | 2024-04-19 06:15 | 24 | 2024-04-18 05:20 | 2024-04-18 06:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 138037 | Rida, Ms. Chaima | N - - - |  | Voice Communication
| CM-2024-12829422 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT ROW 5 ALL COUNTER |  | FM008 |  | 2024-04-18 11:43 | 2024-04-18 12:43 | 2024-04-19 12:43 | 24 | 2024-04-18 11:50 | 2024-04-18 15:30 | 220 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2023-12280580 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW 4 COUNTER 12 |  | FM008 |  | 2023-10-14 17:57 | 2023-10-14 18:57 | 2023-10-15 18:57 | 24 | 2023-10-14 18:05 | 2023-10-14 18:40 | 35 | 35 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | 119777 | Sfar, Ms. Rihab | N - - - |  | Voice Communication
| CM-2023-12324264 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECK IN HALL ROW # 4 COUNTER 13 DEPARTURE |  | FM008 |  | 2023-10-28 05:52 | 2023-10-28 06:52 | 2023-10-29 06:52 | 24 | 2023-10-28 06:00 | 2023-10-28 12:10 | 370 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | 110997 | Mohamed, Ms. Shukri Abdi | N - - - |  | Voice Communication
| CM-2023-12368186 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 4 COUNTER 13 |  | FM008 |  | 2023-11-11 22:21 | 2023-11-11 23:21 | 2023-11-12 23:21 | 24 | 2023-11-11 22:25 | 2023-11-11 23:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | 119702 | Miksam, Ms. Dounia | N - - - |  | Voice Communication
| CM-2023-12379172 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #4 |  | FM008 |  | 2023-11-14 18:12 | 2023-11-14 19:12 | 2023-11-15 19:12 | 24 | 2023-11-14 18:20 | 2023-11-14 23:58 | 338 | 48 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 87807 |  |  | 137299 | Chouklat, Ms. Lyna | N - - - |  | E-mail
| CM-2023-12464720 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN ROW # 5 COUNTER # 1 |  | FM008 |  | 2023-12-12 02:03 | 2023-12-12 03:03 | 2023-12-13 03:03 | 24 | 2023-12-12 02:10 | 2023-12-12 05:15 | 185 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 137935 | Boukhelkhal, Ms. Samira | N - - - |  | Voice Communication
| CM-2023-12464905 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECKING COUNTER 8 ROW #4 |  | FM008 |  | 2023-12-12 19:22 | 2023-12-12 20:22 | 2023-12-13 20:22 | 24 | 2023-12-12 19:25 | 2023-12-13 00:50 | 325 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 132112 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2023-12489779 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -CHECK IN ROW # 4 COUNTER # 7 |  | FM008 |  | 2023-12-19 18:28 | 2023-12-19 19:28 | 2023-12-20 19:28 | 24 | 2023-12-19 18:35 | 2023-12-20 01:05 | 390 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2023-12494302 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD ROW # 5 DEPARTURE CHECK IN AREA |  | FM008 |  | 2023-12-23 02:20 | 2023-12-23 03:20 | 2023-12-24 03:20 | 24 | 2023-12-23 02:25 | 2023-12-23 06:25 | 240 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 87807 |  |  | R10353 | Munyao, Mr. Collins | N - - - |  | Voice Communication
| CM-2024-12577660 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO WARM -CHECK IN ROW # 4 |  | FM008 |  | 2024-01-21 00:03 | 2024-01-21 01:03 | 2024-01-22 01:03 | 24 | 2024-01-21 00:10 | 2024-01-21 04:35 | 265 | 36 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 137355 | Mansouri, Ms. El Yakoute | N - - - |  | Voice Communication
| CM-2024-12629785 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – CHECK IN ROW 4 |  | FM008 |  | 2024-02-07 16:17 | 2024-02-07 17:17 | 2024-02-08 17:17 | 24 | 2024-02-07 16:20 | 2024-02-07 22:05 | 345 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12629980 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING (TOO WARM) - DEPARTURE CHECK-IN ROW #4 COUNTER 4 & 5 AREA |  | FM008 |  | 2024-02-08 16:21 | 2024-02-08 17:21 | 2024-02-09 17:21 | 24 | 2024-02-08 16:30 | 2024-02-08 18:30 | 120 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12652509 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT CHECKIN ROW 4 COUNTER 13 |  | FM008 |  | 2024-02-15 22:20 | 2024-02-15 23:20 | 2024-02-16 23:20 | 24 | 2024-02-15 22:25 | 2024-02-16 00:20 | 115 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 68485 | 95217 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12655660 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT IN CHECK IN ROW # 4, DEPARTURE AREA |  | FM008 |  | 2024-02-18 15:30 | 2024-02-18 16:30 | 2024-02-19 16:30 | 24 | 2024-02-18 15:35 | 2024-02-18 18:00 | 145 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 87807 |  |  | 97236 | Gusain, Mr. Aman Singh | N - - - |  | Voice Communication
| CM-2024-12694608 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – CHECK IN R3 - C13 |  | FM008 |  | 2024-03-03 07:33 | 2024-03-03 08:33 | 2024-03-04 08:33 | 24 | 2024-03-03 07:40 | 2024-03-03 09:35 | 115 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 124419 | Mohamed Azmi, Mr. Sinnen | N - - - |  | Voice Communication
| CM-2024-12699570 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT ROW3- COUNTER 13 & 14 |  | FM008 |  | 2024-03-04 08:08 | 2024-03-04 09:08 | 2024-03-05 09:08 | 24 | 2024-03-04 08:15 | 2024-03-04 19:55 | 700 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 124419 | Mohamed Azmi, Mr. Sinnen | N - - - |  | Voice Communication
| CM-2024-12700001 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO WARM - DEPARTURE CHECK-IN ROW # AREA |  | FM008 |  | 2024-03-05 05:31 | 2024-03-05 06:31 | 2024-03-06 06:31 | 24 | 2024-03-05 05:35 | 2024-03-05 06:30 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 119702 | Miksam, Ms. Dounia | N - - - |  | Voice Communication
| CM-2024-12735024 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | ROW # 4 AC TOO COLD |  | FM008 |  | 2024-03-16 16:57 | 2024-03-16 17:57 | 2024-03-17 17:57 | 24 | 2024-03-16 17:04 | 2024-03-16 23:40 | 396 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12733082 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – ROW 4 COUNTER 12 ENTIRE ROW DEPARTURES |  | FM008 |  | 2024-03-15 18:04 | 2024-03-15 19:04 | 2024-03-16 19:04 | 24 | 2024-03-15 18:07 | 2024-03-15 18:40 | 33 | 33 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12737514 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – ROW 3 AND 4 CHECKING COUNTERS AREA T2 12 26 |  | FM008 |  | 2024-03-18 05:23 | 2024-03-18 06:23 | 2024-03-19 06:23 | 24 | 2024-03-18 05:30 | 2024-03-18 06:20 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2024-12749460 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 7 – AC TOO HOT |  | FM008 |  | 2024-03-20 22:57 | 2024-03-20 23:57 | 2024-03-21 23:57 | 24 | 2024-03-20 23:00 | 2024-03-21 01:02 | 122 | 75 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12794560 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | A/C TOO HOT AT ROW 04 |  | FM008 |  | 2024-04-03 22:47 | 2024-04-03 23:47 | 2024-04-04 23:47 | 24 | 2024-04-03 22:57 | 2024-04-04 02:05 | 188 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12798688 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW NO 03 AC TOO HOT |  | FM008 |  | 2024-04-07 11:15 | 2024-04-07 12:15 | 2024-04-08 12:15 | 24 | 2024-04-07 11:20 | 2024-04-07 12:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 68672 | Kande Appuhamilage, Mr. Chathuranga Senarathna | N - - - |  | Voice Communication
| CM-2024-12815832 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | A/C IS TOO HOT ROW 05 |  | FM008 |  | 2024-04-07 20:06 | 2024-04-07 21:06 | 2024-04-08 21:06 | 24 | 2024-04-07 20:11 | 2024-04-08 01:02 | 291 | 67 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2024-12810561 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 5 ALL COUNTERS AC TOO HOT |  | FM008 |  | 2024-04-09 16:06 | 2024-04-09 17:06 | 2024-04-10 17:06 | 24 | 2024-04-09 16:15 | 2024-04-09 17:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12823978 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | MTB, LEVEL 2, CHECK-IN ROW 4 COUNTER NUMBER 13 – AC TEMPERATURE IS TOO COLD |  | FM008 |  | 2024-04-12 12:33 | 2024-04-12 13:33 | 2024-04-13 13:33 | 24 | 2024-04-12 12:40 | 2024-04-12 18:05 | 325 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 94954 | 87807 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12820713 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE CHECK IN ROW 5 ALL THE COUNTERS |  | FM008 |  | 2024-04-11 16:12 | 2024-04-11 17:12 | 2024-04-12 17:12 | 24 | 2024-04-11 16:20 | 2024-04-11 17:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 87807 |  |  | 139254 | Bellahirech, Ms. Nesrine | N - - - |  | Voice Communication
| CM-2024-12847991 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE CHECK-IN ROW #5 - DUPLICATE COPY OF WORK ORDER CM-2024-12847151 |  | FM008 |  | 2024-04-23 05:43 | 2024-04-23 06:43 | 2024-04-24 06:43 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | FOURTH FLOOR AREA 011 | N |  |  |  | 17573 | 87807 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - | DUPLICATE CM WORK ORDER - MATAR FRC ERROR | Voice Communication
| CM-2024-12851832 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD IN CHECK IN ROW NO 4 COUNTER 14 |  | FM008 |  | 2024-04-27 00:59 | 2024-04-27 01:59 | 2024-04-28 01:59 | 24 | 2024-04-27 01:05 | 2024-04-27 02:05 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 87807 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12872366 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT-DEPARTURE CHECK ROW 5 ALL THE COUNTERS(CM-2024-01-1610) |  | FM008 |  | 2024-04-30 12:13 | 2024-04-30 13:13 | 2024-05-01 13:13 | 24 | 2024-04-30 12:20 | 2024-04-30 13:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 62079 | 87807 |  |  | 137722 | MOHAMED AMINE JABNOUNI | - - - |  | Voice Communication
| CM-2023-12276669 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | SUPPLY MOTOR V BELT DAMAGED - AHU-A1110-430 – T4 09 04 |  | FM008 |  | 2023-10-09 00:32 | 2023-10-09 01:32 | 2023-10-10 01:32 | 24 | 2023-10-09 00:40 | 2023-10-09 02:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12276670 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | RELIEF MOTOR V-BELT DAMAGED – AHU-A1110-430 – T4 09 04 |  | FM008 |  | 2023-10-09 00:36 | 2023-10-09 01:36 | 2023-10-10 01:36 | 24 | 2023-10-09 00:42 | 2023-10-09 03:45 | 183 | 188 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12287656 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -DEPARTURE ROW 4 |  | FM008 |  | 2023-10-15 20:41 | 2023-10-15 21:41 | 2023-10-16 21:41 | 24 | 2023-10-15 20:50 | 2023-10-15 23:50 | 180 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17333 | 87807 |  |  | R10331 | Naserian, Ms. Linda | N - - - |  | Voice Communication
| CM-2023-12322291 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - INFO DESK BETWEEN ROW 3 & 4 |  | FM008 |  | 2023-10-27 01:14 | 2023-10-27 02:14 | 2023-10-28 02:14 | 24 | 2023-10-27 01:20 | 2023-10-27 04:15 | 175 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | T26806 | Azizillaeva, Ms. Khojikhon | N - - - |  | Voice Communication
| CM-2023-12328673 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 04 A/C IS TOO COLD |  | FM008 |  | 2023-10-29 03:10 | 2023-10-29 04:10 | 2023-10-30 04:10 | 24 | 2023-10-29 03:15 | 2023-10-29 05:45 | 150 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | R10225 | Lincoln, Ms. Yvonne Wangui | N - - - |  | Voice Communication
| CM-2023-12363820 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN ROW # 4 COUNTER # 13 |  | FM008 |  | 2023-11-07 17:27 | 2023-11-07 18:27 | 2023-11-08 18:27 | 24 | 2023-11-07 17:35 | 2023-11-07 18:30 | 55 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | R13779 | Zahir, Ms. Majda | N - - - |  | Voice Communication
| CM-2023-12365908 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD CHECKIN ROW 4 |  | FM008 |  | 2023-11-09 08:12 | 2023-11-09 09:12 | 2023-11-10 09:12 | 24 | 2023-11-09 08:20 | 2023-11-09 12:55 | 275 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 105740 | Maxwell, Ms. Tanya Mwayera Pensha | N - - - |  | Voice Communication
| CM-2023-12365466 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | A/C IS TOO COLD AT ROW 4 COUNTER 5 |  | FM008 |  | 2023-11-09 03:45 | 2023-11-09 04:45 | 2023-11-10 04:45 | 24 | 2023-11-09 03:50 | 2023-11-09 04:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | R12227 | El Mahdaoui, Ms. Omayma | N - - - |  | Voice Communication
| CM-2023-12368646 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES ROW 4, ALL COUNTERS |  | FM008 |  | 2023-11-11 08:48 | 2023-11-11 09:48 | 2023-11-12 09:48 | 24 | 2023-11-11 08:55 | 2023-11-11 12:15 | 200 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2023-12483303 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECK IN ROW 4 COUNTER 11 |  | FM008 |  | 2023-12-15 04:55 | 2023-12-15 05:55 | 2023-12-16 05:55 | 24 | 2023-12-15 05:00 | 2023-12-15 06:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2023-12485901 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - ROW # 4 NEAR COUNTER NO 12 |  | FM008 |  | 2023-12-19 02:33 | 2023-12-19 03:33 | 2023-12-20 03:33 | 24 | 2023-12-19 02:40 | 2023-12-19 05:20 | 160 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 138037 | Rida, Ms. Chaima | N - - - |  | Voice Communication
| CM-2024-12537778 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT CHECKIN ROW 4 COUNTER 10 |  | FM008 |  | 2024-01-06 19:03 | 2024-01-06 20:03 | 2024-01-07 20:03 | 24 | 2024-01-06 19:10 | 2024-01-06 22:10 | 180 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 136727 | Dalil, Ms. Fatima Zahra | N - - - |  | Voice Communication
| CM-2024-12570637 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE CHECK IN ROW 4 COUNTER 6 |  | FM008 |  | 2024-01-17 01:36 | 2024-01-17 02:36 | 2024-01-18 02:36 | 24 | 2024-01-17 01:45 | 2024-01-17 04:15 | 150 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 133396 | 17053 |  |  | 142195 | Ishraq, Mr. Mohsin | N - - - |  | Voice Communication
| CM-2024-12623940 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE ROW 4 COUNTER 7 |  | FM008 |  | 2024-02-06 16:18 | 2024-02-06 17:18 | 2024-02-07 17:18 | 24 | 2024-02-06 16:25 | 2024-02-06 21:40 | 315 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 138627 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12635609 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT, CHECK IN ROW-4,COUNTER-4, DEPARTURE AREA |  | FM008 |  | 2024-02-10 17:00 | 2024-02-10 18:00 | 2024-02-11 18:00 | 24 | 2024-02-10 17:10 | 2024-02-10 18:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12634273 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN ROW #4 COUNTER #10 AREA |  | FM008 |  | 2024-02-10 05:12 | 2024-02-10 06:12 | 2024-02-11 06:12 | 24 | 2024-02-10 05:15 | 2024-02-10 06:10 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12652919 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT - ROOM # T2-12-26 |  | FM008 |  | 2024-02-17 00:34 | 2024-02-17 01:34 | 2024-02-18 01:34 | 24 | 2024-02-17 00:40 | 2024-02-17 06:30 | 350 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 87807 |  |  | 95899 | Dhople, Mr. Sanjay Subhashchandra | N - - - |  | Voice Communication
| CM-2024-12653913 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD – DEPARTURE CHECK IN ROW 4 AREA |  | FM008 |  | 2024-02-17 19:39 | 2024-02-17 20:39 | 2024-02-18 20:39 | 24 | 2024-02-17 19:45 | 2024-02-17 23:00 | 195 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 87807 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12768095 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD ROW 4 COUNTER 08 |  | FM008 |  | 2024-03-25 16:52 | 2024-03-25 17:52 | 2024-03-26 17:52 | 24 | 2024-03-25 17:00 | 2024-03-25 23:35 | 395 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2024-12769844 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT - ROW # 05 & COUNTER # 06 |  | FM008 |  | 2024-03-29 07:02 | 2024-03-29 08:02 | 2024-03-30 08:02 | 24 | 2024-03-29 07:05 | 2024-03-29 08:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12823232 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT CHECK-IN ROW 5 |  | FM008 |  | 2024-04-12 23:32 | 2024-04-13 00:32 | 2024-04-14 00:32 | 24 | 2024-04-12 23:40 | 2024-04-13 00:10 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 87807 |  |  | 143052 | Raj, Mr. Puneet | N - - - |  | Voice Communication
| CM-2024-12823049 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT CHECK-IN -ROW-4 |  | FM008 |  | 2024-04-11 22:10 | 2024-04-11 23:10 | 2024-04-12 23:10 | 24 | 2024-04-11 22:15 | 2024-04-12 00:40 | 145 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 87807 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12823568 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURE CHECK-IN 5 COUNTER A11 AREA |  | FM008 |  | 2024-04-13 22:16 | 2024-04-13 23:16 | 2024-04-14 23:16 | 24 | 2024-04-13 22:21 | 2024-04-14 01:25 | 184 | 69 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 137955 | Ghedifi, Ms. Ikram | N - - - |  | Voice Communication
| CM-2024-12829644 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN ROW 5 – AC TOO HOT |  | FM008 |  | 2024-04-19 11:36 | 2024-04-19 12:36 | 2024-04-20 12:36 | 24 | 2024-04-19 11:40 | 2024-04-19 12:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12849301 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT CHECKIN ROW 5 COUNTER 13 |  | FM008 |  | 2024-04-22 10:15 | 2024-04-22 11:15 | 2024-04-23 11:15 | 24 | 2024-04-22 10:20 | 2024-04-22 15:10 | 290 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12847151 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | CHECK IN R5 - AC TOO HOT |  | FM008 |  | 2024-04-23 05:13 | 2024-04-23 06:13 | 2024-04-24 06:13 | 24 | 2024-04-23 05:20 | 2024-04-23 06:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12846513 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD DEPARTURE HIA INFORMATION DESK |  | FM008 |  | 2024-04-25 11:51 | 2024-04-25 12:51 | 2024-04-26 12:51 | 24 | 2024-04-25 11:55 | 2024-04-25 17:00 | 305 | 63 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | T28777 | Abdul Fattah, Ms. Maha | N - - - |  | Voice Communication
| CM-2022-10121073 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-09-04 |  | FM008 |  | 2022-02-09 07:47 | 2022-02-09 08:47 | 2022-02-10 08:47 | 24 | 2022-02-09 07:50 | 2022-02-09 10:00 | 130 | 260 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10226769 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AHU MERINE LIGHT NOT WORKING |  | FM008 |  | 2022-03-11 13:52 | 2022-03-11 14:52 | 2022-03-12 14:52 | 24 | 2022-03-11 14:00 | 2022-03-11 18:00 | 240 | 95 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 17053 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10329199 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN DEPARTURE ROW 3 AND 4 NEAR INFO COUNTER |  | FM008 |  | 2022-04-09 08:33 | 2022-04-09 09:33 | 2022-04-10 09:33 | 24 | 2022-04-09 08:40 | 2022-04-09 11:30 | 170 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 17053 |  |  | 103405 | Abubakarova, Ms. Madina Beslanovna | N - - - |  | Voice Communication
| CM-2022-10592341 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - INFORMATION COUNTER IN-BETWEEN ROW 3 AND 4- DEP GATE 2 |  | FM008 |  | 2022-04-24 22:10 | 2022-04-24 23:10 | 2022-04-25 23:10 | 24 | 2022-04-24 22:19 | 2022-04-24 23:55 | 96 | 36 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 17053 |  |  | 68758 | Antony, Mr. Martin | N - - - |  | Voice Communication
| CM-2022-10614611 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD -ROW AND 4 INFORMATION DESK DEPARTURE |  | FM008 |  | 2022-05-03 09:23 | 2022-05-03 10:23 | 2022-05-04 10:23 | 24 | 2022-05-03 09:30 | 2022-05-03 10:45 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 62648 | Shaikh, Mrs. Madina Abdul Qadeer | N - - - |  | Voice Communication
| CM-2022-10627570 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC VENT IS DIRTY - T2-12-10 (OFFICE) |  | FM008 |  | 2022-05-08 16:07 | 2022-05-08 17:07 | 2022-05-09 17:07 | 24 | 2022-05-08 16:15 | 2022-05-08 22:45 | 390 | 35 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM11021 | Ansari, Mr. Md Shabbir | N - - - |  | Voice Communication
| CM-2022-10771093 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -T4-09-04 |  | FM008 |  | 2022-06-22 07:18 | 2022-06-22 08:18 | 2022-06-23 08:18 | 24 | 2022-06-22 07:20 | 2022-06-22 08:30 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10862469 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE CHECK-IN ROW #4 AREA |  | FM008 |  | 2022-07-22 23:41 | 2022-07-23 00:41 | 2022-07-24 00:41 | 24 | 2022-07-22 23:50 | 2022-07-23 00:30 | 40 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMPERATURE GAUGE FAULTY | RECTIFIED/REPLACED | 17573 | 95217 |  |  | 119703 | El Amrani El Idrissi, Ms. Meryem | N - - - |  | Voice Communication
| CM-2023-11629668 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES HALL, ROW 4 COUNTER 6 AREA |  | FM008 |  | 2023-04-07 11:37 | 2023-04-07 12:37 | 2023-04-08 12:37 | 24 | 2023-04-07 11:43 | 2023-04-07 14:40 | 177 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 121959 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2023-11660781 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD - DEPARTURES ROW 4 COUNTER 12 |  | FM008 |  | 2023-04-14 09:04 | 2023-04-14 10:04 | 2023-04-15 10:04 | 24 | 2023-04-14 09:10 | 2023-04-14 10:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | R12280 | Feddah, Ms. Meriem | N - - - |  | Voice Communication
| CM-2022-10042182 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY -AHU-A1110-430)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-01-12 00:19 | 2022-01-12 01:19 | 2022-01-13 01:19 | 24 | 2022-01-12 00:25 | 2022-01-12 06:45 | 380 | 170 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10262647 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD FAN SPEED IS TOOFAST -DEAPARTURE INFORMATION DESK NEAR CHECK IN ROW 3 |  | FM008 |  | 2022-03-20 06:30 | 2022-03-20 07:30 | 2022-03-21 07:30 | 24 | 2022-03-20 06:40 | 2022-03-20 07:30 | 50 | 50 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 87807 |  |  | 62648 | Shaikh, Mrs. Madina Abdul Qadeer | N - - - |  | Voice Communication
| CM-2023-11584056 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT CHECKIN ALL ROWS |  | FM008 |  | 2023-03-25 00:20 | 2023-03-25 01:20 | 2023-03-26 01:20 | 24 | 2023-03-25 00:30 | 2023-03-25 02:30 | 120 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 123446 | Abou Mosleh, Mr. Ehab | N - - - |  | Voice Communication
| CM-2023-12258519 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC NOT WORKING -ROW 4 DEPARTURE |  | FM008 |  | 2023-10-08 05:33 | 2023-10-08 06:33 | 2023-10-09 06:33 | 24 | 2023-10-08 05:40 | 2023-10-08 06:10 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17333 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2023-12258477 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-430 – T4-09-04 |  | FM008 |  | 2023-10-08 00:25 | 2023-10-08 01:25 | 2023-10-09 01:25 | 24 | 2023-10-08 00:30 | 2023-10-08 04:35 | 245 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12756205 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT - ROW NO 5 & COUNTER # 11 |  | FM008 |  | 2024-03-23 11:22 | 2024-03-23 12:22 | 2024-03-24 12:22 | 24 | 2024-03-23 11:30 | 2024-03-23 15:30 | 240 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12772239 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC HOT ROW 4 COUNTER 8 |  | FM008 |  | 2024-03-26 23:41 | 2024-03-27 00:41 | 2024-03-28 00:41 | 24 | 2024-03-26 23:46 | 2024-03-27 02:05 | 139 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 95217 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12777096 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT DEPARTURE CHECK IN ROW 4 ALL COUNTERS |  | FM008 |  | 2024-03-29 22:41 | 2024-03-29 23:41 | 2024-03-30 23:41 | 24 | 2024-03-29 22:47 | 2024-03-30 00:15 | 88 | 66 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 17053 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2024-12791531 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURESS ROW #4 COUNTER #9 |  | FM008 |  | 2024-04-02 23:04 | 2024-04-03 00:04 | 2024-04-04 00:04 | 24 | 2024-04-02 23:10 | 2024-04-03 00:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 17053 |  |  | 138251 | Bedoui, Mr. Afif | N - - - |  | Voice Communication
| CM-2024-12797125 | ASD-MTB-FOF011-AHU043 | AIR HANDLING UNIT-05 | AC TOO COLD ROW 7 COUNTER 3 - 7 |  | FM008 |  | 2024-04-05 04:28 | 2024-04-05 05:28 | 2024-04-06 05:28 | 24 | 2024-04-05 04:35 | 2024-04-05 06:45 | 130 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 142825 | Wamuyu, Ms. Linda Naserian | N - - - |  | Voice Communication
| CM-2022-10731642 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED T4-09-04 |  | FM008 |  | 2022-06-08 20:27 | 2022-06-08 21:27 | 2022-06-09 21:27 | 24 | 2022-06-08 20:35 | 2022-06-08 22:40 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 87807 | 87807 |  |  | FM1127 | Rahman, Mr. Mohammad Habibur | N - - - |  | Voice Communication
| CM-2022-10968966 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU-A1110-432 – DP2 FILTER ALARM |  | FM008 |  | 2022-08-24 07:43 | 2022-08-24 08:43 | 2022-08-25 08:43 | 24 | 2022-08-24 07:50 | 2022-08-24 11:45 | 235 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11067584 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | SUPPLY FAN V-BELT IS DAMAGED |  | FM008 |  | 2022-10-02 11:38 | 2022-10-02 12:38 | 2022-10-03 12:38 | 24 | 2022-10-02 11:46 | 2022-10-02 17:00 | 314 | 189 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11067585 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | RELIEF FAN V-BELT IS DAMAGED |  | FM008 |  | 2022-10-02 11:38 | 2022-10-02 12:38 | 2022-10-03 12:38 | 24 | 2022-10-02 11:46 | 2022-10-02 15:50 | 244 | 190 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11353178 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | DP3 – FILTER ALARM - AHU-A1110-432 – T4-09-04 |  | FM008 |  | 2023-01-07 02:24 | 2023-01-07 03:24 | 2023-01-08 03:24 | 24 | 2023-01-07 02:30 | 2023-01-07 05:05 | 155 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2024-12882363 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | NOISY FROM AC FAN - DEPARTURE INFORMATION DESK BETWEEN ROW # 4 & 5 AREA |  | FM008 |  | 2024-04-30 19:15 | 2024-04-30 20:15 | 2024-05-01 20:15 | 24 | 2024-04-30 19:20 | 2024-04-30 23:08 | 228 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 17573 | 87807 |  |  | T26823 | Pravinbhai, Mr. Krutarth | N - - - |  | Voice Communication
| CM-2022-11206765 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU-A1110-432 T4-09-04 CHILLED WATER LINE PAINT FADED AND CONDENSATE DRAIN INSULATION DAMAGED |  | FM008 |  | 2022-11-22 07:30 | 2022-11-22 08:30 | 2022-11-23 08:30 | 24 | 2022-11-22 07:35 | 2022-11-22 14:30 | 415 | 485 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 89127 | 17053 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-11218505 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM-MAIN TERMINAL BUILDING-FIRST FLOOR AREA 011 |  | FM008 |  | 2022-11-25 09:48 | 2022-11-25 10:48 | 2022-11-26 10:48 | 24 | 2022-11-25 09:55 | 2022-11-25 11:00 | 65 | 195 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11524355 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU-A1110-432 FILTER ALARM |  | FM008 |  | 2023-03-07 08:23 | 2023-03-07 09:23 | 2023-03-08 09:23 | 24 | 2023-03-07 08:30 | 2023-03-07 11:30 | 180 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 95217 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-12206490 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-09-21 11:04 | 2023-09-21 12:04 | 2023-09-22 12:04 | 24 | 2023-09-21 11:10 | 2023-09-21 13:00 | 110 | 310 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12228489 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU BEARING NOISY |  | FM008 |  | 2023-09-26 10:17 | 2023-09-26 11:17 | 2023-09-27 11:17 | 24 | 2023-09-26 10:25 | 2023-09-26 14:15 | 230 | 440 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 68060 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-11023955 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-09-04-AHU-A1110-432)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-09-14 10:10 | 2022-09-14 11:10 | 2022-09-15 11:10 | 24 | 2022-09-14 10:15 | 2022-09-14 11:40 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17336 | 87807 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-11131280 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-432 |  | FM008 |  | 2022-10-23 19:04 | 2022-10-23 20:04 | 2022-10-24 20:04 | 24 | 2022-10-23 19:10 | 2022-10-23 22:00 | 170 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11888215 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | HEAT WHEEL BELT DAMAGED-AIR HANDLING UNIT 045 (TAG NO:AHU-A1110-432)- |  | FM008 |  | 2023-06-17 13:41 | 2023-06-17 14:41 | 2023-06-18 14:41 | 24 | 2023-06-17 13:50 | 2023-06-17 17:00 | 190 | 290 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 87807 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-12232407 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | SUPPLY AND RELIEF BLOWER PAINT FADED -AHU-A1110-432)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-09-28 13:06 | 2023-09-28 14:06 | 2023-09-29 14:06 | 24 | 2023-09-28 13:10 | 2023-09-28 17:30 | 260 | 650 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17336 | 87807 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2023-12252184 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | DEPART=URE SCREENING AREA – AC TOO HOT - T2-11-40 (SEARCH ROOM)) |  | FM008 |  | 2023-10-02 13:25 | 2023-10-02 14:25 | 2023-10-03 14:25 | 24 | 2023-10-02 13:30 | 2023-10-02 20:00 | 390 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | CT13907 | DOUGLAS | N - - - |  | Voice Communication
| CM-2022-10343968 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 009 |  | FM008 |  | 2022-04-10 07:36 | 2022-04-10 08:36 | 2022-04-11 08:36 | 24 | 2022-04-10 07:45 | 2022-04-10 08:44 | 59 | 118 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10796525 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-432 T4-09-04 |  | FM008 |  | 2022-07-02 00:08 | 2022-07-02 01:08 | 2022-07-03 01:08 | 24 | 2022-07-02 00:15 | 2022-07-02 01:55 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 85125 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11040230 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-09-24 11:30 | 2022-09-24 12:30 | 2022-09-25 12:30 | 24 | 2022-09-24 11:40 | 2022-09-24 15:35 | 235 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10043327 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU-A1110-432 T4-09-04- AIR FILTER DIRTY |  | FM008 |  | 2022-01-12 00:25 | 2022-01-12 01:25 | 2022-01-13 01:25 | 24 | 2022-01-12 00:34 | 2022-01-12 03:30 | 176 | 156 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10119518 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU045 FILTER BLOCKED/DIRTY – T4-11-03 |  | FM008 |  | 2022-02-07 19:15 | 2022-02-07 20:15 | 2022-02-08 20:15 | 24 | 2022-02-07 19:25 | 2022-02-07 23:50 | 265 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106976 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10237429 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR AIR LEAKAGE AHU-A1110-432 T4-09-04 |  | FM008 |  | 2022-03-11 20:41 | 2022-03-11 21:41 | 2022-03-12 21:41 | 24 | 2022-03-11 20:45 | 2022-03-11 22:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 85125 | 17053 |  |  | FM7396 | Chowdhury, Mr. Biswajit | N - - - |  | Voice Communication
| CM-2022-10731165 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU-A1110-432 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-06-11 00:04 | 2022-06-11 01:04 | 2022-06-12 01:04 | 24 | 2022-06-11 00:10 | 2022-06-11 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68485 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10799088 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AHU-A1110-432 – FILTER DIRTY |  | FM008 |  | 2022-07-02 22:00 | 2022-07-02 23:00 | 2022-07-03 23:00 | 24 | 2022-07-02 22:12 | 2022-07-02 23:12 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 95217 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2023-12282195 | ASD-MTB-FOF011-AHU045 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 4 |  | FM008 |  | 2023-10-15 03:23 | 2023-10-15 04:23 | 2023-10-16 04:23 | 24 | 2023-10-15 03:30 | 2023-10-15 05:05 | 95 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 136942 | Kharbouche, Mr. Mohamed Yassir | N - - - |  | Voice Communication
| CM-2023-11340371 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-01-02 06:58 | 2023-01-02 07:58 | 2023-01-03 07:58 | 24 | 2023-01-02 07:05 | 2023-01-02 09:00 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12366804 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | FILTER DIRTY: -AIR HANDLING UNIT 047 (TAG NO:AHU-A1110-434)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2023-11-10 07:19 | 2023-11-10 08:19 | 2023-11-11 08:19 | 24 | 2023-11-10 07:25 | 2023-11-10 08:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 138627 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12505079 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY,AHU-A1110-434,T4-09-04 |  | FM008 |  | 2023-12-26 00:10 | 2023-12-26 01:10 | 2023-12-27 01:10 | 24 | 2023-12-26 00:15 | 2023-12-26 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11230636 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1110-434 |  | FM008 |  | 2022-11-30 00:08 | 2022-11-30 01:08 | 2022-12-01 01:08 | 24 | 2022-11-30 00:15 | 2022-11-30 04:40 | 265 | 425 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 124475 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11331322 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-434 T4-09-04 |  | FM008 |  | 2022-12-31 01:51 | 2022-12-31 02:51 | 2023-01-01 02:51 | 24 | 2022-12-31 02:00 | 2022-12-31 05:10 | 190 | 380 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11697386 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS(PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4FLRP4.MTB434.AHU434.SYSALM.DP3 --T4-11-03 |  | FM008 |  | 2023-04-25 11:06 | 2023-04-25 12:06 | 2023-04-26 12:06 | 24 | 2023-04-25 11:15 | 2023-04-25 15:30 | 255 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12509738 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | SUPPLY BLOWER NOISE – AHU-A1110-434) - |  | FM008 |  | 2023-12-26 11:30 | 2023-12-26 12:30 | 2023-12-27 12:30 | 24 | 2023-12-26 11:35 | 2023-12-26 16:50 | 315 | 725 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | BELT LOOSE | TIGHTENED THE BELT | 132112 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12596443 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | RETURN BELT DAMAGED, AHU-A1110-434, T4-09-04 |  | FM008 |  | 2024-01-28 00:07 | 2024-01-28 01:07 | 2024-01-29 01:07 | 24 | 2024-01-28 00:15 | 2024-01-28 04:15 | 240 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12285565 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | AHU-A1110-432 SUPPLY MOTOR OVERHEATING |  | FM008 |  | 2023-10-16 08:36 | 2023-10-16 09:36 | 2023-10-17 09:36 | 24 | 2023-10-16 08:45 | 2023-10-16 11:10 | 145 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | LACK OF LUBRICATION | REFILL WITH FUEL OR PRODUCT | 68485 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2022-9958634 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1110-434)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 011 |  | FM008 |  | 2022-01-03 23:58 | 2022-01-04 00:58 | 2022-01-05 00:58 | 24 | 2022-01-04 00:05 | 2022-01-04 02:55 | 170 | 340 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10023408 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | DRAINAGE LINE SUMP RUSTED - AHU-A1110-434 – T4-09-04 |  | FM008 |  | 2022-01-05 00:20 | 2022-01-05 01:20 | 2022-01-06 01:20 | 24 | 2022-01-05 00:28 | 2022-01-05 01:56 | 88 | 176 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106973 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-9959207 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | RELIEF BELT IS DAMAGED |  | FM008 |  | 2022-01-04 19:58 | 2022-01-04 20:58 | 2022-01-05 20:58 | 24 | 2022-01-04 20:05 | 2022-01-04 21:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10107679 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | RELEF SIDE BELT IS DAMAGED - AHU-A1110-434 - MECHANICAL ROOM T4-09-04 |  | FM008 |  | 2022-02-04 19:21 | 2022-02-04 20:21 | 2022-02-05 20:21 | 24 | 2022-02-04 19:31 | 2022-02-04 23:55 | 264 | 159 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10747148 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM AHU-A1110-434 T4-09-04 |  | FM008 |  | 2022-06-15 19:00 | 2022-06-15 20:00 | 2022-06-16 20:00 | 24 | 2022-06-15 19:05 | 2022-06-15 20:20 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 85125 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11041168 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-09-24 11:33 | 2022-09-24 12:33 | 2022-09-25 12:33 | 24 | 2022-09-24 11:40 | 2022-09-24 17:10 | 330 | 188 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11179318 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | RETURN GRILL DIRTY T3-11-15 |  | FM008 |  | 2022-11-10 12:55 | 2022-11-10 13:55 | 2022-11-11 13:55 | 24 | 2022-11-10 13:00 | 2022-11-10 15:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10692676 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | AC TOO NOISY |  | FM008 |  | 2022-05-25 09:23 | 2022-05-25 10:23 | 2022-05-26 10:23 | 24 | 2022-05-25 09:30 | 2022-05-25 10:10 | 40 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | VIBRATION DUE TO LOOSE PARTS OR BROKEN COMPONENTS | RECTIFIED | 68485 | 55709 |  |  | MOI | ASHRAF | N - - - |  | Voice Communication
| CM-2022-10910609 | ASD-MTB-FOF011-AHU047 | AIR HANDLING UNIT-05 | AHU-A1110-434 FILTER DIRTY T4-09-04 |  | FM008 |  | 2022-08-02 10:06 | 2022-08-02 11:06 | 2022-08-03 11:06 | 24 | 2022-08-02 10:15 | 2022-08-02 11:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 76858 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10994896 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | RETURN BELT DAMAGED - AHU-A1110-446 – T4-09-04 |  | FM008 |  | 2022-09-03 00:05 | 2022-09-03 01:05 | 2022-09-04 01:05 | 24 | 2022-09-03 00:10 | 2022-09-03 01:50 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12505080 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-12-26 00:10 | 2023-12-26 01:10 | 2023-12-27 01:10 | 24 | 2023-12-26 00:15 | 2023-12-26 04:00 | 225 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-11041468 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-09-04 |  | FM008 |  | 2022-09-24 07:00 | 2022-09-24 08:00 | 2022-09-25 08:00 | 24 | 2022-09-24 07:10 | 2022-09-24 10:10 | 180 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11249494 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED - AHU-A1110-446, 420 & 406 – T4-07-31 |  | FM008 |  | 2022-12-04 21:00 | 2022-12-04 22:00 | 2022-12-05 22:00 | 24 | 2022-12-04 21:10 | 2022-12-05 01:10 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 17053 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2022-11304223 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FUSED -T4-09-04 |  | FM008 |  | 2022-12-26 00:03 | 2022-12-26 01:03 | 2022-12-27 01:03 | 24 | 2022-12-26 00:10 | 2022-12-26 03:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 17333 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11299822 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-446 – T4-09-04 |  | FM008 |  | 2022-12-22 20:00 | 2022-12-22 21:00 | 2022-12-23 21:00 | 24 | 2022-12-22 20:10 | 2022-12-22 23:55 | 225 | 675 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11298497 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | RETURN AND SUPPLY V-BELT IS DAMAGED |  | FM008 |  | 2022-12-23 00:27 | 2022-12-23 01:27 | 2022-12-24 01:27 | 24 | 2022-12-23 00:35 | 2022-12-23 03:25 | 170 | 340 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11363447 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM, AHU-A1110-446, T4-11-06 |  | FM008 |  | 2023-01-12 07:34 | 2023-01-12 08:34 | 2023-01-13 08:34 | 24 | 2023-01-12 07:40 | 2023-01-12 08:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 55709 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12509551 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | SUPPLY BLOWER BEARING NOISY -T4-09-04 |  | FM008 |  | 2023-12-25 12:35 | 2023-12-25 13:35 | 2023-12-26 13:35 | 24 | 2023-12-25 12:45 | 2023-12-25 16:30 | 225 | 675 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-10711009 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | AHU-A1110-446 V BELT DAMAGED T4-09-04 |  | FM008 |  | 2022-06-01 08:36 | 2022-06-01 09:36 | 2022-06-02 09:36 | 24 | 2022-06-01 08:45 | 2022-06-01 10:00 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-11477274 | ASD-MTB-FOF011-AHU059 | AIR HANDLING UNIT-05 | FILTER ALARM – T4-09-04;MEC ROOM |  | FM008 |  | 2023-02-20 07:15 | 2023-02-20 08:15 | 2023-02-21 08:15 | 24 | 2023-02-20 07:20 | 2023-02-20 10:45 | 205 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 011 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2022-10922560 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED -T4-21-03 |  | FM008 |  | 2022-08-08 10:39 | 2022-08-08 11:39 | 2022-08-09 11:39 | 24 | 2022-08-08 10:45 | 2022-08-08 12:00 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 55709 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-10968965 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU-A1110-425 – DP3 FILTER ALARM |  | FM008 |  | 2022-08-24 07:42 | 2022-08-24 08:42 | 2022-08-25 08:42 | 24 | 2022-08-24 07:51 | 2022-08-24 13:00 | 309 | 139 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10987762 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY |  | FM008 |  | 2022-08-29 13:22 | 2022-08-29 14:22 | 2022-08-30 14:22 | 24 | 2022-08-29 13:30 | 2022-08-29 15:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2022-11206321 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING |  | FM008 |  | 2022-11-20 19:12 | 2022-11-20 20:12 | 2022-11-21 20:12 | 24 | 2022-11-20 19:20 | 2022-11-20 21:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11354275 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU-A1110-425- DP3- FILTER ALARM ACTIVATED-- |  | FM008 |  | 2023-01-07 08:45 | 2023-01-07 09:45 | 2023-01-08 09:45 | 24 | 2023-01-07 08:50 | 2023-01-07 11:15 | 145 | 290 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11827514 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-425 – T4-08-04 |  | FM008 |  | 2023-05-27 11:25 | 2023-05-27 12:25 | 2023-05-28 12:25 | 24 | 2023-05-27 11:32 | 2023-05-27 15:35 | 243 | 353 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12156912 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED - AHU-A1110-425 – T4-08-04 |  | FM008 |  | 2023-09-06 02:26 | 2023-09-06 03:26 | 2023-09-07 03:26 | 24 | 2023-09-06 02:32 | 2023-09-06 04:32 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10989648 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | V BELT DAMAGED AIR HANDLING UNIT 038 (TAG NO:AHU-A1110-425)- |  | FM008 |  | 2022-08-29 09:19 | 2022-08-29 10:19 | 2022-08-30 10:19 | 24 | 2022-08-29 09:28 | 2022-08-29 10:45 | 77 | 231 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 55709 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2023-11887490 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED |  | FM008 |  | 2023-06-17 10:06 | 2023-06-17 11:06 | 2023-06-18 11:06 | 24 | 2023-06-17 10:15 | 2023-06-17 12:28 | 133 | 241 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 95216 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11949308 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-08-04 |  | FM008 |  | 2023-07-05 19:27 | 2023-07-05 20:27 | 2023-07-06 20:27 | 24 | 2023-07-05 19:34 | 2023-07-05 23:50 | 256 | 147 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12166435 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | SUPPLY MOTOR FLEXIBLE HOSE DAMAGED - T4-21-01 |  | FM008 |  | 2023-09-09 16:13 | 2023-09-09 17:13 | 2023-09-10 17:13 | 24 | 2023-09-09 16:20 | 2023-09-09 18:49 | 149 | 298 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 95217 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2022-10988871 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU-A1110-425-SUPPLY AIR FLOW MISMATCH |  | FM008 |  | 2022-08-30 07:17 | 2022-08-30 08:17 | 2022-08-31 08:17 | 24 | 2022-08-30 07:25 | 2022-08-30 11:38 | 253 | 181 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 95217 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11062648 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - T4-21-08 |  | FM008 |  | 2022-09-28 00:44 | 2022-09-28 01:44 | 2022-09-29 01:44 | 24 | 2022-09-28 00:50 | 2022-09-28 02:15 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11940116 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | RELIEF BELT DAMAGED-T4-08-04 |  | FM008 |  | 2023-07-04 18:56 | 2023-07-04 19:56 | 2023-07-05 19:56 | 24 | 2023-07-04 19:03 | 2023-07-04 23:10 | 247 | 187 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12555861 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | T4-08-04 FILTER DIRTY AHU-A1110-425) |  | FM008 |  | 2024-01-14 07:40 | 2024-01-14 08:40 | 2024-01-15 08:40 | 24 | 2024-01-14 07:45 | 2024-01-14 13:45 | 360 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 138627 | 95217 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12343800 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | SUPPLY SIDE SPRING RUSTED |  | FM008 |  | 2023-11-01 19:14 | 2023-11-01 20:14 | 2023-11-02 20:14 | 24 | 2023-11-01 19:20 | 2023-11-01 20:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10120874 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU-A1110-425 FILTER BLOCKED – T4-10-03 |  | FM008 |  | 2022-02-08 19:02 | 2022-02-08 20:02 | 2022-02-09 20:02 | 24 | 2022-02-08 19:12 | 2022-02-08 20:45 | 93 | 279 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106976 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10830355 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU-A1110-425 DP1 FILTER ALARM T4-21-03 |  | FM008 |  | 2022-07-13 00:07 | 2022-07-13 01:07 | 2022-07-14 01:07 | 24 | 2022-07-13 00:10 | 2022-07-13 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10125003 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | RELIEF FUN FAIL ALARM-T4-21-03 |  | FM008 |  | 2022-02-12 14:36 | 2022-02-12 15:36 | 2022-02-13 15:36 | 24 | 2022-02-12 14:45 | 2022-02-12 17:04 | 139 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 55709 |  |  | FM7853 | Guilles, Mr. Ronel Balid | N - - - |  | Voice Communication
| CM-2022-10615632 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU-A1110-425 DP3 FILTER ALARM T4-21-03 |  | FM008 |  | 2022-05-05 13:13 | 2022-05-05 14:13 | 2022-05-06 14:13 | 24 | 2022-05-05 13:20 | 2022-05-05 14:20 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 85125 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10786737 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-27 07:02 | 2022-06-27 08:02 | 2022-06-28 08:02 | 24 | 2022-06-27 07:12 | 2022-06-27 08:42 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11654618 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1110-425, T4-21-08 |  | FM008 |  | 2023-04-12 07:20 | 2023-04-12 08:20 | 2023-04-13 08:20 | 24 | 2023-04-12 07:25 | 2023-04-12 09:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12155182 | ASD-MTB-FOF021-AHU038 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-09-06 20:20 | 2023-09-06 21:20 | 2023-09-07 21:20 | 24 | 2023-09-06 20:25 | 2023-09-06 22:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10147326 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435 FILTER DIRTY |  | FM008 |  | 2022-02-18 00:16 | 2022-02-18 01:16 | 2022-02-19 01:16 | 24 | 2022-02-18 00:25 | 2022-02-18 02:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11822583 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | FILTER DIRTY - T4-08-04 |  | FM008 |  | 2023-05-23 11:03 | 2023-05-23 12:03 | 2023-05-24 12:03 | 24 | 2023-05-23 11:07 | 2023-05-23 12:47 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12117885 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | SUPPLY AIRFLOW SENSOR VALUE MISMATCH |  | FM008 |  | 2023-08-27 15:26 | 2023-08-27 16:26 | 2023-08-28 16:26 | 24 | 2023-08-27 15:35 | 2023-08-28 01:30 | 595 | 465 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | SENSOR FAILURE | REPAIR/REPLACE | 95216 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12327914 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | SUPPLY MOTOR AND BLOWER BASE SPRING IS RUSTED |  | FM008 |  | 2023-10-29 00:16 | 2023-10-29 01:16 | 2023-10-30 01:16 | 24 | 2023-10-29 00:25 | 2023-10-29 04:15 | 230 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12478710 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU MOTOR & BLOWER BERAING NOISY - AHU-A1110-435 – T4-08-04 |  | FM008 |  | 2023-12-14 08:02 | 2023-12-14 09:02 | 2023-12-15 09:02 | 24 | 2023-12-14 08:10 | 2023-12-14 14:10 | 360 | 1080 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17573 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-11153933 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY AHU-A1110-435 |  | FM008 |  | 2022-10-30 16:25 | 2022-10-30 17:25 | 2022-10-31 17:25 | 24 | 2022-10-30 16:30 | 2022-10-30 17:59 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106972 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12483153 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY – AHU-A1110-435 – T4-21-01 |  | FM008 |  | 2023-12-14 13:55 | 2023-12-14 14:55 | 2023-12-15 14:55 | 24 | 2023-12-14 14:05 | 2023-12-14 16:50 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12727642 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | A/C IS TOO HOT AT ROW 5 |  | FM008 |  | 2024-03-13 17:30 | 2024-03-13 18:30 | 2024-03-14 18:30 | 24 | 2024-03-13 17:35 | 2024-03-13 18:35 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2022-11006014 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435-DP3 FILETR ALARM |  | FM008 |  | 2022-09-10 00:17 | 2022-09-10 01:17 | 2022-09-11 01:17 | 24 | 2022-09-10 00:25 | 2022-09-10 04:20 | 235 | 305 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95217 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11062623 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435 DP1 FILTER DIRTY |  | FM008 |  | 2022-09-27 19:23 | 2022-09-27 20:23 | 2022-09-28 20:23 | 24 | 2022-09-27 19:32 | 2022-09-27 23:55 | 263 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11193585 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED AHU-A1110-435 |  | FM008 |  | 2022-11-17 00:28 | 2022-11-17 01:28 | 2022-11-18 01:28 | 24 | 2022-11-17 00:35 | 2022-11-17 03:00 | 145 | 435 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11694068 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435 LIGHTING SWITCH DAMAGED |  | FM008 |  | 2023-04-23 13:16 | 2023-04-23 14:16 | 2023-04-24 14:16 | 24 | 2023-04-23 13:25 | 2023-04-23 15:24 | 119 | 238 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 106972 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12513513 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - T4-08-04 |  | FM008 |  | 2023-12-30 00:28 | 2023-12-30 01:28 | 2023-12-31 01:28 | 24 | 2023-12-30 00:35 | 2023-12-30 05:00 | 265 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 17053 |  |  | FM12459 | Devaraj Dhanabalan, | N - - - |  | Voice Communication
| CM-2022-10098154 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435 SUPLLY BELT LOOSE T4-21-03 |  | FM008 |  | 2022-01-31 14:00 | 2022-01-31 15:00 | 2022-02-01 15:00 | 24 | 2022-01-31 14:10 | 2022-01-31 15:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 89127 | 55709 |  |  | FM9671 | Karunagoda Mudalige, Mr. Kasun Lakmal | N - - - |  | Voice Communication
| CM-2022-10202578 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | FRESH AIR DUCT INSULATION DAMAGED - AHU-A1110-435 – T4-21-03 |  | FM008 |  | 2022-03-01 22:17 | 2022-03-01 23:17 | 2022-03-02 23:17 | 24 | 2022-03-01 22:27 | 2022-03-01 23:45 | 78 | 156 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10919171 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435 – DP3 FILTER ALARM-- |  | FM008 |  | 2022-08-09 07:20 | 2022-08-09 08:20 | 2022-08-10 08:20 | 24 | 2022-08-09 07:30 | 2022-08-09 08:25 | 55 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10669579 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU-A1110-435 AHU DRAIN BLOCKED FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-05-17 01:42 | 2022-05-17 02:42 | 2022-05-18 02:42 | 24 | 2022-05-17 01:50 | 2022-05-17 03:30 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17053 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10713624 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU DRAIN LINE IS RUSTED - AHU-A1110-435 - T4-08-04 |  | FM008 |  | 2022-06-03 20:47 | 2022-06-03 21:47 | 2022-06-04 21:47 | 24 | 2022-06-03 20:55 | 2022-06-03 22:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM9663 | Amarasingha Arachchilage, Mr. Priyanga Madura | N - - - |  | Voice Communication
| CM-2022-10903875 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | AHU FILTER ALARM |  | FM008 |  | 2022-08-02 19:10 | 2022-08-02 20:10 | 2022-08-03 20:10 | 24 | 2022-08-02 19:20 | 2022-08-02 22:45 | 205 | 255 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 76858 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11935389 | ASD-MTB-FOF021-AHU048 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-435 |  | FM008 |  | 2023-07-01 06:49 | 2023-07-01 07:49 | 2023-07-02 07:49 | 24 | 2023-07-01 06:55 | 2023-07-01 08:30 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | BMS
| CM-2022-10147327 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU-A1110-437 FILTER DIRTY |  | FM008 |  | 2022-02-18 00:16 | 2022-02-18 01:16 | 2022-02-19 01:16 | 24 | 2022-02-18 00:26 | 2022-02-18 04:45 | 259 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10201696 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT ILLUMINATING INSIDE AHU SUPPLY SIDE - AHU-A1110-437 – T4-21-03 |  | FM008 |  | 2022-03-01 22:16 | 2022-03-01 23:16 | 2022-03-02 23:16 | 24 | 2022-03-01 22:20 | 2022-03-01 23:30 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-11064415 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-09-28 10:32 | 2022-09-28 11:32 | 2022-09-29 11:32 | 24 | 2022-09-28 10:40 | 2022-09-28 12:00 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11201797 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING - AHU-A1110-437 T4-21-03 |  | FM008 |  | 2022-11-20 21:33 | 2022-11-20 22:33 | 2022-11-21 22:33 | 24 | 2022-11-20 21:40 | 2022-11-20 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11483592 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | SUPPLY BLOWER NOISY – AHU-A1110-437, T4-21-10 |  | FM008 |  | 2023-02-23 09:31 | 2023-02-23 10:31 | 2023-02-24 10:31 | 24 | 2023-02-23 09:40 | 2023-02-23 18:30 | 530 | 380 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12062556 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU-A1110-437-FILTER DIRTYMTB--FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-08-08 07:42 | 2023-08-08 08:42 | 2023-08-09 08:42 | 24 | 2023-08-08 07:50 | 2023-08-08 17:05 | 555 | 370 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11065259 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU-A1110-437 RELIEF SIDE BELT DAMAGED |  | FM008 |  | 2022-09-30 00:05 | 2022-09-30 01:05 | 2022-10-01 01:05 | 24 | 2022-09-30 00:10 | 2022-09-30 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 95217 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11267368 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED (AHU-443&425) |  | FM008 |  | 2022-12-13 07:50 | 2022-12-13 08:50 | 2022-12-14 08:50 | 24 | 2022-12-13 08:00 | 2022-12-13 11:00 | 180 | 650 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11823165 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-25 10:19 | 2023-05-25 11:19 | 2023-05-26 11:19 | 24 | 2023-05-25 10:25 | 2023-05-25 12:20 | 115 | 345 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12014148 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING |  | FM008 |  | 2023-07-25 19:16 | 2023-07-25 20:16 | 2023-07-26 20:16 | 24 | 2023-07-25 19:20 | 2023-07-25 21:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12040480 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1110-437 |  | FM008 |  | 2023-07-31 19:05 | 2023-07-31 20:05 | 2023-08-01 20:05 | 24 | 2023-07-31 19:10 | 2023-07-31 21:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10914573 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU-A1110-437 FILTER ALARM T4-21-03 |  | FM008 |  | 2022-08-04 19:07 | 2022-08-04 20:07 | 2022-08-05 20:07 | 24 | 2022-08-04 19:15 | 2022-08-05 00:50 | 335 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12686278 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | SUPPLY MOTOR AND BLOWER NOISY AHU-A1110-437 T4-08-04 |  | FM008 |  | 2024-02-29 09:14 | 2024-02-29 10:14 | 2024-03-01 10:14 | 24 | 2024-02-29 09:20 | 2024-02-29 12:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 68485 | 17053 |  |  | FM12459 | Devaraj Dhanabalan, | N - - - |  | Voice Communication
| CM-2023-12342008 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED |  | FM008 |  | 2023-10-31 00:04 | 2023-10-31 01:04 | 2023-11-01 01:04 | 24 | 2023-10-31 00:10 | 2023-10-31 04:15 | 245 | 455 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12611700 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | SUPPLY SIDE BEARING NOISY, AHU-A1110-437 , T4-08-04 |  | FM008 |  | 2024-02-01 09:15 | 2024-02-01 10:15 | 2024-02-02 10:15 | 24 | 2024-02-01 09:20 | 2024-02-01 13:20 | 240 | 960 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 124475 | 17053 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2023-12343801 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | SUPPLY SIDE SPRING RUSTED |  | FM008 |  | 2023-11-01 19:15 | 2023-11-01 20:15 | 2023-11-02 20:15 | 24 | 2023-11-01 19:20 | 2023-11-01 20:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | UNIT IS RUSTED | CLEANED & REPAINT THE UNIT | 121959 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2024-12634247 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU DP1 FILTER DIRTY - AHU-A1110-437 – TG-08-04 |  | FM008 |  | 2024-02-10 03:06 | 2024-02-10 04:06 | 2024-02-11 04:06 | 24 | 2024-02-10 03:10 | 2024-02-10 05:00 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 133396 | 17053 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2022-10102926 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU DRAIN LINE IS BLOCKED - AHU-A1110-437 - T4-21-04 |  | FM008 |  | 2022-01-31 15:30 | 2022-01-31 16:30 | 2022-02-01 16:30 | 24 | 2022-01-31 15:39 | 2022-01-31 17:15 | 96 | 192 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 55709 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2022-10959346 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | CHILLED WATER INSULATION DAMAGED - AHU-A1110-437 |  | FM008 |  | 2022-08-23 07:36 | 2022-08-23 08:36 | 2022-08-24 08:36 | 24 | 2022-08-23 07:40 | 2022-08-23 09:00 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10669580 | ASD-MTB-FOF021-AHU050 | AIR HANDLING UNIT-05 | AHU BELT LOOSE FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-05-17 01:43 | 2022-05-17 02:43 | 2022-05-18 02:43 | 24 | 2022-05-17 01:50 | 2022-05-17 03:30 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 17053 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10874260 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AHU-A1110-439 MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-07-27 19:11 | 2022-07-27 20:11 | 2022-07-28 20:11 | 24 | 2022-07-27 19:15 | 2022-07-27 20:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11178096 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING - AHU-A1110-439 – T4-21-03 |  | FM008 |  | 2022-11-12 19:13 | 2022-11-12 20:13 | 2022-11-13 20:13 | 24 | 2022-11-12 19:20 | 2022-11-12 21:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-12014930 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | AHU-A1110-439)-CABIN LAMP NOT WORKING -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-07-28 19:17 | 2023-07-28 20:17 | 2023-07-29 20:17 | 24 | 2023-07-28 19:25 | 2023-07-29 01:00 | 335 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 77406 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12824137 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS, AHU-A1110-439, MECHANICAL ROOM T4-21-03 |  | FM008 |  | 2024-04-13 11:02 | 2024-04-13 12:02 | 2024-04-14 12:02 | 24 | 2024-04-13 11:05 | 2024-04-13 18:05 | 420 | 245 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-11065260 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | AHU-A1110-439 SUPPLY MOTOR BLOWER BASE SPRING DAMAGED |  | FM008 |  | 2022-09-30 00:06 | 2022-09-30 01:06 | 2022-10-01 01:06 | 24 | 2022-09-30 00:12 | 2022-09-30 01:42 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 68485 | 95217 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11062647 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY - T4-21-03 |  | FM008 |  | 2022-09-28 00:43 | 2022-09-28 01:43 | 2022-09-29 01:43 | 24 | 2022-09-28 00:50 | 2022-09-28 02:15 | 85 | 255 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11822321 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | AHU-A1110-439 FILTER IS DIRTY |  | FM008 |  | 2023-05-22 10:46 | 2023-05-22 11:46 | 2023-05-23 11:46 | 24 | 2023-05-22 10:53 | 2023-05-22 15:00 | 247 | 337 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10147123 | ASD-MTB-FOF021-AHU052 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-02-17 00:07 | 2022-02-17 01:07 | 2022-02-18 01:07 | 24 | 2022-02-17 00:16 | 2022-02-17 02:16 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10272468 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE ROW #10 AREA |  | FM008 |  | 2022-03-21 15:29 | 2022-03-21 16:29 | 2022-03-22 16:29 | 24 | 2022-03-21 15:35 | 2022-03-21 17:15 | 100 | 45 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17573 | 87807 |  |  | 72839 | Roy, Mr. Sumit | N - - - |  | Voice Communication
| CM-2022-10690010 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-05-22 19:09 | 2022-05-22 20:09 | 2022-05-23 20:09 | 24 | 2022-05-22 19:15 | 2022-05-22 21:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10777563 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU –A1110-441 – DP1 FILTER ALARM – T4-21-03 |  | FM008 |  | 2022-06-26 07:10 | 2022-06-26 08:10 | 2022-06-27 08:10 | 24 | 2022-06-26 07:15 | 2022-06-26 13:50 | 395 | 165 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10886866 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC IS TOO COLD -DEPARTURE ROW 10 -WHOLE ROW -MAIN TERMINAL BUILDING-SECOND FLOOR AREA 014 |  | FM008 |  | 2022-07-30 00:48 | 2022-07-30 01:48 | 2022-07-31 01:48 | 24 | 2022-07-30 00:55 | 2022-07-30 06:50 | 355 | 40 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 87807 |  |  | 107576 | Hichri, Ms. Amira | N - - - |  | Voice Communication
| CM-2022-11145919 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | INSIDE AHU LIGHTS NOT WORKING -AHU-A1110-441)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-10-30 01:45 | 2022-10-30 02:45 | 2022-10-31 02:45 | 24 | 2022-10-30 01:50 | 2022-10-30 02:20 | 30 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17336 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12300153 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK IN ROW 10 BRNING SMELL |  | FM008 |  | 2023-10-20 02:50 | 2023-10-20 03:20 | 2023-10-20 07:20 | 4 | 2023-10-20 03:00 | 2023-10-20 12:30 | 570 | 1190 | 6 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 021 | N | BADSMELL | CLOGGED AIR FILTER | CLEANED/REPLACED | 68060 | 87807 |  |  | 72845 | Aseem, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12298568 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC NOT COOLING - DEPARTURE CHECK-IN ROW #9 |  | FM008 |  | 2023-10-20 11:38 | 2023-10-20 12:38 | 2023-10-21 12:38 | 24 | 2023-10-20 11:45 | 2023-10-20 13:15 | 90 | 20 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17573 | 87807 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2023-12448153 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | PULLEY RUNOUT - AHU-A1110-441 – T4-08-04 |  | FM008 |  | 2023-12-06 09:45 | 2023-12-06 10:45 | 2023-12-07 10:45 | 24 | 2023-12-06 09:50 | 2023-12-06 13:45 | 235 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17573 | 17053 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-12464763 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | BASE ADJUSTING BOLT LOOSE |  | FM008 |  | 2023-12-12 08:34 | 2023-12-12 09:34 | 2023-12-13 09:34 | 24 | 2023-12-12 08:40 | 2023-12-12 11:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 121959 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2023-12504900 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | ROW NO 10 AC TOO COLD FROM COUNTER 12-14 |  | FM008 |  | 2023-12-25 07:44 | 2023-12-25 08:44 | 2023-12-26 08:44 | 24 | 2023-12-25 07:50 | 2023-12-25 11:50 | 240 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 111238 | Munaki, Ms. Ruth Zoe | N - - - |  | Voice Communication
| CM-2024-12556947 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT CHECKIN ROW 10 COUNTER 10 |  | FM008 |  | 2024-01-14 15:29 | 2024-01-14 16:29 | 2024-01-15 16:29 | 24 | 2024-01-14 15:35 | 2024-01-14 17:30 | 115 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 95217 |  |  | 83391 | Gowda, Mr. Sandesh Ramesh | N - - - |  | Voice Communication
| CM-2024-12591443 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK IN HALL ROW # 10 AC TOO HOT |  | FM008 |  | 2024-01-22 15:16 | 2024-01-22 16:16 | 2024-01-23 16:16 | 24 | 2024-01-22 15:25 | 2024-01-22 19:15 | 230 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | 83391 | Gowda, Mr. Sandesh Ramesh | N - - - |  | Voice Communication
| CM-2024-12727158 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK IN ROW 10 – AC TOO HOT |  | FM008 |  | 2024-03-11 16:16 | 2024-03-11 17:16 | 2024-03-12 17:16 | 24 | 2024-03-11 16:20 | 2024-03-11 20:00 | 220 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | 116586 | Assisi, Mr. Jaison Sanu | N - - - |  | Voice Communication
| CM-2024-12822583 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC NOT WORKING -ROW 10 |  | FM008 |  | 2024-04-13 06:43 | 2024-04-13 07:43 | 2024-04-14 07:43 | 24 | 2024-04-13 06:48 | 2024-04-13 09:00 | 132 | 62 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 17333 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2022-11095933 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE GATE 4 AROUND COUNTER NO 10&9 OPEN AREA |  | FM008 |  | 2022-10-11 15:09 | 2022-10-11 16:09 | 2022-10-12 16:09 | 24 | 2022-10-11 15:15 | 2022-10-11 17:00 | 105 | 40 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 92544 | Kabu, Ms. Anne Wanjiku | N - - - |  | Voice Communication
| CM-2022-11113696 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD -DEPARTURE ROW 10 |  | FM008 |  | 2022-10-20 01:06 | 2022-10-20 02:06 | 2022-10-21 02:06 | 24 | 2022-10-20 01:15 | 2022-10-20 06:50 | 335 | 30 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 100756 | MARIAM | N - - - |  | Voice Communication
| CM-2022-11268226 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -T4-21-04 |  | FM008 |  | 2022-12-12 10:09 | 2022-12-12 11:09 | 2022-12-13 11:09 | 24 | 2022-12-12 10:15 | 2022-12-12 14:00 | 225 | 450 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-11480017 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARM , AHU-A1110-441 , T4-21-03 |  | FM008 |  | 2023-02-24 07:02 | 2023-02-24 08:02 | 2023-02-25 08:02 | 24 | 2023-02-24 07:10 | 2023-02-24 10:10 | 180 | 260 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11611580 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU-A1110-441- FILTER DIRTY -T4-21-03 |  | FM008 |  | 2023-03-30 19:30 | 2023-03-30 20:30 | 2023-03-31 20:30 | 24 | 2023-03-30 19:35 | 2023-03-30 21:10 | 95 | 285 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 87807 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11768749 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC IS TOO COLD -T2-22-08 |  | FM008 |  | 2023-05-08 08:45 | 2023-05-08 09:45 | 2023-05-09 09:45 | 24 | 2023-05-08 08:50 | 2023-05-08 09:45 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17336 | 87807 |  |  | 13381 | Ibrahim, Ms. Farida | N - - - |  | Voice Communication
| CM-2023-12140240 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU MOTOR NOT WORKING - AHU-A1110-441 – T4 08 04 |  | FM008 |  | 2023-09-03 07:21 | 2023-09-03 08:21 | 2023-09-04 08:21 | 24 | 2023-09-03 07:30 | 2023-09-03 13:30 | 360 | 2160 | 6 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12251639 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD AND NOISY – CHECK IN ROW 7&10 |  | FM008 |  | 2023-10-02 01:39 | 2023-10-02 02:39 | 2023-10-03 02:39 | 24 | 2023-10-02 01:45 | 2023-10-02 05:50 | 245 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 118773 | Wanjiru, Mr. Samuel Ngugi | N - - - |  | Voice Communication
| CM-2023-12322080 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC NOT WORKING – T2-22-10 |  | FM008 |  | 2023-10-26 10:16 | 2023-10-26 11:16 | 2023-10-27 11:16 | 24 | 2023-10-26 10:25 | 2023-10-26 15:20 | 295 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 87807 |  |  | 114161 | Devnani, Mr. Kush Vishinkumar | N - - - |  | Voice Communication
| CM-2023-12341850 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD -CHECK IN ROW # 10 |  | FM008 |  | 2023-10-30 10:53 | 2023-10-30 11:53 | 2023-10-31 11:53 | 24 | 2023-10-30 11:00 | 2023-10-30 12:15 | 75 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 87807 |  |  | 111583 | Matiko, Ms. Mary Otaigo | N - - - |  | Voice Communication
| CM-2023-12513633 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TEMP VERY COLD - T2-22-10 (OFFICE)) |  | FM008 |  | 2023-12-30 14:14 | 2023-12-30 15:14 | 2023-12-31 15:14 | 24 | 2023-12-30 14:20 | 2023-12-30 15:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 77406 | 17053 |  |  | 126908 | Kaur, Ms. Manpreet | N - - - |  | E-mail
| CM-2024-12675116 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT - DEPARTURE ROW #9 COUNTER AREA |  | FM008 |  | 2024-02-24 17:13 | 2024-02-24 18:13 | 2024-02-25 18:13 | 24 | 2024-02-24 17:20 | 2024-02-24 23:59 | 399 | 32 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 83391 | Gowda, Mr. Sandesh Ramesh | N - - - |  | Voice Communication
| CM-2024-12791877 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | T2-22-10-AC TEMP VERY COLD |  | FM008 |  | 2024-04-04 07:32 | 2024-04-04 08:32 | 2024-04-05 08:32 | 24 | 2024-04-04 07:40 | 2024-04-04 10:10 | 150 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 77406 | 17053 |  |  | 126908 | Kaur, Ms. Manpreet | N - - - |  | Voice Communication
| CM-2024-12831426 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | T2-22-10 DEP ROW 9 AC TOO COLD |  | FM008 |  | 2024-04-18 08:06 | 2024-04-18 09:06 | 2024-04-19 09:06 | 24 | 2024-04-18 08:10 | 2024-04-18 14:25 | 375 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 126908 | Kaur, Ms. Manpreet | N - - - |  | Voice Communication
| CM-2024-12861835 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT CHECKIN ROW 10 COUNTER 12,13,14 |  | FM008 |  | 2024-04-29 14:17 | 2024-04-29 15:17 | 2024-04-30 15:17 | 24 | 2024-04-29 14:20 | 2024-04-29 17:00 | 160 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 123699 | Rai, Ms. Rubi | N - - - |  | Voice Communication
| CM-2022-11063598 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1110-441 |  | FM008 |  | 2022-09-28 07:21 | 2022-09-28 08:21 | 2022-09-29 08:21 | 24 | 2022-09-28 07:30 | 2022-09-28 10:30 | 180 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11103677 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | ROW 10 COUNTER 1 TO 5 AC TOO COLD |  | FM008 |  | 2022-10-16 01:01 | 2022-10-16 02:01 | 2022-10-17 02:01 | 24 | 2022-10-16 01:10 | 2022-10-16 05:30 | 260 | 55 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 17053 |  |  | T22062 | Ghosh, Ms. Shreyadrita | N - - - |  | Voice Communication
| CM-2022-11131281 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-441 |  | FM008 |  | 2022-10-23 19:05 | 2022-10-23 20:05 | 2022-10-24 20:05 | 24 | 2022-10-23 19:15 | 2022-10-23 23:45 | 270 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11327311 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -(AHU-A1110-441) - AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-12-28 01:25 | 2022-12-28 02:25 | 2022-12-29 02:25 | 24 | 2022-12-28 01:35 | 2022-12-28 03:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11859161 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT - AMERICAN TOURISTER SHOP- BETWEEN ROW 8 AND 9 |  | FM008 |  | 2023-06-06 01:49 | 2023-06-06 02:49 | 2023-06-07 02:49 | 24 | 2023-06-06 01:55 | 2023-06-06 05:20 | 205 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 121959 | 94954 |  |  | CT17583 | JONATHAN | N - - - |  | Voice Communication
| CM-2023-11883417 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT INSIDE T2-22-10 ,MAIN TERMINAL BUILDING-SECOND FLOOR AREA 022 |  | FM008 |  | 2023-06-14 11:24 | 2023-06-14 12:24 | 2023-06-15 12:24 | 24 | 2023-06-14 11:33 | 2023-06-14 14:20 | 167 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ATUACTOR DAMAGE | REPLACED THE COIL | 124475 | 87807 |  |  | 114161 | Devnani, Mr. Kush Vishinkumar | N - - - |  | Voice Communication
| CM-2023-11940117 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | FILTER DIRTY - T4-08-04 |  | FM008 |  | 2023-07-04 18:58 | 2023-07-04 19:58 | 2023-07-05 19:58 | 24 | 2023-07-04 19:06 | 2023-07-04 21:35 | 149 | 187 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12141012 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT - T2-22-10 |  | FM008 |  | 2023-09-03 05:18 | 2023-09-03 06:18 | 2023-09-04 06:18 | 24 | 2023-09-03 05:25 | 2023-09-03 07:45 | 140 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 133396 | 87807 |  |  | 128975 | Bringues, Ms. May Ann Cantomayor | N - - - |  | Voice Communication
| CM-2024-12536323 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT SUPPLY BLOWER PULLEY RUN OUT - T4-08-04 |  | FM008 |  | 2024-01-04 13:57 | 2024-01-04 14:57 | 2024-01-05 14:57 | 24 | 2024-01-04 14:05 | 2024-01-04 18:00 | 235 | 155 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17053 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2024-12595620 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -T4-08-04 |  | FM008 |  | 2024-01-27 00:07 | 2024-01-27 01:07 | 2024-01-28 01:07 | 24 | 2024-01-27 00:15 | 2024-01-27 03:50 | 215 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12599264 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT T2-22-10 |  | FM008 |  | 2024-01-28 10:50 | 2024-01-28 11:50 | 2024-01-29 11:50 | 24 | 2024-01-28 10:55 | 2024-01-28 13:40 | 165 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 11065 | Joseph, Mr. Joy | N - - - |  | Voice Communication
| CM-2024-12825824 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT IN ROW-9 COUNTER-5 |  | FM008 |  | 2024-04-14 15:56 | 2024-04-14 16:56 | 2024-04-15 16:56 | 24 | 2024-04-14 16:00 | 2024-04-14 23:15 | 435 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 124475 | 17053 |  |  | 46249 | Rangagodage, Ms. Pathini De Silva Nape | N - - - |  | Voice Communication
| CM-2023-12340869 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD-T2-22-10 |  | FM008 |  | 2023-10-30 15:51 | 2023-10-30 16:51 | 2023-10-31 16:51 | 24 | 2023-10-30 15:55 | 2023-10-30 18:45 | 170 | 52 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 87807 |  |  | 117830 | Fouzul Ameer, Mr. Mohammed Osman | N - - - |  | Voice Communication
| CM-2023-12406919 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD - DEAPRTURE CHECK-IN ROW 10 AREA |  | FM008 |  | 2023-11-23 03:57 | 2023-11-23 04:57 | 2023-11-24 04:57 | 24 | 2023-11-23 04:00 | 2023-11-23 06:40 | 160 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 120428 | Kanjori, Mr. Mohamoud Mohamed | N - - - |  | Voice Communication
| CM-2023-12484856 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK IN ROW NO 10 AC TO COLD |  | FM008 |  | 2023-12-17 08:55 | 2023-12-17 09:55 | 2023-12-18 09:55 | 24 | 2023-12-17 09:00 | 2023-12-17 13:40 | 280 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 17053 |  |  | 137937 | Bendjeddou, Ms. Zina | N - - - |  | Voice Communication
| CM-2023-12488605 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD IN CHECK IN ROW NO 10 |  | FM008 |  | 2023-12-20 05:25 | 2023-12-20 06:25 | 2023-12-21 06:25 | 24 | 2023-12-20 05:30 | 2023-12-20 06:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 110866 | Mehri, Ms. Sahar | N - - - |  | Voice Communication
| CM-2024-12713739 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | ROW 9 COUNTER 7 AC TOO HOT |  | FM008 |  | 2024-03-08 14:32 | 2024-03-08 15:32 | 2024-03-09 15:32 | 24 | 2024-03-08 14:35 | 2024-03-08 15:30 | 55 | 55 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106972 | 17053 |  |  | T23661 | Jalaludeen, Mr. Jasid | N - - - |  | Voice Communication
| CM-2024-12789999 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU-A1110-441 DP1 FINAL FILTER STATUS |  | FM008 |  | 2024-04-01 10:37 | 2024-04-01 11:37 | 2024-04-02 11:37 | 24 | 2024-04-01 10:45 | 2024-04-01 15:35 | 290 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-12300163 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | A/C IS TOO HOT T2-22-10 |  | FM008 |  | 2023-10-20 03:46 | 2023-10-20 04:46 | 2023-10-21 04:46 | 24 | 2023-10-20 03:50 | 2023-10-20 13:15 | 565 | 20 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 87807 |  |  | 11065 | Joseph, Mr. Joy | N - - - |  | Voice Communication
| CM-2023-12302781 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC NOT WORKING - T2-22-10 |  | FM008 |  | 2023-10-20 23:58 | 2023-10-21 00:58 | 2023-10-22 00:58 | 24 | 2023-10-21 00:05 | 2023-10-21 02:06 | 121 | 70 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 133396 | 87807 |  |  | 128975 | Bringues, Ms. May Ann Cantomayor | N - - - |  | Voice Communication
| CM-2023-12358541 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK IN ROW 10 – AC TOO COLD |  | FM008 |  | 2023-11-07 03:16 | 2023-11-07 04:16 | 2023-11-08 04:16 | 24 | 2023-11-07 03:20 | 2023-11-07 06:15 | 175 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 101413 | Hewagamage Dona, Ms. Shalani Ann Lakshani | N - - - |  | Voice Communication
| CM-2024-12545470 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK IN ROW 10 - AC TOO HOT |  | FM008 |  | 2024-01-07 15:42 | 2024-01-07 16:42 | 2024-01-08 16:42 | 24 | 2024-01-07 15:50 | 2024-01-07 16:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 83391 | Gowda, Mr. Sandesh Ramesh | N - - - |  | Voice Communication
| CM-2024-12553705 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | A/C BLOWER AIR BLOWING HIGH |  | FM008 |  | 2024-01-11 06:19 | 2024-01-11 07:19 | 2024-01-12 07:19 | 24 | 2024-01-11 06:25 | 2024-01-11 09:35 | 190 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | BLOCKAGE OF AIR FLOW | REPAIR/REPLACE | 95216 | 17053 |  |  | 115104 | Badtya, Mr. Raj Kumar | N - - - |  | Voice Communication
| CM-2024-12690598 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT - MT-2009 AMERICAN TOURIST |  | FM008 |  | 2024-02-28 01:17 | 2024-02-28 02:17 | 2024-02-29 02:17 | 24 | 2024-02-28 01:25 | 2024-02-28 04:40 | 195 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 131403 | Ranwala Liyana Arachchige Don, Mr. Madura Nandana Pushpakumara | N - - - |  | Voice Communication
| CM-2024-12700075 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT - ROW # 9 & COUNTER NO 7 |  | FM008 |  | 2024-03-05 12:36 | 2024-03-05 13:36 | 2024-03-06 13:36 | 24 | 2024-03-05 12:45 | 2024-03-05 13:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 83391 | Gowda, Mr. Sandesh Ramesh | N - - - |  | Voice Communication
| CM-2024-12791784 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT – DEPARTURE CHECK IN ROW 9 COUNTER 7 |  | FM008 |  | 2024-04-03 16:57 | 2024-04-03 17:57 | 2024-04-04 17:57 | 24 | 2024-04-03 17:05 | 2024-04-03 22:58 | 353 | 63 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 133396 | 17053 |  |  | 86129 | Moratalla, Ms. Mara Meliz Grabillo | N - - - |  | Voice Communication
| CM-2024-12821665 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD – ROW 10, COUNTER 12 TO 13 |  | FM008 |  | 2024-04-11 03:11 | 2024-04-11 04:11 | 2024-04-12 04:11 | 24 | 2024-04-11 03:15 | 2024-04-11 05:10 | 115 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 87807 |  |  | 110997 | Mohamed, Ms. Shukri Abdi | N - - - |  | Voice Communication
| CM-2024-12810766 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | CHECK-IN ROW 5 AC TOO HOT |  | FM008 |  | 2024-04-10 15:26 | 2024-04-10 16:26 | 2024-04-11 16:26 | 24 | 2024-04-10 15:30 | 2024-04-10 17:30 | 120 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 138627 | 17053 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2024-12847788 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD - T2-22-10 |  | FM008 |  | 2024-04-22 07:26 | 2024-04-22 08:26 | 2024-04-23 08:26 | 24 | 2024-04-22 07:30 | 2024-04-22 16:15 | 525 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 126908 | Kaur, Ms. Manpreet | N - - - |  | Voice Communication
| CM-2022-10147124 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-02-17 00:08 | 2022-02-17 01:08 | 2022-02-18 01:08 | 24 | 2022-02-17 00:17 | 2022-02-17 05:30 | 313 | 220 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10032378 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED -AHU-A1110-441)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-01-08 10:25 | 2022-01-08 11:25 | 2022-01-09 11:25 | 24 | 2022-01-08 10:34 | 2022-01-08 13:10 | 156 | 130 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10107677 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU-A1110-441 – DP1 FILTER ALARM – T4-21-03 |  | FM008 |  | 2022-02-04 19:18 | 2022-02-04 20:18 | 2022-02-05 20:18 | 24 | 2022-02-04 19:25 | 2022-02-04 20:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94954 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10575623 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-04-24 10:25 | 2022-04-24 11:25 | 2022-04-25 11:25 | 24 | 2022-04-24 10:30 | 2022-04-24 13:00 | 150 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10730229 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT -DEPARTURE COUNTERS ROW NO 9 COUNTER 1-3 |  | FM008 |  | 2022-06-08 23:44 | 2022-06-09 00:44 | 2022-06-10 00:44 | 24 | 2022-06-08 23:50 | 2022-06-09 00:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106914 | 87807 |  |  | 86127 | Panquico, Ms. Jocelyn Basbas | N - - - |  | Voice Communication
| CM-2022-11104913 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | HEAT WHEEL DIRTY - AHU-A1110-441 - ROOM T4-21-03 |  | FM008 |  | 2022-10-16 12:43 | 2022-10-16 13:43 | 2022-10-17 13:43 | 24 | 2022-10-16 12:53 | 2022-10-16 18:40 | 347 | 155 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11973739 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AHU-A1110-441 FILTER DIRTY T4-08-04 |  | FM008 |  | 2023-07-15 00:06 | 2023-07-15 01:06 | 2023-07-16 01:06 | 24 | 2023-07-15 00:13 | 2023-07-15 02:13 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10237393 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO HOT ROW 9 COUNTER 1 CHECK IN HALL DEPARTURE |  | FM008 |  | 2022-03-11 16:39 | 2022-03-11 17:39 | 2022-03-12 17:39 | 24 | 2022-03-11 16:48 | 2022-03-11 18:00 | 72 | 37 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106972 | 17053 |  |  | 67571 | Kalb-E-Haider, Mr. Syed | N - - - |  | Voice Communication
| CM-2022-10616947 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | SIDE OFFICE AC VENT NEEDS PAINTING IN ROW NUMBER 10- T2-22-08 |  | FM008 |  | 2022-05-05 13:36 | 2022-05-05 14:36 | 2022-05-06 14:36 | 24 | 2022-05-05 13:45 | 2022-05-05 16:10 | 145 | 150 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106914 | 17053 |  |  | FM11021 | MOHAMED SHABIR | N - - - |  | Voice Communication
| CM-2022-10782044 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-441 – T4-21-03 |  | FM008 |  | 2022-06-28 09:48 | 2022-06-28 10:48 | 2022-06-29 10:48 | 24 | 2022-06-28 09:55 | 2022-06-28 11:30 | 95 | 165 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11959646 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | AC TOO COLD – T2-22-10 |  | FM008 |  | 2023-07-09 08:37 | 2023-07-09 09:37 | 2023-07-10 09:37 | 24 | 2023-07-09 08:45 | 2023-07-09 11:55 | 190 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106973 | 87807 |  |  | 13381 | Ibrahim, Ms. Farida | N - - - |  | Voice Communication
| CM-2023-12302388 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | SF FAIL ALARM AIR HANDLING UNIT 054 (TAG NO:AHU-A1110-441)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 (DUPLICATE COPY OF CM-2023-12300153) |  | FM008 |  | 2023-10-20 03:22 | 2023-10-20 04:22 | 2023-10-21 04:22 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED |  |  | 106972 | 17333 |  |  | FM10302 | Thomas J K | N - - - | DUPLICATE CM WORK ORDER - MATAR FRC ERROR | BMS
| CM-2024-12769377 | ASD-MTB-FOF021-AHU054 | AIR HANDLING UNIT-05 | ROW 5 COUNTER 9 AC TOO HOT |  | FM008 |  | 2024-03-27 05:36 | 2024-03-27 06:36 | 2024-03-28 06:36 | 24 | 2024-03-27 05:45 | 2024-03-27 08:00 | 135 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 95217 |  |  | 137722 | Jabnouni, Mr. Mohamed Amine | N - - - |  | Voice Communication
| CM-2022-10084316 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM-AHU-A1110-443)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-01-27 21:06 | 2022-01-27 22:06 | 2022-01-28 22:06 | 24 | 2022-01-27 21:10 | 2022-01-27 22:55 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10809715 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU DP1 FILTER ALARM - T4-21-03 |  | FM008 |  | 2022-07-04 00:02 | 2022-07-04 01:02 | 2022-07-05 01:02 | 24 | 2022-07-04 00:05 | 2022-07-04 01:35 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 95217 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10914738 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AC NOT WORKING - DEPARTURE ,COUNTER 03 ,BAGGAGE WRAP AREA NEAR GATE 02 |  | FM008 |  | 2022-08-05 11:49 | 2022-08-05 12:49 | 2022-08-06 12:49 | 24 | 2022-08-05 11:55 | 2022-08-05 17:45 | 350 | 52 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 55709 |  |  | 95392 | Adhikari, Mr. Bidur | N - - - |  | Voice Communication
| CM-2022-11004591 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED - AHU-A1110-443) MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-09-06 15:37 | 2022-09-06 16:37 | 2022-09-07 16:37 | 24 | 2022-09-06 15:45 | 2022-09-06 17:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 121959 | 94954 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11354276 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443- DP3- FILTER ALARM ACTIVATED-- |  | FM008 |  | 2023-01-07 08:46 | 2023-01-07 09:46 | 2023-01-08 09:46 | 24 | 2023-01-07 08:55 | 2023-01-07 11:25 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11403609 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | A1110-443-DP1 FILTER ALARM-T4-21-03 |  | FM008 |  | 2023-01-27 09:23 | 2023-01-27 10:23 | 2023-01-28 10:23 | 24 | 2023-01-27 09:32 | 2023-01-27 13:30 | 238 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | E-mail
| CM-2023-11681858 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -T4-21-03 |  | FM008 |  | 2023-04-19 07:03 | 2023-04-19 08:03 | 2023-04-20 08:03 | 24 | 2023-04-19 07:10 | 2023-04-19 08:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-11859104 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-06-06 00:14 | 2023-06-06 01:14 | 2023-06-07 01:14 | 24 | 2023-06-06 00:20 | 2023-06-06 01:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 94954 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12042440 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED -T4-08-04 |  | FM008 |  | 2023-08-04 00:40 | 2023-08-04 01:40 | 2023-08-05 01:40 | 24 | 2023-08-04 00:50 | 2023-08-04 02:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 17053 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-12138874 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AC NOT WORKING - T2-22-10 (OFFICE) |  | FM008 |  | 2023-09-02 21:57 | 2023-09-02 22:57 | 2023-09-03 22:57 | 24 | 2023-09-02 22:00 | 2023-09-02 23:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 17573 | 77406 |  |  | 60420 | Khan, Mr. Amir Saeed | N - - - |  | Voice Communication
| CM-2023-12162728 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AMERICAN TOURISTER SHOP - AC TOO HOT |  | FM008 |  | 2023-09-06 06:17 | 2023-09-06 07:17 | 2023-09-07 07:17 | 24 | 2023-09-06 06:25 | 2023-09-06 08:00 | 95 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 105233 | 17053 |  |  | R11600 | Zahr, Mr. Alaa | N - - - |  | Voice Communication
| CM-2023-12327186 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-443 - MECHANICAL ROOM T4-21-03 |  | FM008 |  | 2023-10-29 01:44 | 2023-10-29 02:44 | 2023-10-30 02:44 | 24 | 2023-10-29 01:50 | 2023-10-29 05:20 | 210 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1018 | NIKITA | N - - - |  | Voice Communication
| CM-2022-11071013 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443 SUPPLY CANVAS DAMAGED |  | FM008 |  | 2022-10-05 07:51 | 2022-10-05 08:51 | 2022-10-06 08:51 | 24 | 2022-10-05 08:00 | 2022-10-05 11:30 | 210 | 200 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68485 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12098614 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-08-18 10:26 | 2023-08-18 11:26 | 2023-08-19 11:26 | 24 | 2023-08-18 10:31 | 2023-08-18 12:31 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12155304 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1110-443 T4-21-03 |  | FM008 |  | 2023-09-07 07:23 | 2023-09-07 08:23 | 2023-09-08 08:23 | 24 | 2023-09-07 07:30 | 2023-09-07 10:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM12459 | Dhanabalan, Mr. Devaraj | N - - - |  | Voice Communication
| CM-2022-10914574 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443 FILTER ALARM T4-21-03 |  | FM008 |  | 2022-08-04 19:08 | 2022-08-04 20:08 | 2022-08-05 20:08 | 24 | 2022-08-04 19:15 | 2022-08-05 01:30 | 375 | 110 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | E-mail
| CM-2022-10994689 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443- DP1 FILTER DIRTY -T4-21-29 – - |  | FM008 |  | 2022-09-01 15:13 | 2022-09-01 16:13 | 2022-09-02 16:13 | 24 | 2022-09-01 15:20 | 2022-09-01 16:30 | 70 | 210 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10994691 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443- BELT BROKEN (SUPPLY & RELIEF) -T4-21-29 – - |  | FM008 |  | 2022-09-01 15:14 | 2022-09-01 16:14 | 2022-09-02 16:14 | 24 | 2022-09-01 15:20 | 2022-09-01 17:30 | 130 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11550722 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED - T4-21-10 |  | FM008 |  | 2023-03-11 00:21 | 2023-03-11 01:21 | 2023-03-12 01:21 | 24 | 2023-03-11 00:30 | 2023-03-11 02:15 | 105 | 210 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 105233 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11865315 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443 – RELIEF BELT IS DAMAGED – T4-08-04 |  | FM008 |  | 2023-06-08 02:02 | 2023-06-08 03:02 | 2023-06-09 03:02 | 24 | 2023-06-08 02:10 | 2023-06-08 03:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94954 | 87807 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11916958 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS,AHU-A1110-443,AIR HANDLING UNIT 056 (TAG NO:AHU-A1110-443)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-06-24 19:32 | 2023-06-24 20:32 | 2023-06-25 20:32 | 24 | 2023-06-24 19:40 | 2023-06-24 23:10 | 210 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12346673 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443 – SUPPLY DUCT INSULATION DAMAGED - T4-08-04 |  | FM008 |  | 2023-11-03 10:21 | 2023-11-03 11:21 | 2023-11-04 11:21 | 24 | 2023-11-03 10:25 | 2023-11-03 13:45 | 200 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 105233 | 17053 |  |  | FM12459 | Devaraj Dhanabalan, | N - - - |  | Voice Communication
| CM-2023-12507937 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-12-27 15:44 | 2023-12-27 16:44 | 2023-12-28 16:44 | 24 | 2023-12-27 15:56 | 2023-12-28 02:10 | 614 | 244 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 121959 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12609161 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | RELEASE BELT DAMAGED :AHU-A1110-443 |  | FM008 |  | 2024-01-31 20:02 | 2024-01-31 21:02 | 2024-02-01 21:02 | 24 | 2024-01-31 20:05 | 2024-01-31 23:15 | 190 | 305 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2022-10120875 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443 FILTER BLOCKED – T4-10-03 |  | FM008 |  | 2022-02-08 19:05 | 2022-02-08 20:05 | 2022-02-09 20:05 | 24 | 2022-02-08 19:14 | 2022-02-08 20:45 | 91 | 182 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106976 | 55709 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10048848 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU-A1110-443 RELIEF BELT DAMAGED- T4-08-04 |  | FM008 |  | 2022-01-15 22:33 | 2022-01-15 23:33 | 2022-01-16 23:33 | 24 | 2022-01-15 22:40 | 2022-01-15 23:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 87807 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11182128 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING - AHU-A1110-443 - MECHANICAL ROOM T4-21-03 |  | FM008 |  | 2022-11-12 21:09 | 2022-11-12 22:09 | 2022-11-13 22:09 | 24 | 2022-11-12 21:15 | 2022-11-12 23:30 | 135 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 124475 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10781980 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AIR HANDLING UNIT 056 (TAG NO:AHU-A1110-443)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-06-28 02:05 | 2022-06-28 03:05 | 2022-06-29 03:05 | 24 | 2022-06-28 02:10 | 2022-06-28 03:25 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10840764 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AC IS BLOWING AND MAKING A LOT OF NOISE-ROW 10 NEAR -BAG WRAP |  | FM008 |  | 2022-07-16 07:17 | 2022-07-16 08:17 | 2022-07-17 08:17 | 24 | 2022-07-16 07:27 | 2022-07-16 10:10 | 163 | 489 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 87807 | 95217 |  |  | 80794 | Rajcoomar, Ms. Andrishka Karis | N - - - |  | Voice Communication
| CM-2022-10861425 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM CEILING - IN FRONT OF ROW 9 |  | FM008 |  | 2022-07-23 11:07 | 2022-07-23 12:07 | 2022-07-24 12:07 | 24 | 2022-07-23 11:16 | 2022-07-23 12:00 | 44 | 44 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17154 | 95217 |  |  | 52856 | Oliveros, Mr. Jovito Jr. Panganiban | N - - - |  | Voice Communication
| CM-2023-12166653 | ASD-MTB-FOF021-AHU056 | AIR HANDLING UNIT-05 | AHU BEARING NOISY T4-21-03 |  | FM008 |  | 2023-09-10 07:20 | 2023-09-10 08:20 | 2023-09-11 08:20 | 24 | 2023-09-10 07:25 | 2023-09-10 11:25 | 240 | 960 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM12459 | Devaraj Dhanabalan, | N - - - |  | Voice Communication
| CM-2022-10079452 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AHU-A1155-401 COOLING COIL DIRTY T4-21-01 |  | FM008 |  | 2022-01-25 19:24 | 2022-01-25 20:24 | 2022-01-26 20:24 | 24 | 2022-01-25 19:30 | 2022-01-25 23:30 | 240 | 960 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10628629 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-11 07:21 | 2022-05-11 08:21 | 2022-05-12 08:21 | 24 | 2022-05-11 07:30 | 2022-05-11 16:00 | 510 | 455 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2022-10861908 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AHU-A1155-401 – FILTER IS BLOCKED - MECHANICAL ROOM T4-21-01 |  | FM008 |  | 2022-07-20 13:20 | 2022-07-20 14:20 | 2022-07-21 14:20 | 24 | 2022-07-20 13:25 | 2022-07-20 15:20 | 115 | 345 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11131340 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT SUPPLY BELT DOUBLING,- (AHU-A1155-401) |  | FM008 |  | 2022-10-24 08:17 | 2022-10-24 09:17 | 2022-10-25 09:17 | 24 | 2022-10-24 08:25 | 2022-10-24 09:25 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11350378 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AIR FROM THE DAMAGED DUCT -T4-21-10 |  | FM008 |  | 2023-01-06 09:09 | 2023-01-06 10:09 | 2023-01-07 10:09 | 24 | 2023-01-06 09:18 | 2023-01-06 14:30 | 312 | 347 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-12199127 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-21-01 |  | FM008 |  | 2023-09-19 07:12 | 2023-09-19 08:12 | 2023-09-20 08:12 | 24 | 2023-09-19 07:20 | 2023-09-19 09:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-11043286 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | FILTER DIRTY - MEC ROOM 4TH FLOOR |  | FM008 |  | 2022-09-24 22:03 | 2022-09-24 23:03 | 2022-09-25 23:03 | 24 | 2022-09-24 22:05 | 2022-09-24 23:05 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11181827 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | CHILL WATER LINE PAINT FADED – T4-21-01 |  | FM008 |  | 2022-11-13 11:06 | 2022-11-13 12:06 | 2022-11-14 12:06 | 24 | 2022-11-13 11:10 | 2022-11-13 13:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11455373 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-21-04 |  | FM008 |  | 2023-02-13 15:26 | 2023-02-13 16:26 | 2023-02-14 16:26 | 24 | 2023-02-13 15:35 | 2023-02-13 18:35 | 180 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17573 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11654679 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER IS DIRTY |  | FM008 |  | 2023-04-12 10:49 | 2023-04-12 11:49 | 2023-04-13 11:49 | 24 | 2023-04-12 10:55 | 2023-04-12 15:05 | 250 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68060 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-12485913 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AHU-A1155-401 ABNORMAL SOUNDS T4-21-01 |  | FM008 |  | 2023-12-19 07:06 | 2023-12-19 08:06 | 2023-12-20 08:06 | 24 | 2023-12-19 07:15 | 2023-12-19 10:30 | 195 | 780 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10952999 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM STRAINER COUPLING - AHU-A1155-401 - T4-21-10 |  | FM008 |  | 2022-08-17 09:56 | 2022-08-17 10:56 | 2022-08-18 10:56 | 24 | 2022-08-17 10:00 | 2022-08-17 12:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 55709 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2022-11191055 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AHU-A1155-401 MARINE LIGHT NOT WORKING T4-21-01 |  | FM008 |  | 2022-11-16 21:33 | 2022-11-16 22:33 | 2022-11-17 22:33 | 24 | 2022-11-16 21:40 | 2022-11-16 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11465347 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE-T4-21-01 |  | FM008 |  | 2023-02-18 00:20 | 2023-02-18 01:20 | 2023-02-19 01:20 | 24 | 2023-02-18 00:30 | 2023-02-18 03:30 | 180 | 720 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11995674 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING – T4-21-01 |  | FM008 |  | 2023-07-22 03:43 | 2023-07-22 04:43 | 2023-07-23 04:43 | 24 | 2023-07-22 03:50 | 2023-07-22 06:20 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106914 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11997716 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | SUPPLY AIRFLOW SENSOR NOT WORKING (C4210-AHU-901) - C4210-03SO058 (new cm CM-2023-11997722) |  | FM008 |  | 2023-07-22 04:14 | 2023-07-22 05:14 | 2023-07-23 05:14 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED |  |  | 106914 | 87807 |  |  | C03293 | Mahesh | N - - - | ASSET NOT IN SCOPE | E-mail
| CM-2023-12521412 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1155-401 – T4-21-01 |  | FM008 |  | 2023-12-31 14:52 | 2023-12-31 15:52 | 2024-01-01 15:52 | 24 | 2023-12-31 15:00 | 2023-12-31 17:30 | 150 | 165 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12457301 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM AHU |  | FM008 |  | 2023-12-10 14:58 | 2023-12-10 15:58 | 2023-12-11 15:58 | 24 | 2023-12-10 15:00 | 2023-12-10 17:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12515317 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - MECHANICAL ROOM T4-21-01 |  | FM008 |  | 2023-12-29 03:22 | 2023-12-29 04:22 | 2023-12-30 04:22 | 24 | 2023-12-29 03:30 | 2023-12-29 06:30 | 180 | 290 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2024-12593355 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM AHU,AHU-A1155-401 T4-21-01 |  | FM008 |  | 2024-01-25 11:26 | 2024-01-25 12:26 | 2024-01-26 12:26 | 24 | 2024-01-25 11:30 | 2024-01-25 18:40 | 430 | 525 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12609199 | ASD-MTB-FOF021-AHU185 | AIR HANDLING UNIT-05 | AHU-A1155-401 FILTER DIRTY |  | FM008 |  | 2024-02-01 00:03 | 2024-02-01 01:03 | 2024-02-02 01:03 | 24 | 2024-02-01 00:10 | 2024-02-01 03:00 | 170 | 350 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 68485 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11350377 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AIR LEAKING FROM ACCESS DOOR -T4-21-10 |  | FM008 |  | 2023-01-06 09:08 | 2023-01-06 10:08 | 2023-01-07 10:08 | 24 | 2023-01-06 09:15 | 2023-01-06 13:00 | 225 | 705 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-11779991 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2023-05-11 21:40 | 2023-05-11 22:40 | 2023-05-12 22:40 | 24 | 2023-05-11 21:45 | 2023-05-11 23:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 121959 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11842441 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | FILTER BLOCKED - AHU-A1155-402 – T4-21-01 |  | FM008 |  | 2023-06-02 00:13 | 2023-06-02 01:13 | 2023-06-03 01:13 | 24 | 2023-06-02 00:20 | 2023-06-02 02:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12421974 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | FILTER BLOCKED -AIR HANDLING UNIT 186 (TAG NO:AHU-A1155-402)-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-11-27 04:25 | 2023-11-27 05:25 | 2023-11-28 05:25 | 24 | 2023-11-27 04:35 | 2023-11-27 06:00 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17336 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12592299 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU HAVING ABNORMAL NOISY |  | FM008 |  | 2024-01-25 08:04 | 2024-01-25 09:04 | 2024-01-26 09:04 | 24 | 2024-01-25 08:10 | 2024-01-25 10:15 | 125 | 375 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2023-11365287 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU RETURN SIDE INSULATION DAMAGED - T4-21-01 |  | FM008 |  | 2023-01-12 20:14 | 2023-01-12 21:14 | 2023-01-13 21:14 | 24 | 2023-01-12 20:20 | 2023-01-12 23:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17053 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-11997074 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED - T4 21 01 |  | FM008 |  | 2023-07-19 10:24 | 2023-07-19 11:24 | 2023-07-20 11:24 | 24 | 2023-07-19 10:30 | 2023-07-19 11:45 | 75 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 132112 | 87807 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12055511 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | T4-21-01 DRAIN LINE BLOCKED |  | FM008 |  | 2023-08-06 13:35 | 2023-08-06 14:35 | 2023-08-07 14:35 | 24 | 2023-08-06 13:40 | 2023-08-06 17:00 | 200 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106972 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12057264 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU DP1 FILTER ALARM - T4-21-01 |  | FM008 |  | 2023-08-07 20:47 | 2023-08-07 21:47 | 2023-08-08 21:47 | 24 | 2023-08-07 20:50 | 2023-08-07 22:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2024-12831188 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | SUPPLY& RETURN SIDE BELT WOBBLING - AHU-A1155-402 – T4-24-01 |  | FM008 |  | 2024-04-17 02:07 | 2024-04-17 03:07 | 2024-04-18 03:07 | 24 | 2024-04-17 02:10 | 2024-04-17 03:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11112674 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | FILTER BLOCKED - AHU-A1155-402 |  | FM008 |  | 2022-10-19 12:32 | 2022-10-19 13:32 | 2022-10-20 13:32 | 24 | 2022-10-19 12:40 | 2022-10-19 17:10 | 270 | 325 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11216893 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – MEC ROOM T4-21-01 |  | FM008 |  | 2022-11-25 14:22 | 2022-11-25 15:22 | 2022-11-26 15:22 | 24 | 2022-11-25 14:30 | 2022-11-25 18:00 | 210 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11446017 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – T4-21-04 |  | FM008 |  | 2023-02-12 11:45 | 2023-02-12 12:45 | 2023-02-13 12:45 | 24 | 2023-02-12 11:50 | 2023-02-12 17:15 | 325 | 365 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12223810 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1155-402 â?? T4-21-01 |  | FM008 |  | 2023-09-25 08:37 | 2023-09-25 09:37 | 2023-09-26 09:37 | 24 | 2023-09-25 08:45 | 2023-09-25 11:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2023-12324583 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-10-28 16:33 | 2023-10-28 17:33 | 2023-10-29 17:33 | 24 | 2023-10-28 16:45 | 2023-10-28 18:30 | 105 | 315 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2024-12689619 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU-A1155-402-AHU FILTER DIRTY |  | FM008 |  | 2024-02-28 00:32 | 2024-02-28 01:32 | 2024-02-29 01:32 | 24 | 2024-02-28 00:35 | 2024-02-28 04:00 | 205 | 170 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2024-12521728 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU-A1155-402 DUCT INSULATION DAMAGE - -AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2024-01-02 13:23 | 2024-01-02 14:23 | 2024-01-03 14:23 | 24 | 2024-01-02 13:30 | 2024-01-02 15:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 119320 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10191168 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-A1155-402 T4-21-01 |  | FM008 |  | 2022-02-25 19:26 | 2022-02-25 20:26 | 2022-02-26 20:26 | 24 | 2022-02-25 19:30 | 2022-02-25 23:30 | 240 | 480 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10209268 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU-A1155-402 CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-03-04 10:16 | 2022-03-04 11:16 | 2022-03-05 11:16 | 24 | 2022-03-04 10:20 | 2022-03-04 12:45 | 145 | 290 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | E-mail
| CM-2022-10781694 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU-A1155-402 – DP1- FILTER ALARM – T4-21-01 |  | FM008 |  | 2022-06-26 11:20 | 2022-06-26 12:20 | 2022-06-27 12:20 | 24 | 2022-06-26 11:25 | 2022-06-26 15:30 | 245 | 260 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 95217 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-11060813 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU-A1155-402 DP1 FILTER DIRTY T4-21-01 |  | FM008 |  | 2022-09-28 20:06 | 2022-09-28 21:06 | 2022-09-29 21:06 | 24 | 2022-09-28 20:10 | 2022-09-28 21:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11191047 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU FILTER BLOCKED - T4-21-01 |  | FM008 |  | 2022-11-16 20:29 | 2022-11-16 21:29 | 2022-11-17 21:29 | 24 | 2022-11-16 20:35 | 2022-11-16 23:00 | 145 | 435 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 121959 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11269289 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | AHU INSIDE CABIN LIGHT NOT ILLUMINATING - AHU-A1155-402 – T4-21-01 |  | FM008 |  | 2022-12-13 00:07 | 2022-12-13 01:07 | 2022-12-14 01:07 | 24 | 2022-12-13 00:17 | 2022-12-13 03:17 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10282376 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-03-26 13:40 | 2022-03-26 14:40 | 2022-03-27 14:40 | 24 | 2022-03-26 13:45 | 2022-03-26 16:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-12258473 | ASD-MTB-FOF021-AHU186 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-10-08 00:06 | 2023-10-08 01:06 | 2023-10-09 01:06 | 24 | 2023-10-08 00:10 | 2023-10-08 03:00 | 170 | 340 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-11760024 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-01 08:26 | 2023-05-01 09:26 | 2023-05-02 09:26 | 24 | 2023-05-01 08:35 | 2023-05-01 11:32 | 177 | 354 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12005282 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU-A1155-403)-CABIN LAMP FAULTY -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-07-24 11:08 | 2023-07-24 12:08 | 2023-07-25 12:08 | 24 | 2023-07-24 11:15 | 2023-07-24 13:35 | 140 | 280 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 77406 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12199128 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-21-01 |  | FM008 |  | 2023-09-19 07:13 | 2023-09-19 08:13 | 2023-09-20 08:13 | 24 | 2023-09-19 07:20 | 2023-09-19 11:25 | 245 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12366288 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1155-403) – D4 21 01 |  | FM008 |  | 2023-11-10 20:37 | 2023-11-10 21:37 | 2023-11-11 21:37 | 24 | 2023-11-10 20:45 | 2023-11-10 22:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 17053 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2023-12464601 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY -- AHU-A1155-403)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-12-11 14:13 | 2023-12-11 15:13 | 2023-12-12 15:13 | 24 | 2023-12-11 14:20 | 2023-12-11 17:40 | 200 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 138627 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-11365288 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU-A1155-403 - CHILLED WATER LINE PAINT FADED - T4-21-01 |  | FM008 |  | 2023-01-12 20:15 | 2023-01-12 21:15 | 2023-01-13 21:15 | 24 | 2023-01-12 20:20 | 2023-01-12 23:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17053 | 55709 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12055510 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | T4-21-01 DRAIN LINE BLOCKED |  | FM008 |  | 2023-08-06 13:33 | 2023-08-06 14:33 | 2023-08-07 14:33 | 24 | 2023-08-06 13:40 | 2023-08-06 16:30 | 170 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106972 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-11877646 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | -AHU-A1155-403-LIGHTING SWITCHED DAMAGE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-06-13 15:11 | 2023-06-13 16:11 | 2023-06-14 16:11 | 24 | 2023-06-13 15:20 | 2023-06-13 17:18 | 118 | 236 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12236000 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – T4-21-01 |  | FM008 |  | 2023-09-30 19:07 | 2023-09-30 20:07 | 2023-10-01 20:07 | 24 | 2023-09-30 19:15 | 2023-09-30 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 106914 | 87807 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2024-12532433 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1155-403) – T4 21 01 |  | FM008 |  | 2024-01-02 08:24 | 2024-01-02 09:24 | 2024-01-03 09:24 | 24 | 2024-01-02 08:30 | 2024-01-02 11:15 | 165 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12277393 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU IS NOISY - AHU-A1155-403 - MECHANICAL ROOM T4-21-01 |  | FM008 |  | 2023-10-11 07:40 | 2023-10-11 08:40 | 2023-10-12 08:40 | 24 | 2023-10-11 07:45 | 2023-10-11 11:20 | 215 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17573 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10161189 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU-A1155-403-COIL DIRTY |  | FM008 |  | 2022-02-22 19:58 | 2022-02-22 20:58 | 2022-02-23 20:58 | 24 | 2022-02-22 20:10 | 2022-02-22 23:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95217 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10202174 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2022-03-04 12:49 | 2022-03-04 13:49 | 2022-03-05 13:49 | 24 | 2022-03-04 12:55 | 2022-03-04 15:30 | 155 | 310 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17053 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10873253 | ASD-MTB-FOF021-AHU187 | AIR HANDLING UNIT-05 | AHU FILTER ALARM - TAG NO:AHU-A1155-403) MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-07-27 21:24 | 2022-07-27 22:24 | 2022-07-28 22:24 | 24 | 2022-07-27 21:30 | 2022-07-27 22:40 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-10214507 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | CHILL WATER LINE PIPE PAINT IS FADED - AHU-A1155-404 - T4-21-08 |  | FM008 |  | 2022-03-05 07:27 | 2022-03-05 08:27 | 2022-03-06 08:27 | 24 | 2022-03-05 07:30 | 2022-03-05 10:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 17053 |  |  | FM0016 | Paramasamy, Mr. Jeyaram | N - - - |  | Voice Communication
| CM-2022-10873251 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU FILTER ALARM - TAG NO:AHU-A1155-404) MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-07-27 21:23 | 2022-07-27 22:23 | 2022-07-28 22:23 | 24 | 2022-07-27 21:30 | 2022-07-27 23:50 | 140 | 135 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-12366290 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1155-404 ) – D4 21 01 |  | FM008 |  | 2023-11-10 20:40 | 2023-11-10 21:40 | 2023-11-11 21:40 | 24 | 2023-11-10 20:45 | 2023-11-10 22:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2023-11368214 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED, T4-21-01 |  | FM008 |  | 2023-01-14 20:16 | 2023-01-14 21:16 | 2023-01-15 21:16 | 24 | 2023-01-14 20:20 | 2023-01-14 23:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 133396 | 55709 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2023-11888190 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU-A1155-404 – LIGHTING SWITCH DAMAGED |  | FM008 |  | 2023-06-17 11:34 | 2023-06-17 12:34 | 2023-06-18 12:34 | 24 | 2023-06-17 11:40 | 2023-06-17 14:34 | 174 | 243 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | CABLE FAULTY | REPLACED THE CABLE | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2024-12589699 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU-A1155-404-ABNORMAL NOISE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2024-01-22 08:49 | 2024-01-22 09:49 | 2024-01-23 09:49 | 24 | 2024-01-22 08:55 | 2024-01-22 17:00 | 485 | 345 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 77406 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-11189074 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU-A1155-404- AHU LIGHTING FLEXIBLE COCKPIT DAMAGED |  | FM008 |  | 2022-11-14 20:24 | 2022-11-14 21:24 | 2022-11-15 21:24 | 24 | 2022-11-14 20:30 | 2022-11-14 23:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12204799 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT 188 (TAG NO:AHU-A1155-404)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-09-19 13:19 | 2023-09-19 14:19 | 2023-09-20 14:19 | 24 | 2023-09-19 13:25 | 2023-09-19 16:00 | 155 | 310 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12532434 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – (AHU-A1155-404) – T4 21 01 |  | FM008 |  | 2024-01-02 08:27 | 2024-01-02 09:27 | 2024-01-03 09:27 | 24 | 2024-01-02 08:35 | 2024-01-02 13:00 | 265 | 205 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 132112 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12671459 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | Detached pipe line support outside T4-10-05 |  | FM008 |  | 2024-02-21 15:46 | 2024-02-21 16:46 | 2024-02-22 16:46 | 24 | 2024-02-21 15:55 | 2024-02-21 17:15 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 121959 | 17053 |  |  | 134092 | Almario, Mr. Neftali Tinao | N - - - |  | E-mail
| CM-2022-10059161 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU-A1155-404 - COOLING COIL DIRTY |  | FM008 |  | 2022-01-21 13:21 | 2022-01-21 14:21 | 2022-01-22 14:21 | 24 | 2022-01-21 13:30 | 2022-01-21 16:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10214643 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU-A1155-404 FILTER DIRTY T4-21-01 |  | FM008 |  | 2022-03-05 14:56 | 2022-03-05 15:56 | 2022-03-06 15:56 | 24 | 2022-03-05 15:00 | 2022-03-05 17:30 | 150 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11271756 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | SUPPLY CHILLED WATER LINE TEMPERATURE GAUGE IS NOT WORKING -AHU-A1155-404)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2022-12-15 08:30 | 2022-12-15 09:30 | 2022-12-16 09:30 | 24 | 2022-12-15 08:35 | 2022-12-15 10:45 | 130 | 390 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PRESSURE GAUGE DAMAGED | REPAIRED/REPLACED | 17336 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10160456 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | AHU-A1155-404-COOLING COIL DIRTY-T4-21-01 |  | FM008 |  | 2022-02-21 19:27 | 2022-02-21 20:27 | 2022-02-22 20:27 | 24 | 2022-02-21 19:35 | 2022-02-21 22:30 | 175 | 525 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12258472 | ASD-MTB-FOF021-AHU188 | AIR HANDLING UNIT-05 | DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-10-08 00:04 | 2023-10-08 01:04 | 2023-10-09 01:04 | 24 | 2023-10-08 00:10 | 2023-10-08 03:00 | 170 | 340 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 68060 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2022-10214699 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU-A1155-405 – UNIT FILTER BLOCKED-- |  | FM008 |  | 2022-03-05 22:08 | 2022-03-05 23:08 | 2022-03-06 23:08 | 24 | 2022-03-05 22:15 | 2022-03-05 23:55 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 94953 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10791764 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | FILTER BLOCKED – T4-21-01 |  | FM008 |  | 2022-06-29 03:50 | 2022-06-29 04:50 | 2022-06-30 04:50 | 24 | 2022-06-29 04:00 | 2022-06-29 06:00 | 120 | 260 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 105233 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12484191 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | ABNORMAL SOUND |  | FM008 |  | 2023-12-18 07:38 | 2023-12-18 08:38 | 2023-12-19 08:38 | 24 | 2023-12-18 07:45 | 2023-12-18 13:30 | 345 | 530 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68060 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12631896 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING AHU-A1155-405 |  | FM008 |  | 2024-02-08 19:15 | 2024-02-08 20:15 | 2024-02-09 20:15 | 24 | 2024-02-08 19:24 | 2024-02-08 23:15 | 231 | 335 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106972 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-11114931 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU-A1155-405 AIRFLOW MISMATCHED T4-21-01 |  | FM008 |  | 2022-10-21 12:09 | 2022-10-21 13:09 | 2022-10-22 13:09 | 24 | 2022-10-21 12:15 | 2022-10-21 15:55 | 220 | 730 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 89127 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11269266 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU INSIDE CABIN LIGHT NOT ILLUMINATING - AHU-A1155-405 – T4-21-01 |  | FM008 |  | 2022-12-12 19:08 | 2022-12-12 20:08 | 2022-12-13 20:08 | 24 | 2022-12-12 19:15 | 2022-12-12 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17573 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12206594 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU DUCT INSULATION IS DAMAGED |  | FM008 |  | 2023-09-21 19:08 | 2023-09-21 20:08 | 2023-09-22 20:08 | 24 | 2023-09-21 19:15 | 2023-09-21 22:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68060 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2023-12204801 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT 189 (TAG NO:AHU-A1155-405)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 021 |  | FM008 |  | 2023-09-19 13:24 | 2023-09-19 14:24 | 2023-09-20 14:24 | 24 | 2023-09-19 13:30 | 2023-09-19 16:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12516195 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1155-405 – T4-21-01 |  | FM008 |  | 2023-12-31 14:52 | 2023-12-31 15:52 | 2024-01-01 15:52 | 24 | 2023-12-31 15:00 | 2023-12-31 16:30 | 90 | 90 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12235999 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED – T4-21-01 |  | FM008 |  | 2023-09-30 19:05 | 2023-09-30 20:05 | 2023-10-01 20:05 | 24 | 2023-09-30 19:15 | 2023-09-30 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106914 | 87807 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2024-12599921 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | FILTER BLOCKED AHU-A1155-405 |  | FM008 |  | 2024-01-30 22:08 | 2024-01-30 23:08 | 2024-01-31 23:08 | 24 | 2024-01-30 22:15 | 2024-01-31 00:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10257088 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU-A1155-405 – CHILLED WATER LINE PAINT FADED- |  | FM008 |  | 2022-03-19 09:18 | 2022-03-19 10:18 | 2022-03-20 10:18 | 24 | 2022-03-19 09:25 | 2022-03-19 12:10 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94953 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10146662 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | COIL DIRTY |  | FM008 |  | 2022-02-16 21:27 | 2022-02-16 22:27 | 2022-02-17 22:27 | 24 | 2022-02-16 21:35 | 2022-02-16 23:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11060812 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU-A1155-405 DP1 FILTER DIRTY T4-21-01 |  | FM008 |  | 2022-09-28 20:04 | 2022-09-28 21:04 | 2022-09-29 21:04 | 24 | 2022-09-28 20:10 | 2022-09-28 23:15 | 185 | 190 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11423005 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED -T4-21-01 |  | FM008 |  | 2023-02-01 21:42 | 2023-02-01 22:42 | 2023-02-02 22:42 | 24 | 2023-02-01 21:50 | 2023-02-01 23:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17333 | 87807 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | Voice Communication
| CM-2022-10877468 | ASD-MTB-FOF021-AHU189 | AIR HANDLING UNIT-05 | AHU-A1155-405 FILTER ALARM - T4-21-01 |  | FM008 |  | 2022-07-27 19:18 | 2022-07-27 20:18 | 2022-07-28 20:18 | 24 | 2022-07-27 19:20 | 2022-07-27 20:00 | 40 | 80 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 021 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10045373 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | RETUN FAN TERMINAL BOX FLEXIBLE CONNECTOR DAMAGED |  | FM008 |  | 2022-01-13 09:22 | 2022-01-13 10:22 | 2022-01-14 10:22 | 24 | 2022-01-13 09:30 | 2022-01-13 13:29 | 239 | 183 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 95216 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11138340 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-24-01 |  | FM008 |  | 2022-10-28 10:53 | 2022-10-28 11:53 | 2022-10-29 11:53 | 24 | 2022-10-28 11:00 | 2022-10-28 18:05 | 425 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11615563 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – AHU-A1157-406- T4-24-01 |  | FM008 |  | 2023-04-02 12:22 | 2023-04-02 13:22 | 2023-04-03 13:22 | 24 | 2023-04-02 12:30 | 2023-04-02 16:30 | 240 | 480 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12148735 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | CHILLER WATER LINE INSULATION DAMAGED – (AHU-A1157-406) T4 24 01 |  | FM008 |  | 2023-09-04 14:43 | 2023-09-04 15:43 | 2023-09-05 15:43 | 24 | 2023-09-04 14:50 | 2023-09-04 16:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 132112 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12341357 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AC TOO COLD ROW 2 QR TICKETING OFFICE |  | FM008 |  | 2023-11-02 07:13 | 2023-11-02 08:13 | 2023-11-03 08:13 | 24 | 2023-11-02 07:20 | 2023-11-02 13:00 | 340 | 45 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68485 | 17053 |  |  | 81713 | Rodrigues, Mr. Savio Xavier | N - - - |  | Voice Communication
| CM-2023-11622004 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1157-406 – T4-24-01 |  | FM008 |  | 2023-04-05 19:20 | 2023-04-05 20:21 | 2023-04-06 20:21 | 24 | 2023-04-05 19:30 | 2023-04-05 22:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11941165 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-24-01 |  | FM008 |  | 2023-07-03 13:43 | 2023-07-03 14:43 | 2023-07-04 14:43 | 24 | 2023-07-03 13:50 | 2023-07-03 17:15 | 205 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12140702 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AHU-A1157-406 COOLING COIL DIRTY T4-24-01 |  | FM008 |  | 2023-09-02 03:58 | 2023-09-02 04:58 | 2023-09-03 04:58 | 24 | 2023-09-02 04:05 | 2023-09-02 06:30 | 145 | 435 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 87807 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12515061 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1157-406 -T4-24-01 |  | FM008 |  | 2023-12-30 08:24 | 2023-12-30 09:24 | 2023-12-31 09:24 | 24 | 2023-12-30 08:30 | 2023-12-30 10:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12632592 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AHU-A1157-406 CABIN LIGHT SWITCH FAULTY – T4-24-01 |  | FM008 |  | 2024-02-09 00:11 | 2024-02-09 01:11 | 2024-02-10 01:11 | 24 | 2024-02-09 00:21 | 2024-02-09 03:05 | 164 | 328 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | THE EQUIPMENT HAS BEEN SWITCH OFF | THE POWER HAS BEEN RESTORED | 106914 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2022-10044595 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AHU-A1157-406 – FILTER DIRTY |  | FM008 |  | 2022-01-13 18:56 | 2022-01-13 19:56 | 2022-01-14 19:56 | 24 | 2022-01-13 19:05 | 2022-01-13 21:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10162338 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AC TOO HOT |  | FM008 |  | 2022-02-24 11:13 | 2022-02-24 12:13 | 2022-02-25 12:13 | 24 | 2022-02-24 11:20 | 2022-02-24 12:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | MOI | JAN | N - - - |  | Voice Communication
| CM-2022-10162319 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AC NOT WORKING |  | FM008 |  | 2022-02-24 10:52 | 2022-02-24 11:22 | 2022-02-24 15:22 | 4 | 2022-02-24 11:02 | 2022-02-24 12:00 | 58 | 58 | 1 | HVAC |  | Closed | Urgent | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | MOI | FARIS | N - - - |  | Voice Communication
| CM-2023-11363115 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | FILTER DIRTY -AIR HANDLING UNIT 005 (TAG NO:AHU-A1157-406)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-01-10 19:10 | 2023-01-10 20:10 | 2023-01-11 20:10 | 24 | 2023-01-10 19:15 | 2023-01-10 21:15 | 120 | 480 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10146401 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-02-15 10:18 | 2022-02-15 11:18 | 2022-02-16 11:18 | 24 | 2022-02-15 10:25 | 2022-02-15 13:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10162335 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | AC TOO HOT ICTOC OFFICE |  | FM008 |  | 2022-02-24 11:11 | 2022-02-24 12:11 | 2022-02-25 12:11 | 24 | 2022-02-24 11:20 | 2022-02-24 12:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 55709 |  |  | 60920 | Mitri, Mr. Joseph | N - - - |  | Voice Communication
| CM-2023-11648419 | ASD-MTB-FOF024-AHU005 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED – T4-24-01 |  | FM008 |  | 2023-04-10 13:02 | 2023-04-10 14:02 | 2023-04-11 14:02 | 24 | 2023-04-10 13:11 | 2023-04-10 18:45 | 334 | 188 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 105233 | 94954 |  |  | FM7343 | Azad Hussain Ansari, | N - - - |  | Voice Communication
| CM-2022-10124993 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | AIR FILTER IS DIRTY - AHU-A1110-426 - T4-09-04 |  | FM008 |  | 2022-02-12 14:21 | 2022-02-12 15:21 | 2022-02-13 15:21 | 24 | 2022-02-12 14:30 | 2022-02-12 18:10 | 220 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | E-mail
| CM-2022-10832030 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED-T4-09-04 |  | FM008 |  | 2022-07-15 07:21 | 2022-07-15 08:21 | 2022-07-16 08:21 | 24 | 2022-07-15 07:30 | 2022-07-15 09:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12202435 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | RELIEF FAN BELT DAMAGED - AHU-A1110-426 – T4-09-04 |  | FM008 |  | 2023-09-20 00:01 | 2023-09-20 01:01 | 2023-09-21 01:01 | 24 | 2023-09-20 00:06 | 2023-09-20 03:10 | 184 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12202436 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED - AHU-A1110-426 – T4-09-04 |  | FM008 |  | 2023-09-20 00:02 | 2023-09-20 01:02 | 2023-09-21 01:02 | 24 | 2023-09-20 00:07 | 2023-09-20 04:45 | 278 | 186 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11227030 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED -T4-09-04 |  | FM008 |  | 2022-11-30 03:47 | 2022-11-30 04:47 | 2022-12-01 04:47 | 24 | 2022-11-30 03:55 | 2022-11-30 05:25 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11826693 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-26 19:46 | 2023-05-26 20:46 | 2023-05-27 20:46 | 24 | 2023-05-26 19:50 | 2023-05-26 21:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11328712 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARM - (AHU-A1110-426) - AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2022-12-30 07:32 | 2022-12-30 08:32 | 2022-12-31 08:32 | 24 | 2022-12-30 07:40 | 2022-12-30 09:45 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11476022 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-426 – T4-09-04 |  | FM008 |  | 2023-02-20 07:08 | 2023-02-20 08:08 | 2023-02-21 08:08 | 24 | 2023-02-20 07:15 | 2023-02-20 08:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11607507 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | AC IS TOO HOT -IMMIGRATION SCREENING AREA -BUSINESS CLASS - |  | FM008 |  | 2023-03-28 07:22 | 2023-03-28 08:22 | 2023-03-29 08:22 | 24 | 2023-03-28 07:27 | 2023-03-28 12:35 | 308 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 87807 |  |  | CT15021 | VITALIS | N - - - |  | Voice Communication
| CM-2023-11824118 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | AC TOO COLD - CHECKING COUNTER ROW #1 FIRST CLASS |  | FM008 |  | 2023-05-26 04:35 | 2023-05-26 05:34 | 2023-05-27 05:34 | 24 | 2023-05-26 04:40 | 2023-05-26 06:35 | 115 | 35 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 132112 | 17053 |  |  | 84857 | Ben Abdallah, Ms. Refka | N - - - |  | Voice Communication
| CM-2023-12208815 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT FUSED |  | FM008 |  | 2023-09-22 03:09 | 2023-09-22 04:09 | 2023-09-23 04:09 | 24 | 2023-09-22 03:20 | 2023-09-22 05:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12211094 | ASD-MTB-FOF024-AHU039 | AIR HANDLING UNIT-05 | FILTER DIRTY -AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 -T4-09-04 |  | FM008 |  | 2023-09-23 19:02 | 2023-09-23 20:02 | 2023-09-24 20:02 | 24 | 2023-09-23 19:10 | 2023-09-23 21:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10103529 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU-A1110-436 FILTER DIRTY |  | FM008 |  | 2022-02-02 00:05 | 2022-02-02 01:05 | 2022-02-03 01:05 | 24 | 2022-02-02 00:15 | 2022-02-02 01:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11145898 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | INSIDE AHU LIGHT NOT WORKING – T4-09-04 |  | FM008 |  | 2022-10-30 00:09 | 2022-10-30 01:09 | 2022-10-31 01:09 | 24 | 2022-10-30 00:15 | 2022-10-30 01:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-12341955 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | SUPPLY BLOWER PAINT FADED - AIR HANDLING UNIT 049 (TAG NO:AHU-A1110-436)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 024 |  | FM008 |  | 2023-10-30 19:03 | 2023-10-30 20:03 | 2023-10-31 20:03 | 24 | 2023-10-30 19:10 | 2023-10-30 21:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | SUPPLY FAN MOTOR BURNT | REPLACED THE MOTOR | 119320 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10930542 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU-A1110-436 - SUPPLY DUCT INSULATION DAMAGED- T4-09-04 |  | FM008 |  | 2022-08-10 22:08 | 2022-08-10 23:08 | 2022-08-11 23:08 | 24 | 2022-08-10 22:15 | 2022-08-11 00:30 | 135 | 405 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 87807 | 55709 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11230541 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | CHILLED WATER PAINT FADED – T4-09-04 |  | FM008 |  | 2022-11-29 12:29 | 2022-11-29 13:29 | 2022-11-30 13:29 | 24 | 2022-11-29 12:35 | 2022-11-29 17:40 | 305 | 485 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 17053 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2023-12014214 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU CABIN LAMP SWITCH DAMAGED – T4-09-04;MEC ROOM |  | FM008 |  | 2023-07-26 01:22 | 2023-07-26 02:22 | 2023-07-27 02:22 | 24 | 2023-07-26 01:30 | 2023-07-26 04:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 105233 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12097010 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1110-436 – T4-09-04 |  | FM008 |  | 2023-08-18 19:15 | 2023-08-18 20:15 | 2023-08-19 20:15 | 24 | 2023-08-18 19:20 | 2023-08-18 21:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-11060313 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-09-26 07:16 | 2022-09-26 08:16 | 2022-09-27 08:16 | 24 | 2022-09-26 07:25 | 2022-09-26 09:30 | 125 | 250 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11698594 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU-A1110-436 BLOWER NOISY |  | FM008 |  | 2023-04-23 11:53 | 2023-04-23 12:53 | 2023-04-24 12:53 | 24 | 2023-04-23 12:00 | 2023-04-23 15:35 | 215 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 106972 | 87807 |  |  | FM10619 | Junaid, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-11826757 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU-A1110-436 FILTER DIRTY T4-24-01 |  | FM008 |  | 2023-05-27 00:35 | 2023-05-27 01:35 | 2023-05-28 01:35 | 24 | 2023-05-27 00:40 | 2023-05-27 03:35 | 175 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-11149306 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU-A1110-436- CHILLED WATER LINE INSULATION DAMAGED-- |  | FM008 |  | 2022-10-29 18:57 | 2022-10-29 19:57 | 2022-10-30 19:57 | 24 | 2022-10-29 19:05 | 2022-10-29 20:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10131536 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | FILTER IS DIRTY – AHU-A1110-436 - T4-09-04 |  | FM008 |  | 2022-02-11 07:11 | 2022-02-11 08:11 | 2022-02-12 08:11 | 24 | 2022-02-11 07:15 | 2022-02-11 09:15 | 120 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2022-10902609 | ASD-MTB-FOF024-AHU049 | AIR HANDLING UNIT-05 | AHU-A1110-436 FILTER DIRTY |  | FM008 |  | 2022-08-01 08:00 | 2022-08-01 09:00 | 2022-08-02 09:00 | 24 | 2022-08-01 08:09 | 2022-08-01 10:00 | 111 | 333 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 024 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10079540 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1153-401 – C4-06A-04 |  | FM008 |  | 2022-01-26 07:36 | 2022-01-26 08:36 | 2022-01-27 08:36 | 24 | 2022-01-26 07:45 | 2022-01-26 09:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10195866 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU -A1153-401 – FILTER BLOCKED - T4-06A-03 |  | FM008 |  | 2022-02-27 10:13 | 2022-02-27 11:13 | 2022-02-28 11:13 | 24 | 2022-02-27 10:20 | 2022-02-27 13:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 105233 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10192147 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | MOTOR BELT WOBBLING-T4-06A-03 |  | FM008 |  | 2022-02-27 15:21 | 2022-02-27 16:21 | 2022-02-28 16:21 | 24 | 2022-02-27 15:30 | 2022-02-27 17:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10861748 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | SUPPLY BELT WOBBLING – T4-06A-04 |  | FM008 |  | 2022-07-19 15:28 | 2022-07-19 16:28 | 2022-07-20 16:28 | 24 | 2022-07-19 15:35 | 2022-07-19 18:45 | 190 | 125 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10861906 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | FILTER IS BLOCKED - AHU-A1153-401 - MECHANICAL ROOM T4-06A-04 |  | FM008 |  | 2022-07-20 13:16 | 2022-07-20 14:16 | 2022-07-21 14:16 | 24 | 2022-07-20 13:25 | 2022-07-20 17:30 | 245 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17573 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11039076 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU-A1153-401 FILTER DIRTY |  | FM008 |  | 2022-09-22 21:18 | 2022-09-22 22:18 | 2022-09-23 22:18 | 24 | 2022-09-22 21:25 | 2022-09-22 23:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11065475 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | FILTER BLOCKED |  | FM008 |  | 2022-10-01 02:33 | 2022-10-01 03:33 | 2022-10-02 03:33 | 24 | 2022-10-01 02:40 | 2022-10-01 04:40 | 120 | 480 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11654588 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM – T4-06A-04 |  | FM008 |  | 2023-04-12 00:37 | 2023-04-12 01:37 | 2023-04-13 01:37 | 24 | 2023-04-12 00:45 | 2023-04-12 02:15 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-11935852 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-07-02 09:55 | 2023-07-02 10:55 | 2023-07-03 10:55 | 24 | 2023-07-02 10:00 | 2023-07-02 13:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM12484 | Tekoken, Mr. Antara Hadji Hassan | N - - - |  | Voice Communication
| CM-2023-12111162 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH FAULTY - AHU-A1153-401 - T4-06A-04 |  | FM008 |  | 2023-08-24 11:03 | 2023-08-24 12:03 | 2023-08-25 12:03 | 24 | 2023-08-24 11:10 | 2023-08-24 15:30 | 260 | 305 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 133396 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2022-11224784 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU ABIN LIGHT FAULTY -T4-06A-04 |  | FM008 |  | 2022-11-27 15:37 | 2022-11-27 16:37 | 2022-11-28 16:37 | 24 | 2022-11-27 15:43 | 2022-11-27 17:08 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11253045 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | FILTER DIRTY – T4-06A-04 |  | FM008 |  | 2022-12-06 07:57 | 2022-12-06 08:57 | 2022-12-07 08:57 | 24 | 2022-12-06 08:05 | 2022-12-06 09:30 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11368182 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE - AHU-A1153-401 – T4-06A-04 |  | FM008 |  | 2023-01-14 12:54 | 2023-01-14 13:54 | 2023-01-15 13:54 | 24 | 2023-01-14 13:00 | 2023-01-14 17:15 | 255 | 965 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 124475 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12022191 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU-A1153-401-CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-07-30 11:19 | 2023-07-30 12:19 | 2023-07-31 12:19 | 24 | 2023-07-30 11:25 | 2023-07-30 13:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 77406 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12115279 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED - AHU-A1153-401 – T4-06A-04 |  | FM008 |  | 2023-08-26 12:19 | 2023-08-26 13:19 | 2023-08-27 13:19 | 24 | 2023-08-26 12:25 | 2023-08-26 15:30 | 185 | 555 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-12377768 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | A/C IS TOO COLD SN-1048 (FOOD COURT) |  | FM008 |  | 2023-11-13 11:21 | 2023-11-13 12:21 | 2023-11-14 12:21 | 24 | 2023-11-13 11:25 | 2023-11-13 16:00 | 275 | 60 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  |  | MAHEDI | N - - - |  | Voice Communication
| CM-2023-11800205 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AIR HANDLING UNIT 172 (TAG NO:AHU-A1153-401)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 06A |  | FM008 |  | 2023-05-17 19:04 | 2023-05-17 20:04 | 2023-05-18 20:04 | 24 | 2023-05-17 19:10 | 2023-05-17 22:35 | 205 | 365 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 132112 | 17053 |  |  | 10302 | Thomas J K | N - - - |  | BMS
| CM-2024-12627915 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM AHU |  | FM008 |  | 2024-02-05 10:34 | 2024-02-05 11:34 | 2024-02-06 11:34 | 24 | 2024-02-05 10:45 | 2024-02-05 14:00 | 195 | 536 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12364270 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-11-09 12:00 | 2023-11-09 13:00 | 2023-11-10 13:00 | 24 | 2023-11-09 12:05 | 2023-11-09 15:30 | 205 | 410 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 121959 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2024-12644822 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING |  | FM008 |  | 2024-02-12 19:03 | 2024-02-12 20:03 | 2024-02-13 20:03 | 24 | 2024-02-12 19:10 | 2024-02-12 21:55 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12708080 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM THE UNIT, AHU-A1153-401, T4-06A-04 |  | FM008 |  | 2024-03-05 14:21 | 2024-03-05 15:21 | 2024-03-06 15:21 | 24 | 2024-03-05 14:30 | 2024-03-05 17:00 | 150 | 600 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10059922 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY T4-06A-04 |  | FM008 |  | 2022-01-20 03:01 | 2022-01-20 04:01 | 2022-01-21 04:01 | 24 | 2022-01-20 03:05 | 2022-01-20 06:55 | 230 | 460 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10201551 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | DUCT INSULLATION IS DAMAGED - AHU-A1153-401 - T4-06A-04 |  | FM008 |  | 2022-02-28 22:32 | 2022-02-28 23:32 | 2022-03-01 23:32 | 24 | 2022-02-28 22:40 | 2022-02-28 23:55 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11112600 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | FILTER DIRTY-T4-06A-04 |  | FM008 |  | 2022-10-19 08:18 | 2022-10-19 09:18 | 2022-10-20 09:18 | 24 | 2022-10-19 08:25 | 2022-10-19 12:40 | 255 | 200 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10604202 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | AHU-A1153-401- FILTER DIRTY -T4-06A-04 |  | FM008 |  | 2022-04-28 19:34 | 2022-04-28 20:34 | 2022-04-29 20:34 | 24 | 2022-04-28 19:40 | 2022-04-28 21:30 | 110 | 330 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10791704 | ASD-MTB-FOF06A-AHU172 | AIR HANDLING UNIT-05 | FILTER BLOCKED – T4-06A-04 |  | FM008 |  | 2022-06-28 22:34 | 2022-06-28 23:34 | 2022-06-29 23:34 | 24 | 2022-06-28 22:44 | 2022-06-28 23:59 | 75 | 225 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10079063 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU-A1153-402 – COIL DIRTY- T4-06A-04 |  | FM008 |  | 2022-01-24 19:06 | 2022-01-24 20:06 | 2022-01-25 20:06 | 24 | 2022-01-24 19:15 | 2022-01-24 23:15 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11062423 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU-A1153-402-DP1 FILTER DIRTY |  | FM008 |  | 2022-09-27 02:27 | 2022-09-27 03:27 | 2022-09-28 03:27 | 24 | 2022-09-27 02:35 | 2022-09-27 05:30 | 175 | 260 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11764330 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1153-402 – T4-06A-04 |  | FM008 |  | 2023-05-04 15:10 | 2023-05-04 16:10 | 2023-05-05 16:10 | 24 | 2023-05-04 15:15 | 2023-05-04 18:45 | 210 | 205 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12117683 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1153-402 – T4-06A-04 |  | FM008 |  | 2023-08-26 19:09 | 2023-08-26 20:09 | 2023-08-27 20:09 | 24 | 2023-08-26 19:15 | 2023-08-26 21:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12365506 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED AHU-A1153-402 |  | FM008 |  | 2023-11-09 07:56 | 2023-11-09 08:56 | 2023-11-10 08:56 | 24 | 2023-11-09 08:00 | 2023-11-09 11:30 | 210 | 420 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11093908 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING.-AHU-A1153-402 |  | FM008 |  | 2022-10-09 19:11 | 2022-10-09 20:11 | 2022-10-10 20:11 | 24 | 2022-10-09 19:15 | 2022-10-09 20:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 77406 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11486709 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKING - AHU-A1153-402 – T4-06A-04 |  | FM008 |  | 2023-02-25 19:29 | 2023-02-25 20:29 | 2023-02-26 20:29 | 24 | 2023-02-25 19:35 | 2023-02-25 22:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11825612 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1153-402 - - T4 06A 04 |  | FM008 |  | 2023-05-26 20:03 | 2023-05-26 21:03 | 2023-05-27 21:03 | 24 | 2023-05-26 20:10 | 2023-05-26 23:00 | 170 | 340 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12033210 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED - AHU-A1153-402 - T4-06A-04 |  | FM008 |  | 2023-07-31 07:35 | 2023-07-31 08:35 | 2023-08-01 08:35 | 24 | 2023-07-31 07:40 | 2023-07-31 10:00 | 140 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 133396 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12138851 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU-A1153-402-DUCT INSULATION DAMAGE-T4-06A-04 |  | FM008 |  | 2023-09-02 19:18 | 2023-09-02 20:18 | 2023-09-03 20:18 | 24 | 2023-09-02 19:25 | 2023-09-02 22:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 77406 | 77406 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12504929 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU NOISY – (AHU-A1153-402) - |  | FM008 |  | 2023-12-25 10:08 | 2023-12-25 11:08 | 2023-12-26 11:08 | 24 | 2023-12-25 10:15 | 2023-12-25 17:00 | 405 | 945 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 132112 | 87807 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-12521495 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU-SUPPLY DUCT INSULATION DAMAGE T4-06A-04 |  | FM008 |  | 2023-12-31 23:18 | 2024-01-01 00:18 | 2024-01-02 00:18 | 24 | 2023-12-31 23:25 | 2024-01-01 01:30 | 125 | 195 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 77406 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12620996 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AHU-A1153-402-DUCT INSULATION DAMAGED |  | FM008 |  | 2024-02-05 01:08 | 2024-02-05 02:08 | 2024-02-06 02:08 | 24 | 2024-02-05 01:15 | 2024-02-05 04:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 17053 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2024-12627917 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM AHU |  | FM008 |  | 2024-02-05 10:35 | 2024-02-05 11:35 | 2024-02-06 11:35 | 24 | 2024-02-05 10:40 | 2024-02-05 16:30 | 350 | 440 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 121959 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2024-12655553 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY - AHU-A1153-402 – T4-06A-04 |  | FM008 |  | 2024-02-18 10:20 | 2024-02-18 11:20 | 2024-02-19 11:20 | 24 | 2024-02-18 10:30 | 2024-02-18 13:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10282557 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | CHILLED WATER LINE WATER PAINT FADED |  | FM008 |  | 2022-03-26 19:06 | 2022-03-26 20:06 | 2022-03-27 20:06 | 24 | 2022-03-26 19:10 | 2022-03-26 21:55 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68060 | 55709 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10734903 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | DRAIN LINE PIT DIRTY-AHU-A1153-402)-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 06A |  | FM008 |  | 2022-06-11 19:37 | 2022-06-11 20:37 | 2022-06-12 20:37 | 24 | 2022-06-11 19:40 | 2022-06-11 21:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17336 | 87807 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2022-10885711 | ASD-MTB-FOF06A-AHU173 | AIR HANDLING UNIT-05 | FILTER ALARM -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 06A |  | FM008 |  | 2022-07-28 19:49 | 2022-07-28 20:49 | 2022-07-29 20:49 | 24 | 2022-07-28 19:55 | 2022-07-28 21:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10772101 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-21 20:49 | 2022-06-21 21:49 | 2022-06-22 21:49 | 24 | 2022-06-21 20:55 | 2022-06-21 22:30 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68060 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11062424 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU-A1153-403-DP1 FILTER DIRTY |  | FM008 |  | 2022-09-27 02:29 | 2022-09-27 03:29 | 2022-09-28 03:29 | 24 | 2022-09-27 02:35 | 2022-09-27 04:00 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95217 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11805255 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU-A1153-403-FILTER BLOCKED-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 06A |  | FM008 |  | 2023-05-21 21:27 | 2023-05-21 22:27 | 2023-05-22 22:27 | 24 | 2023-05-21 21:35 | 2023-05-21 23:00 | 85 | 255 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12064779 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU-A1153-403-ABNORMAL SOUND COMNG FROM THE UNIT-T4-06A-02 |  | FM008 |  | 2023-08-09 08:34 | 2023-08-09 09:34 | 2023-08-10 09:34 | 24 | 2023-08-09 08:40 | 2023-08-09 11:30 | 170 | 465 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 95217 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12321659 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU-A1153-403 FILTER BLOCKED |  | FM008 |  | 2023-10-24 19:33 | 2023-10-24 20:33 | 2023-10-25 20:33 | 24 | 2023-10-24 19:40 | 2023-10-24 21:15 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12364605 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – T4-06A-04 |  | FM008 |  | 2023-11-11 07:37 | 2023-11-11 08:37 | 2023-11-12 08:37 | 24 | 2023-11-11 07:45 | 2023-11-11 10:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 105233 | 87807 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-12033209 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED - AHU-A1153-403 - T4-06A-04 |  | FM008 |  | 2023-07-31 07:32 | 2023-07-31 08:32 | 2023-08-01 08:32 | 24 | 2023-07-31 07:37 | 2023-07-31 12:30 | 293 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 133396 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12116792 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1153-403 – T4-06A-04 |  | FM008 |  | 2023-08-26 23:07 | 2023-08-27 00:07 | 2023-08-28 00:07 | 24 | 2023-08-26 23:15 | 2023-08-27 01:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM7252 | Anquillano, Mr. Arcie Gingco | N - - - |  | BMS
| CM-2024-12526983 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM THE UNITY – (AHU-A1153-403) – T4 06A 04 |  | FM008 |  | 2024-01-03 08:15 | 2024-01-03 09:15 | 2024-01-04 09:15 | 24 | 2024-01-03 08:20 | 2024-01-03 13:45 | 325 | 545 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 132112 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12537122 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1153-403 – T4-06A-04 |  | FM008 |  | 2024-01-07 07:54 | 2024-01-07 08:54 | 2024-01-08 08:54 | 24 | 2024-01-07 08:00 | 2024-01-07 14:00 | 360 | 245 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12553355 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1153-403 – T4-06A-04 |  | FM008 |  | 2024-01-09 07:38 | 2024-01-09 08:38 | 2024-01-10 08:38 | 24 | 2024-01-09 07:40 | 2024-01-09 11:00 | 200 | 705 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12539175 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | ABNORMAL SOUND COMING FROM UNIT - AHU-A1153-403 – T4-06A-04 |  | FM008 |  | 2024-01-09 10:37 | 2024-01-09 11:37 | 2024-01-10 11:37 | 24 | 2024-01-09 10:48 | 2024-01-09 18:40 | 472 | 377 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106973 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12576325 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU ABNORMAL NOISE -T4-06A-04 |  | FM008 |  | 2024-01-19 08:07 | 2024-01-19 09:07 | 2024-01-20 09:07 | 24 | 2024-01-19 08:15 | 2024-01-19 18:30 | 615 | 440 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2023-11969334 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU-A1153-403 FILTER ALARM - T4-06A-04 |  | FM008 |  | 2023-07-11 09:16 | 2023-07-11 10:16 | 2023-07-12 10:16 | 24 | 2023-07-11 09:20 | 2023-07-11 12:40 | 200 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12770876 | ASD-MTB-FOF06A-AHU174 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1153-403 – T4-06A-04 |  | FM008 |  | 2024-03-28 21:00 | 2024-03-28 22:00 | 2024-03-29 22:00 | 24 | 2024-03-28 21:10 | 2024-03-28 22:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 06A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 95217 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10778455 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AC TOO HOT - ARMANI, SN 1054 - HAVELOCK TEAM CARRYING OUT LEAK TEST IN THE DRAIN LINE - Fri 6/24/2022 2:06 PM |  | FM008 |  | 2022-06-24 09:00 | 2022-06-24 10:00 | 2022-06-25 10:00 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | FOURTH FLOOR AREA 07A | N |  |  |  | 121959 | 17053 |  |  | 59996 | Pahala Ange Kumbure Gedara, Mr. Shirantha Gayan Senavirathna | N - - - | ASSET NOT HANDED OVER | Voice Communication
| CM-2023-11503807 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU-A1154-401 SUPPLY BLOWER ISOLATOR SPRING DAMAGED |  | FM008 |  | 2023-03-01 19:37 | 2023-03-01 20:37 | 2023-03-02 20:37 | 24 | 2023-03-01 19:40 | 2023-03-01 21:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | BLOWER DAMAGE | REPLACED THE BLOWER | 68485 | 94954 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11620999 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED AHU-A1154-401 - T4-07A-03 |  | FM008 |  | 2023-04-05 02:37 | 2023-04-05 03:37 | 2023-04-06 03:37 | 24 | 2023-04-05 02:45 | 2023-04-05 04:45 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | CONTACTOR DAMAGED | REPLACED THE CONTCATOR | 133396 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12058906 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AC TOO WARM - ARMANI STORE |  | FM008 |  | 2023-08-08 13:12 | 2023-08-08 14:12 | 2023-08-09 14:12 | 24 | 2023-08-08 13:17 | 2023-08-08 17:35 | 258 | 65 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 87807 |  |  | 95437 | Thason, Mr. Augustine Vinoj Kumar | N - - - |  | Voice Communication
| CM-2022-11039918 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - SADDLE BAG EAST-FOURTH FLOOR AREA 07A |  | FM008 |  | 2022-09-22 19:07 | 2022-09-22 20:07 | 2022-09-23 20:07 | 24 | 2022-09-22 19:15 | 2022-09-22 21:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12189657 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | SN-1054 EMPORIO ARMANI AC TOO HOT |  | FM008 |  | 2023-09-17 01:11 | 2023-09-17 02:11 | 2023-09-18 02:11 | 24 | 2023-09-17 01:20 | 2023-09-17 03:00 | 100 | 60 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 89127 | 87807 |  |  | 116966 | Mazheika, Ms. Anastasiya | N - - - |  | Voice Communication
| CM-2023-12199277 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AHU-A1154-401 – T4-07A-03 |  | FM008 |  | 2023-09-19 18:55 | 2023-09-19 19:55 | 2023-09-20 19:55 | 24 | 2023-09-19 19:05 | 2023-09-19 21:50 | 165 | 330 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12518958 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY,AHU-A1154-401, T4-09A-03 |  | FM008 |  | 2024-01-01 07:43 | 2024-01-01 08:43 | 2024-01-02 08:43 | 24 | 2024-01-01 07:50 | 2024-01-01 12:00 | 250 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12684395 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1154-401 – T4-07A-03 |  | FM008 |  | 2024-02-26 00:20 | 2024-02-26 01:20 | 2024-02-27 01:20 | 24 | 2024-02-26 00:25 | 2024-02-26 06:30 | 365 | 455 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12324075 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU IS FILTER IS DIRTY |  | FM008 |  | 2023-10-27 00:07 | 2023-10-27 01:07 | 2023-10-28 01:07 | 24 | 2023-10-27 00:10 | 2023-10-27 01:45 | 95 | 190 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2022-10131747 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | FILTER DIRTY – AHU-A1154-401 – T4-07A-03 |  | FM008 |  | 2022-02-12 10:44 | 2022-02-12 11:44 | 2022-02-13 11:44 | 24 | 2022-02-12 10:50 | 2022-02-12 12:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10351782 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU-A1154-401 – DP3 FILTER ALARM – - |  | FM008 |  | 2022-04-12 10:20 | 2022-04-12 11:20 | 2022-04-13 11:20 | 24 | 2022-04-12 10:30 | 2022-04-12 12:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11135709 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 179,-FILTER DIRTY ,-SADDLE BAG EAST-FOURTH FLOOR AREA 07A. |  | FM008 |  | 2022-10-26 19:37 | 2022-10-26 20:37 | 2022-10-27 20:37 | 24 | 2022-10-26 19:45 | 2022-10-26 22:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11165630 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU-A1154-401- SUPPLY AIR DUCT AIR LEAKAGE FROM ACCESS DOOR-- |  | FM008 |  | 2022-11-07 13:25 | 2022-11-07 14:25 | 2022-11-08 14:25 | 24 | 2022-11-07 13:30 | 2022-11-07 15:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 94953 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-11615938 | ASD-MTB-FOF07A-AHU179 | AIR HANDLING UNIT-05 | AHU-A1154-401- SUPPLY DUCT INSULATION DAMAGED – T4-07A-03 |  | FM008 |  | 2023-04-04 02:21 | 2023-04-04 03:21 | 2023-04-05 03:21 | 24 | 2023-04-04 02:30 | 2023-04-04 03:50 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-11654559 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT ILLUMINATING - AHU-A1154-402 - MECHANICAL ROOM T4-07A-03 |  | FM008 |  | 2023-04-11 19:12 | 2023-04-11 20:12 | 2023-04-12 20:12 | 24 | 2023-04-11 19:20 | 2023-04-11 23:58 | 278 | 231 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-11787183 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | THERMOSTAT IS DETACHED - AHU-A1154-402 - TRANSFER-B BEFORE SCREENING LINE 25 |  | FM008 |  | 2023-05-14 00:57 | 2023-05-14 01:57 | 2023-05-15 01:57 | 24 | 2023-05-14 01:02 | 2023-05-14 03:45 | 163 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | FAULTY CONTROL THERMOSTAT | REPLACED THE THERMOSTAT | 17573 | 17053 |  |  | CT18523 | DERRICK | N - - - |  | Voice Communication
| CM-2023-12338819 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | LIGHTING FLEXIBLE CONNECTOR DAMAGED -T4-07A-03 |  | FM008 |  | 2023-10-30 16:08 | 2023-10-30 17:08 | 2023-10-31 17:08 | 24 | 2023-10-30 16:18 | 2023-10-30 18:40 | 142 | 247 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17333 | 87807 |  |  | FM8715 | Torino, Mr. Joriken Villondo | N - - - |  | Voice Communication
| CM-2024-12525116 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY ,AHU-A1154-402, T4-09A-03 |  | FM008 |  | 2024-01-01 07:43 | 2024-01-01 08:43 | 2024-01-02 08:43 | 24 | 2024-01-01 07:50 | 2024-01-01 09:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11276789 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 180-INSIDE MOTOR COPEX DAMAGE -T4-07A-03 |  | FM008 |  | 2022-12-18 13:49 | 2022-12-18 14:49 | 2022-12-19 14:49 | 24 | 2022-12-18 13:58 | 2022-12-18 16:58 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 77406 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11624885 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | GRILL DIRTY - CRC-A1154-402 - T4 07A 01 |  | FM008 |  | 2023-04-07 20:14 | 2023-04-07 21:14 | 2023-04-08 21:14 | 24 | 2023-04-07 20:20 | 2023-04-07 23:00 | 160 | 320 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 132112 | 87807 |  |  | FM7899 | Kazim Raza, | N - - - |  | Voice Communication
| CM-2023-11824779 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-07A-03 |  | FM008 |  | 2023-05-26 23:55 | 2023-05-27 00:55 | 2023-05-28 00:55 | 24 | 2023-05-27 | 2023-05-27 02:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12329716 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | RETURN SIDE BLOWER ABNORMAL NOISY - AHU-A1154-402 - AIR HANDLING UNIT 180-AIRSIDE-SADDLE BAG EAST-FOURTH FLOOR AREA 07A |  | FM008 |  | 2023-10-29 10:20 | 2023-10-29 11:20 | 2023-10-30 11:20 | 24 | 2023-10-29 10:30 | 2023-10-29 14:30 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 119320 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2024-12690542 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1154-402 – T4-07A-03 |  | FM008 |  | 2024-02-27 19:59 | 2024-02-27 20:59 | 2024-02-28 20:59 | 24 | 2024-02-27 20:05 | 2024-02-27 22:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2024-12770947 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | AHU-A1154-402 FILTER DIRTY – T4-07A-03 |  | FM008 |  | 2024-03-25 02:44 | 2024-03-25 03:44 | 2024-03-26 03:44 | 24 | 2024-03-25 02:50 | 2024-03-25 04:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12404600 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | AHU-A1154-402 DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-21 20:36 | 2023-11-21 21:36 | 2023-11-22 21:36 | 24 | 2023-11-21 20:40 | 2023-11-21 22:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 87807 |  |  | FM11837 | Md Shamsul Haque Ansari, Mr. Md Zafar Iqbal Ansari | N - - - |  | Voice Communication
| CM-2022-10141841 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – T4-07A-03 |  | FM008 |  | 2022-02-18 11:50 | 2022-02-18 12:50 | 2022-02-19 12:50 | 24 | 2022-02-18 11:55 | 2022-02-18 14:55 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 55709 |  |  | FM0422 | Thekkekara Jose, Mr. Shoby | N - - - |  | Voice Communication
| CM-2022-11131869 | ASD-MTB-FOF07A-AHU180 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1154-402 – T4-24-01 |  | FM008 |  | 2022-10-26 23:10 | 2022-10-27 00:10 | 2022-10-28 00:10 | 24 | 2022-10-26 23:15 | 2022-10-27 00:55 | 100 | 200 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11077313 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-10-04 00:11 | 2022-10-04 01:11 | 2022-10-05 01:11 | 24 | 2022-10-04 00:15 | 2022-10-04 02:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11887469 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | BELT DAMAGED - AHU-A1154-403 – T4 07A 03 |  | FM008 |  | 2023-06-17 09:42 | 2023-06-17 10:42 | 2023-06-18 10:42 | 24 | 2023-06-17 09:50 | 2023-06-17 13:00 | 190 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11935930 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | FILTER DIRTY, AHU-A1154-403, T4-07A-03 |  | FM008 |  | 2023-07-02 18:58 | 2023-07-02 19:58 | 2023-07-03 19:58 | 24 | 2023-07-02 19:05 | 2023-07-02 21:45 | 160 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12041254 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - T4-07A-03,MEC ROOM |  | FM008 |  | 2023-08-02 02:52 | 2023-08-02 03:52 | 2023-08-03 03:52 | 24 | 2023-08-02 03:00 | 2023-08-02 05:30 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12138997 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | DP1 FILTER ALAM |  | FM008 |  | 2023-09-03 08:13 | 2023-09-03 09:13 | 2023-09-04 09:13 | 24 | 2023-09-03 08:20 | 2023-09-03 13:30 | 310 | 425 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-12202205 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT 181-AIRSIDE-SADDLE BAG EAST-FOURTH FLOOR AREA 07A |  | FM008 |  | 2023-09-19 07:19 | 2023-09-19 08:19 | 2023-09-20 08:19 | 24 | 2023-09-19 07:25 | 2023-09-19 11:33 | 248 | 485 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12322052 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU-A1154-403-ABNORMAL SOUND FROM BLOWER (T4-074-03 |  | FM008 |  | 2023-10-26 08:51 | 2023-10-26 09:51 | 2023-10-27 09:51 | 24 | 2023-10-26 09:00 | 2023-10-26 13:00 | 240 | 720 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 77406 | 87807 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2022-11039919 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - SADDLE BAG EAST-FOURTH FLOOR AREA 07A |  | FM008 |  | 2022-09-22 19:09 | 2022-09-22 20:09 | 2022-09-23 20:09 | 24 | 2022-09-22 19:15 | 2022-09-22 21:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-11254796 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU-A1154-403 SUPPLY DUCT CANVASS DAMAGED T4-07-0 |  | FM008 |  | 2022-12-09 12:12 | 2022-12-09 13:12 | 2022-12-10 13:12 | 24 | 2022-12-09 12:20 | 2022-12-09 16:20 | 240 | 960 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12513621 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU-A1154-403 – DUCT INSULATION IS DAMAGED – T4-07A-03 |  | FM008 |  | 2023-12-30 13:41 | 2023-12-30 14:41 | 2023-12-31 14:41 | 24 | 2023-12-30 13:50 | 2023-12-30 15:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2022-11328235 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1154-403 – T4-07-03 |  | FM008 |  | 2022-12-28 19:47 | 2022-12-28 20:47 | 2022-12-29 20:47 | 24 | 2022-12-28 19:50 | 2022-12-28 23:10 | 200 | 365 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12342157 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | SUPPLY MOTOR NOISY -T4-24-07 |  | FM008 |  | 2023-10-31 14:58 | 2023-10-31 15:58 | 2023-11-01 15:58 | 24 | 2023-10-31 15:05 | 2023-10-31 18:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12343272 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | LIGHTING SWITCH NOT WORKING |  | FM008 |  | 2023-10-30 14:26 | 2023-10-30 15:26 | 2023-10-31 15:26 | 24 | 2023-10-30 14:35 | 2023-10-30 16:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOT WORKING | SUPPLY POWER FAILURE | RESET THE BREAKER | 95216 | 87807 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2024-12552391 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AC VENT DIRTY - QA1 MAIN DINING AREA NEAR FOUNTAIN BACK OF HOUSE ENTRANCE |  | FM008 |  | 2024-01-08 23:59 | 2024-01-09 00:59 | 2024-01-10 00:59 | 24 | 2024-01-09 00:10 | 2024-01-09 02:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17053 |  |  | FM11292 | Muturi, Ms. Grace | N - - - |  | Voice Communication
| CM-2024-12713524 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2024-03-07 13:56 | 2024-03-07 14:56 | 2024-03-08 14:56 | 24 | 2024-03-07 14:05 | 2024-03-07 16:00 | 115 | 345 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10074881 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – T4-07A-03 |  | FM008 |  | 2022-01-26 07:49 | 2022-01-26 08:49 | 2022-01-27 08:49 | 24 | 2022-01-26 07:55 | 2022-01-26 09:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 55709 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2022-11135707 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 181,FILTER DIRTY ,-SADDLE BAG EAST-FOURTH FLOOR AREA 07A. |  | FM008 |  | 2022-10-26 19:35 | 2022-10-26 20:35 | 2022-10-27 20:35 | 24 | 2022-10-26 19:45 | 2022-10-26 22:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11321868 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-12-28 00:08 | 2022-12-28 01:08 | 2022-12-29 01:08 | 24 | 2022-12-28 00:15 | 2022-12-28 03:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11606404 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | Event Source :RF Fail Alarm [RETURN FAN FAIL ALARM] A1154-AHU-403 |  | FM008 |  | 2023-03-30 10:11 | 2023-03-30 11:11 | 2023-03-31 11:11 | 24 | 2023-03-30 10:15 | 2023-03-30 10:45 | 30 | 30 | 1 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | WARNING | AHU TRIP ALARM | RESET UNIT | 68485 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10118041 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU-A1154-403 LIGHTING FLEXIBLE DAMAGED T4-07A-03 |  | FM008 |  | 2022-02-07 10:25 | 2022-02-07 11:25 | 2022-02-08 11:25 | 24 | 2022-02-07 10:35 | 2022-02-07 12:04 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 89127 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10654421 | ASD-MTB-FOF07A-AHU181 | AIR HANDLING UNIT-05 | AHU-A1154-403- FILTER DIRTY – T4-07A-03 |  | FM008 |  | 2022-05-11 21:39 | 2022-05-11 22:39 | 2022-05-12 22:39 | 24 | 2022-05-11 21:45 | 2022-05-12 00:15 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10162309 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU-A1110-003 AIR FILTER DIRTY |  | FM008 |  | 2022-02-24 10:41 | 2022-02-24 11:41 | 2022-02-25 11:41 | 24 | 2022-02-24 10:45 | 2022-02-24 12:00 | 75 | 225 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10256866 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-AHU-A1110-003 |  | FM008 |  | 2022-03-17 18:30 | 2022-03-17 19:30 | 2022-03-18 19:30 | 24 | 2022-03-17 18:39 | 2022-03-17 19:30 | 51 | 96 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95217 | 87807 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - |  | E-mail
| CM-2022-10578423 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | TG-06-04 – AHU A1110-003 – SUPPLY V BELT IS DAMAGED |  | FM008 |  | 2022-04-22 09:47 | 2022-04-22 10:47 | 2022-04-23 10:47 | 24 | 2022-04-22 09:57 | 2022-04-22 12:28 | 151 | 182 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94954 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2022-10859651 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU-A1110-003- DP 1 FILTER ALARM - |  | FM008 |  | 2022-07-19 09:06 | 2022-07-19 10:06 | 2022-07-20 10:06 | 24 | 2022-07-19 09:10 | 2022-07-19 09:45 | 35 | 70 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11064417 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-09-28 10:34 | 2022-09-28 11:34 | 2022-09-29 11:34 | 24 | 2022-09-28 10:40 | 2022-09-28 13:45 | 185 | 95 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11066384 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU-A1110-003 BELT DAMAGED TG-06-02 |  | FM008 |  | 2022-09-30 19:06 | 2022-09-30 20:06 | 2022-10-01 20:06 | 24 | 2022-09-30 19:15 | 2022-09-30 20:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11879514 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM AHU ATTACHED PIPES IN TX-A AREA - AHU-A1110-003 NEAR TG 06 29 |  | FM008 |  | 2023-06-13 08:30 | 2023-06-13 09:30 | 2023-06-14 09:30 | 24 | 2023-06-13 08:35 | 2023-06-13 14:30 | 355 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 133396 | 87807 |  |  | R15805 | Tariniganti, Mr. Santosh Kumar | N - - - |  | E-mail
| CM-2023-11932288 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | HOT AIR COMING FROM AHU IN BHS AREA- NEAR TG-06-29 |  | FM008 |  | 2023-06-26 19:35 | 2023-06-26 20:35 | 2023-06-27 20:35 | 24 | 2023-06-26 19:40 | 2023-06-26 21:10 | 90 | 188 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | BLOCKAGE OF AIR FLOW | REPAIR/REPLACE | 106914 | 17053 |  |  | 123812 | Kannan, Mr. Prakash | N - - - |  | Voice Communication
| CM-2023-12491342 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-12-20 08:27 | 2023-12-20 09:27 | 2023-12-21 09:27 | 24 | 2023-12-20 08:35 | 2023-12-20 15:00 | 385 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11932850 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY GROUND FLOOR AREA 006 |  | FM008 |  | 2023-06-28 21:38 | 2023-06-28 22:38 | 2023-06-29 22:38 | 24 | 2023-06-28 21:46 | 2023-06-28 23:55 | 129 | 186 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12095966 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2023-08-17 09:01 | 2023-08-17 10:01 | 2023-08-18 10:01 | 24 | 2023-08-17 09:10 | 2023-08-17 11:55 | 165 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12186905 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 002 (TAG NO:AHU-A1110-003)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 AHU-A1110-003 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP1.MTB0601.AHU003.SYSALM.DP1 / |  | FM008 |  | 2023-09-16 16:43 | 2023-09-16 17:43 | 2023-09-17 17:43 | 24 | 2023-09-16 16:45 | 2023-09-16 23:50 | 425 | 65 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94954 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12207030 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | BELT DAMAGED – AHU-A1110-003 - |  | FM008 |  | 2023-09-23 00:09 | 2023-09-23 01:09 | 2023-09-24 01:09 | 24 | 2023-09-23 00:15 | 2023-09-23 01:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12420969 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-WEST BHS GROUND FLOOR NEAR BELT TX06-002(CM-2023-02-0788) |  | FM008 |  | 2023-11-26 23:14 | 2023-11-27 00:14 | 2023-11-28 00:14 | 24 | 2023-11-26 23:20 | 2023-11-27 02:10 | 170 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 87807 | 17053 |  |  | FM11814 | Ayyappan Arunachalam | - - - |  | E-mail
| CM-2022-10995007 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU-A1110-003 DP1 FILTER DIRTY |  | FM008 |  | 2022-09-03 17:33 | 2022-09-03 18:33 | 2022-09-04 18:33 | 24 | 2022-09-03 17:40 | 2022-09-03 18:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11103144 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU-A1110-003 FILTER DIRTY |  | FM008 |  | 2022-10-16 07:24 | 2022-10-16 08:24 | 2022-10-17 08:24 | 24 | 2022-10-16 07:30 | 2022-10-16 09:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11145611 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-10-29 00:04 | 2022-10-29 01:04 | 2022-10-30 01:04 | 24 | 2022-10-29 00:10 | 2022-10-29 01:30 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11471514 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | AHU-A1110-003 FILTER DIRTY AND BELT DAMAGED |  | FM008 |  | 2023-02-18 12:53 | 2023-02-18 13:53 | 2023-02-19 13:53 | 24 | 2023-02-18 12:55 | 2023-02-18 17:10 | 255 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12378048 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | ABNORMAL NOISE FROM AHU-A1110-003, |  | FM008 |  | 2023-11-14 12:47 | 2023-11-14 13:47 | 2023-11-15 13:47 | 24 | 2023-11-14 12:55 | 2023-11-14 16:55 | 240 | 870 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10653719 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-05-13 14:51 | 2022-05-13 15:51 | 2022-05-14 15:51 | 24 | 2022-05-13 15:00 | 2022-05-13 18:49 | 229 | 128 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10707702 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS FILTERS 755-AIR HANDLING UNIT 002 (TAG NO:AHU-A1110-003)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP1.MTB0601.AHU003.SYSALM.DP1 / |  | FM008 |  | 2022-05-30 12:45 | 2022-05-30 13:45 | 2022-05-31 13:45 | 24 | 2022-05-30 12:50 | 2022-05-30 14:30 | 100 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2022-11097835 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-AHU-A1110-003-AIR HANDLING UNIT 002 (TAG NO:AHU-A1110-003)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006-PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP1.MTB0601.AHU003.SYSALM.DP1 / |  | FM008 |  | 2022-10-12 23:35 | 2022-10-13 00:35 | 2022-10-14 00:35 | 24 | 2022-10-12 23:40 | 2022-10-13 04:10 | 270 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10162310 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED |  | FM008 |  | 2022-02-24 10:42 | 2022-02-24 11:42 | 2022-02-25 11:42 | 24 | 2022-02-24 10:50 | 2022-02-24 13:15 | 145 | 230 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10679393 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-05-20 21:01 | 2022-05-20 22:01 | 2022-05-21 22:01 | 24 | 2022-05-20 21:10 | 2022-05-20 22:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10798957 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-003 |  | FM008 |  | 2022-07-02 04:41 | 2022-07-02 05:41 | 2022-07-03 05:41 | 24 | 2022-07-02 04:50 | 2022-07-02 06:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 85125 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10826105 | ASD-MTB-GFL006-AHU002 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2022-07-10 09:48 | 2022-07-10 10:48 | 2022-07-11 10:48 | 24 | 2022-07-10 09:55 | 2022-07-10 11:00 | 65 | 130 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10192270 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | CABIN LIGHT FAULTY -TX06002 |  | FM008 |  | 2022-02-28 09:24 | 2022-02-28 10:24 | 2022-03-01 10:24 | 24 | 2022-02-28 09:33 | 2022-02-28 13:33 | 240 | 181 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17333 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10208397 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 – FILTER DIRTY – TG-06-04 |  | FM008 |  | 2022-03-01 02:02 | 2022-03-01 03:02 | 2022-03-02 03:02 | 24 | 2022-03-01 02:12 | 2022-03-01 03:12 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10256867 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-004-DP3 DUST FILTER STATUS |  | FM008 |  | 2022-03-17 18:31 | 2022-03-17 19:31 | 2022-03-18 19:31 | 24 | 2022-03-17 18:40 | 2022-03-17 20:05 | 85 | 95 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 87807 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - |  | E-mail
| CM-2022-10593642 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM AHU-A1110-005 BHS |  | FM008 |  | 2022-04-26 14:17 | 2022-04-26 15:17 | 2022-04-27 15:17 | 24 | 2022-04-26 14:30 | 2022-04-26 17:30 | 180 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 85125 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10676451 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2022-05-19 13:21 | 2022-05-19 14:21 | 2022-05-20 14:21 | 24 | 2022-05-19 13:25 | 2022-05-19 16:40 | 195 | 65 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 121959 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10710830 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-31 08:15 | 2022-05-31 09:15 | 2022-06-01 09:15 | 24 | 2022-05-31 08:25 | 2022-05-31 13:00 | 275 | 145 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11064418 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-09-28 10:36 | 2022-09-28 11:36 | 2022-09-29 11:36 | 24 | 2022-09-28 10:45 | 2022-09-28 14:30 | 225 | 75 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11230259 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-005 |  | FM008 |  | 2022-11-28 09:14 | 2022-11-28 10:14 | 2022-11-29 10:14 | 24 | 2022-11-28 09:20 | 2022-11-28 14:00 | 280 | 840 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 17053 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2023-11362668 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DPI FILTER ALARM - AHU-A1110-005 – TG-06-02 |  | FM008 |  | 2023-01-12 07:26 | 2023-01-12 08:26 | 2023-01-13 08:26 | 24 | 2023-01-12 07:35 | 2023-01-12 09:00 | 85 | 175 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11362670 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | BELT DAMAGED – AHU-A1110-005 – TG-06-02 |  | FM008 |  | 2023-01-12 07:27 | 2023-01-12 08:27 | 2023-01-13 08:27 | 24 | 2023-01-12 07:30 | 2023-01-12 08:30 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11564457 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS AHU-A1110-005 GROUND FLOOR AREA 006 |  | FM008 |  | 2023-03-15 15:06 | 2023-03-15 16:06 | 2023-03-16 16:06 | 24 | 2023-03-15 15:10 | 2023-03-15 23:55 | 525 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11587492 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | BELT DAMAGED -AIR HANDLING UNIT 004 (TAG NO:AHU-A1110-005)--MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2023-03-22 21:12 | 2023-03-22 22:12 | 2023-03-23 22:12 | 24 | 2023-03-22 21:21 | 2023-03-22 23:00 | 99 | 198 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11800845 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-005 - TG-06-04 |  | FM008 |  | 2023-05-16 21:18 | 2023-05-16 22:18 | 2023-05-17 22:18 | 24 | 2023-05-16 21:25 | 2023-05-16 23:59 | 154 | 173 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-11859123 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM FILTERS 757-AIR HANDLING UNIT 004 (TAG NO:AHU-A1110-005)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2023-06-06 00:50 | 2023-06-06 01:50 | 2023-06-07 01:50 | 24 | 2023-06-06 00:55 | 2023-06-06 03:30 | 155 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 94954 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12015392 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 -FILTER DIRTY NEAR BELT TX-06-002 |  | FM008 |  | 2023-07-29 00:10 | 2023-07-29 01:10 | 2023-07-30 01:10 | 24 | 2023-07-29 00:16 | 2023-07-29 02:16 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11215207 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 SUPPLY FAN MOTOR FLEXIBLE CONNECTOR DAMAGED NEAR BELT TX06-002 |  | FM008 |  | 2022-11-22 13:31 | 2022-11-22 14:31 | 2022-11-23 14:31 | 24 | 2022-11-22 13:38 | 2022-11-22 15:03 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11587142 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | FILTER DIRTY - A1110-005 - TG 06 04 |  | FM008 |  | 2023-03-23 00:30 | 2023-03-23 01:30 | 2023-03-24 01:30 | 24 | 2023-03-23 00:35 | 2023-03-23 04:00 | 205 | 195 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11866077 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | TG-06-19 AREA -TO FIX DAMAGE DUCT AIR FLOW NEAR MT01 X- RAY MACHINE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006- |  | FM008 |  | 2023-06-10 15:51 | 2023-06-10 16:51 | 2023-06-11 16:51 | 24 | 2023-06-10 16:00 | 2023-06-10 18:40 | 160 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 17336 | 87807 |  |  | 118157 | Shekher, Mr. Sheshank | N - - - |  | Voice Communication
| CM-2023-12015519 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | WEE BELT DAMAGED - AHU-A1110-005 – TG-06-02 |  | FM008 |  | 2023-07-29 12:28 | 2023-07-29 13:28 | 2023-07-30 13:28 | 24 | 2023-07-29 12:35 | 2023-07-29 15:15 | 160 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-11471515 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 FILTER DIRTY AND BELT DAMAGED |  | FM008 |  | 2023-02-18 12:53 | 2023-02-18 13:53 | 2023-02-19 13:53 | 24 | 2023-02-18 13:03 | 2023-02-18 15:30 | 147 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12209743 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | V-BELT DAMAGED |  | FM008 |  | 2023-09-22 09:44 | 2023-09-22 10:44 | 2023-09-23 10:44 | 24 | 2023-09-22 09:50 | 2023-09-22 10:50 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12281524 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | HEAVY WATER LEAKAGE – (AHU- A1110-003) -TG 06 02 |  | FM008 |  | 2023-10-15 09:40 | 2023-10-15 10:40 | 2023-10-16 10:40 | 24 | 2023-10-15 09:50 | 2023-10-15 11:40 | 110 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 132112 | 87807 |  |  | CT18378 | SARANDRAJ | N - - - |  | Voice Communication
| CM-2023-12399216 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | BEARING NOISY - AIR HANDLING UNIT 004 (TAG NO:AHU-A1110-005)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2023-11-22 10:05 | 2023-11-22 11:05 | 2023-11-23 11:05 | 24 | 2023-11-22 10:15 | 2023-11-22 12:20 | 125 | 375 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 119320 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2024-12796940 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 DP3 FILTER DIRTY |  | FM008 |  | 2024-04-04 10:10 | 2024-04-04 11:10 | 2024-04-05 11:10 | 24 | 2024-04-04 10:15 | 2024-04-04 18:35 | 500 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM12908 | Kumar, Mr. Abhishek | N - - - |  | Voice Communication
| CM-2022-10118588 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM - |  | FM008 |  | 2022-02-06 20:31 | 2022-02-06 21:31 | 2022-02-07 21:31 | 24 | 2022-02-06 20:40 | 2022-02-06 22:25 | 105 | 280 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10203910 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU V BELT DAMAGED -TG-06-02 |  | FM008 |  | 2022-02-28 13:09 | 2022-02-28 14:09 | 2022-03-01 14:09 | 24 | 2022-02-28 13:15 | 2022-02-28 14:30 | 75 | 225 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10252480 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 DP3 FILTER ALARM TG-06-04 |  | FM008 |  | 2022-03-14 21:08 | 2022-03-14 22:08 | 2022-03-15 22:08 | 24 | 2022-03-14 21:18 | 2022-03-14 22:30 | 72 | 144 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10307706 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED -AHU-A1110-005)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2022-03-30 07:01 | 2022-03-30 08:01 | 2022-03-31 08:01 | 24 | 2022-03-30 07:10 | 2022-03-30 08:30 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10652425 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM |  | FM008 |  | 2022-05-11 09:35 | 2022-05-11 10:35 | 2022-05-12 10:35 | 24 | 2022-05-11 09:45 | 2022-05-11 10:45 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10771095 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP 3 FILTER ALARM -BHS GF |  | FM008 |  | 2022-06-22 07:22 | 2022-06-22 08:22 | 2022-06-23 08:22 | 24 | 2022-06-22 07:30 | 2022-06-22 10:00 | 150 | 186 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17333 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10824990 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS -FILTERS 757-AIR HANDLING UNIT 004 |  | FM008 |  | 2022-07-09 05:14 | 2022-07-09 06:14 | 2022-07-10 06:14 | 24 | 2022-07-09 05:20 | 2022-07-09 08:10 | 170 | 215 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10886156 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP1.MTB0601.AHU005.SYSALM.DP3 //FILTERS 757-AIR HANDLING UNIT 004 (TAG NO:AHU-A1110-005)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2022-07-30 10:49 | 2022-07-30 11:49 | 2022-07-31 11:49 | 24 | 2022-07-30 10:55 | 2022-07-30 20:00 | 545 | 130 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 87807 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - |  | BMS
| CM-2022-11063059 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | V-BELT DAMAGED-AHU-A1110-005)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 006 |  | FM008 |  | 2022-09-30 08:32 | 2022-09-30 09:32 | 2022-10-01 09:32 | 24 | 2022-09-30 08:40 | 2022-09-30 11:00 | 140 | 145 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 95217 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-10078886 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS AHU-A1110-005 NEAR BELT TX06-002 |  | FM008 |  | 2022-01-24 06:30 | 2022-01-24 07:30 | 2022-01-25 07:30 | 24 | 2022-01-24 06:40 | 2022-01-24 08:00 | 80 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 55709 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | BMS
| CM-2022-10359756 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM AHU-A1110-005 |  | FM008 |  | 2022-04-12 00:52 | 2022-04-12 01:52 | 2022-04-13 01:52 | 24 | 2022-04-12 01:00 | 2022-04-12 09:40 | 520 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2022-10676579 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-20 06:24 | 2022-05-20 07:24 | 2022-05-21 07:24 | 24 | 2022-05-20 06:30 | 2022-05-20 14:30 | 480 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | E-mail
| CM-2022-10709213 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AHU-A1110-005 SUPPLY BELT DAMAGED |  | FM008 |  | 2022-06-02 00:11 | 2022-06-02 01:11 | 2022-06-03 01:11 | 24 | 2022-06-02 00:20 | 2022-06-02 01:35 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2023-11931556 | ASD-MTB-GFL006-AHU004 | AIR HANDLING UNIT-05 | AC TOO HOT (NO AIR FLOW) - FCU NUMBERS: FCU-A7211-COA-L0-001 & FCU-A7211-COB-L0-003 |  | FM008 |  | 2023-06-27 15:38 | 2023-06-27 16:38 | 2023-06-28 16:38 | 24 | 2023-06-27 15:45 | 2023-06-27 17:35 | 110 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 006 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 121959 | 17053 |  |  | CBG159 | JOHN PETER | N - - - |  | Voice Communication
| CM-2024-12715630 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM SUPPLY SIDE - AHU-A1110-007 – TG-06-04 |  | FM008 |  | 2024-03-10 09:30 | 2024-03-10 10:30 | 2024-03-11 10:30 | 24 | 2024-03-10 09:35 | 2024-03-10 13:30 | 235 | 705 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 133396 | 87807 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12057216 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | :AHU-A1110-007)-WATER DRIPPING FROM THE CEILING -NEAR TG-S03 |  | FM008 |  | 2023-08-07 17:36 | 2023-08-07 18:36 | 2023-08-08 18:36 | 24 | 2023-08-07 17:40 | 2023-08-07 22:05 | 265 | 250 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 77406 | 87807 |  |  | 108454 | Khan, Mr. Mohammed Javed Shamshad | N - - - |  | Voice Communication
| CM-2023-12128322 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | AHU-A1110-007 SUPPLY BELT DAMAGED |  | FM008 |  | 2023-08-30 10:33 | 2023-08-30 11:33 | 2023-08-31 11:33 | 24 | 2023-08-30 10:40 | 2023-08-30 16:05 | 325 | 276 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12342349 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | AHU-A1110-007 V-BELT DAMAGED TG-07-02 |  | FM008 |  | 2023-11-01 13:34 | 2023-11-01 14:34 | 2023-11-02 14:34 | 24 | 2023-11-01 13:40 | 2023-11-01 15:00 | 80 | 160 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 87807 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-12344598 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1110-007 – TG-07-02 |  | FM008 |  | 2023-11-04 10:54 | 2023-11-04 11:54 | 2023-11-05 11:54 | 24 | 2023-11-04 11:00 | 2023-11-04 18:30 | 450 | 155 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM5381 | Thomas, Mr. Joseph | N - - - |  | Voice Communication
| CM-2024-12611423 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM AHU A1110-007 AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 008 |  | FM008 |  | 2024-01-30 23:57 | 2024-01-31 00:57 | 2024-02-01 00:57 | 24 | 2024-01-31 00:05 | 2024-01-31 03:15 | 190 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 138627 | 17053 |  |  | 127430 | Pheme, Mrs. Mmaphefo Paballo Martha | N - - - |  | Voice Communication
| CM-2023-12258117 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2023-10-06 20:01 | 2023-10-06 21:01 | 2023-10-07 21:01 | 24 | 2023-10-06 20:10 | 2023-10-06 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 87807 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2022-10987782 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | WATER LEAKAGE FRROM THE AHU /CEILING (ONE NEAR THE LIGHT) - TG-06-28 |  | FM008 |  | 2022-08-29 15:30 | 2022-08-29 16:00 | 2022-08-29 20:00 | 4 | 2022-08-29 15:35 | 2022-08-29 16:05 | 30 | 30 | 1 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 55709 |  |  | R12402 | Dhaya, Mr. Lotfi Ben | N - - - |  | Voice Communication
| CM-2023-12186669 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | AC TOO HOT TG-07-16 |  | FM008 |  | 2023-09-15 16:21 | 2023-09-15 17:21 | 2023-09-16 17:21 | 24 | 2023-09-15 16:30 | 2023-09-15 17:25 | 55 | 55 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 68485 | 17053 |  |  | 118474 | Jha, Mr. Ashish | N - - - |  | Voice Communication
| CM-2023-12257480 | ASD-MTB-GFL008-AHU006 | AIR HANDLING UNIT-05 | CONDENSATION DRAIN PUMP FAULTY - AHU-A1110-007 – TG-08-19 |  | FM008 |  | 2023-10-08 00:01 | 2023-10-08 01:01 | 2023-10-09 01:01 | 24 | 2023-10-08 00:06 | 2023-10-08 02:30 | 144 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | DRAIN PUMP FAULTY | REPAIRED/REPLACED | 106973 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10730303 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS WEST BHS GROUND FLOOR NEAR BELT TX06-002 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP4.MTB0801.AHU009.SYSALM.DP3 / - UNDER MTT-JV - Fri 6/10/2022 12:38 AM |  | FM008 |  | 2022-06-09 11:59 | 2022-06-09 12:59 | 2022-06-10 12:59 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | GROUND FLOOR AREA 008 | N | DAMAGED |  |  | 106972 | 17053 |  |  | FM0459 | MANHANDAVIDA SHAHEEL | N - - - | ASSET NOT HANDED OVER | E-mail
| CM-2023-12206382 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS |  | FM008 |  | 2023-09-21 00:40 | 2023-09-21 01:40 | 2023-09-22 01:40 | 24 | 2023-09-21 00:50 | 2023-09-21 18:35 | 1065 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12313675 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM |  | FM008 |  | 2023-10-23 08:25 | 2023-10-23 09:25 | 2023-10-24 09:25 | 24 | 2023-10-23 08:30 | 2023-10-23 18:40 | 610 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12346450 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-009 – TG-08-19 |  | FM008 |  | 2023-11-04 11:03 | 2023-11-04 12:03 | 2023-11-05 12:03 | 24 | 2023-11-04 11:10 | 2023-11-04 18:35 | 445 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12366254 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM- WEST BHS GROUND FLOOR NEAR BELT TX06-002 |  | FM008 |  | 2023-11-10 18:12 | 2023-11-10 19:12 | 2023-11-11 19:12 | 24 | 2023-11-10 18:20 | 2023-11-10 22:25 | 245 | 277 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106914 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2024-12824136 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS, AHU-A1110-009, WEST BHS GROUND FLOOR NEAR BELT TX06-002 |  | FM008 |  | 2024-04-13 11:00 | 2024-04-13 12:00 | 2024-04-14 12:00 | 24 | 2024-04-13 11:05 | 2024-04-13 16:00 | 295 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | E-mail
| CM-2023-12325029 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM AHU-A1110-009 |  | FM008 |  | 2023-10-26 02:24 | 2023-10-26 03:24 | 2023-10-27 03:24 | 24 | 2023-10-26 02:30 | 2023-10-26 12:15 | 585 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12132263 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED AHU-A1110-009 |  | FM008 |  | 2023-08-30 13:19 | 2023-08-30 14:19 | 2023-08-31 14:19 | 24 | 2023-08-30 13:25 | 2023-08-30 16:35 | 190 | 187 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12232035 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS |  | FM008 |  | 2023-09-27 08:20 | 2023-09-27 09:20 | 2023-09-28 09:20 | 24 | 2023-09-27 08:30 | 2023-09-27 17:15 | 525 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12299054 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM WEST BHS GROUND FLOOR NEAR BELT TX06-002 |  | FM008 |  | 2023-10-18 21:09 | 2023-10-18 22:09 | 2023-10-19 22:09 | 24 | 2023-10-18 21:15 | 2023-10-19 01:32 | 257 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106972 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12379695 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM |  | FM008 |  | 2023-11-13 06:22 | 2023-11-13 07:22 | 2023-11-14 07:22 | 24 | 2023-11-13 06:30 | 2023-11-13 12:05 | 335 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - | ASSET CURRENTLY IN USE/OPERATION | BMS
| CM-2023-12252492 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM WEST BHS GROUND FLOOR NEAR BELT TX06-002 |  | FM008 |  | 2023-10-03 21:17 | 2023-10-03 22:17 | 2023-10-04 22:17 | 24 | 2023-10-03 21:25 | 2023-10-04 04:00 | 395 | 130 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12278452 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM LOCATION: WEST BHS GROUND FLOOR NEAR BELT TX06-002 EXTRA REMARKS: PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP4.MTB0801.AHU009.SYSALM.DP3 / |  | FM008 |  | 2023-10-12 07:49 | 2023-10-12 08:49 | 2023-10-13 08:49 | 24 | 2023-10-12 08:00 | 2023-10-13 01:00 | 1020 | 125 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 138627 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2023-12343945 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | AHU-A1110-009 DP3 DUST FILTER STATUS ALARM WEST BHS GROUND FLOOR NEAR BELT TX06-002 |  | FM008 |  | 2023-11-02 09:36 | 2023-11-02 10:36 | 2023-11-03 10:36 | 24 | 2023-11-02 09:45 | 2023-11-02 10:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12346621 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | BLOWER PAINT FADED - AIR HANDLING UNIT 008 (TAG NO:AHU-A1110-009)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 008 - TG-08-19 |  | FM008 |  | 2023-11-05 07:20 | 2023-11-05 08:20 | 2023-11-06 08:20 | 24 | 2023-11-05 07:25 | 2023-11-05 09:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 119320 | 17053 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12383109 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM |  | FM008 |  | 2023-11-15 18:19 | 2023-11-15 19:19 | 2023-11-16 19:19 | 24 | 2023-11-15 18:25 | 2023-11-15 20:30 | 125 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12422323 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM-(WEST BHS GROUND FLOOR NEAR BELT TX06-002) |  | FM008 |  | 2023-11-28 09:55 | 2023-11-28 10:55 | 2023-11-29 10:55 | 24 | 2023-11-28 10:10 | 2023-11-28 18:10 | 480 | 188 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 77406 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2024-12851455 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AHU-A1110-009 - WEST BHS GROUND FLOOR NEAR BELT TX06-002 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP4.MTB0801.AHU009.SYSALM.DP3 / |  | FM008 |  | 2024-04-28 06:39 | 2024-04-28 07:39 | 2024-04-29 07:39 | 24 | 2024-04-28 06:45 | 2024-04-28 08:30 | 105 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-11189915 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - MAIN TERMINAL BUILDING-GROUND FLOOR AREA 008 |  | FM008 |  | 2022-11-15 14:13 | 2022-11-15 15:13 | 2022-11-16 15:13 | 24 | 2022-11-15 14:20 | 2022-11-15 15:00 | 40 | 120 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11384597 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | AHU-A1110-009 – WATER DRIPPING FROM CHILLED WATER LINE - TG-06-04 |  | FM008 |  | 2023-01-19 13:04 | 2023-01-19 14:04 | 2023-01-20 14:04 | 24 | 2023-01-19 13:14 | 2023-01-19 18:00 | 286 | 146 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 94954 |  |  | FM5829 | Soosai Manickam, Mr. Sundar John Bosco | N - - - |  | Voice Communication
| CM-2023-12157105 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AIR HANDLING UNIT 008 (TAG NO:AHU-A1110-009)-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 008 |  | FM008 |  | 2023-09-06 21:18 | 2023-09-06 22:18 | 2023-09-07 22:18 | 24 | 2023-09-06 21:25 | 2023-09-06 23:40 | 135 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-12180201 | ASD-MTB-GFL008-AHU008 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AHU-A1110-009 - WEST BHS GROUND FLOOR NEAR BELT TX06-002 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP4.MTB0801.AHU009.SYSALM.DP3 / |  | FM008 |  | 2023-09-11 04:17 | 2023-09-11 05:17 | 2023-09-12 05:17 | 24 | 2023-09-11 04:25 | 2023-09-11 08:30 | 245 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2022-10612955 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | FILTER DIRTY :AHU-A1110-001) |  | FM008 |  | 2022-04-30 19:42 | 2022-04-30 20:42 | 2022-05-01 20:42 | 24 | 2022-04-30 19:51 | 2022-04-30 21:40 | 109 | 218 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11340370 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM -MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-01-02 06:57 | 2023-01-02 07:57 | 2023-01-03 07:57 | 24 | 2023-01-02 07:05 | 2023-01-02 11:10 | 245 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11901729 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | DP1 FULTER ALARM - AHU-A1110-001)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 -TG-07-11 |  | FM008 |  | 2023-06-21 19:01 | 2023-06-21 20:01 | 2023-06-22 20:01 | 24 | 2023-06-21 19:10 | 2023-06-21 21:35 | 145 | 188 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12065703 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | WATER LEAKING FROM CHILLED WATER PIPE – NEAR TG-07-11 |  | FM008 |  | 2023-08-10 16:44 | 2023-08-10 17:44 | 2023-08-11 17:44 | 24 | 2023-08-10 16:50 | 2023-08-10 23:25 | 395 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 106973 | 87807 |  |  | CT17930 | DHANABALAN | N - - - |  | Voice Communication
| CM-2023-12226022 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - AHU-A1110-001 â?? TG-07-11 |  | FM008 |  | 2023-09-25 14:44 | 2023-09-25 15:44 | 2023-09-26 15:44 | 24 | 2023-09-25 14:50 | 2023-09-25 17:50 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 133396 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-11254181 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | CHILLED WATER LINE INSOLATION DAMAGED AND PAINT FADED- AHU-A1110-001 |  | FM008 |  | 2022-12-07 00:35 | 2022-12-07 01:35 | 2022-12-08 01:35 | 24 | 2022-12-07 00:40 | 2022-12-07 04:10 | 210 | 420 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM9663 | PRIYANGA MADURA AA, Mr. | N - - - |  | Voice Communication
| CM-2022-11217236 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - GROUND FLOOR AREA 007 |  | FM008 |  | 2022-11-23 16:26 | 2022-11-23 17:26 | 2022-11-24 17:26 | 24 | 2022-11-23 16:30 | 2022-11-23 18:25 | 115 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11253228 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | FILTER DIRTY -TG-07-11 |  | FM008 |  | 2022-12-06 18:51 | 2022-12-06 19:51 | 2022-12-07 19:51 | 24 | 2022-12-06 19:00 | 2022-12-06 20:30 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11579538 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-001 ,TG-07-14 |  | FM008 |  | 2023-03-21 00:11 | 2023-03-21 01:11 | 2023-03-22 01:11 | 24 | 2023-03-21 00:20 | 2023-03-21 01:45 | 85 | 255 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2024-12649823 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | FILTER DIRYT AHU-A1110-001) |  | FM008 |  | 2024-02-13 09:55 | 2024-02-13 10:55 | 2024-02-14 10:55 | 24 | 2024-02-13 10:05 | 2024-02-13 17:30 | 445 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM11231 | Maria Thayalan, Mr. Anto Sam Daniel | N - - - |  | Voice Communication
| CM-2022-10159033 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-001 – TG-07-11 |  | FM008 |  | 2022-02-22 19:12 | 2022-02-22 20:12 | 2022-02-23 20:12 | 24 | 2022-02-22 19:20 | 2022-02-22 20:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10159034 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | BELT DAMAGED - AHU-A1110-001 – TG-07-11 |  | FM008 |  | 2022-02-22 19:13 | 2022-02-22 20:13 | 2022-02-23 20:13 | 24 | 2022-02-22 19:20 | 2022-02-22 22:15 | 175 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10251407 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - AHU-A1110-001 – TG-07-11 |  | FM008 |  | 2022-03-14 08:06 | 2022-03-14 09:06 | 2022-03-15 09:06 | 24 | 2022-03-14 08:16 | 2022-03-14 12:10 | 234 | 190 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12188624 | ASD-MTB-GFL007-AHU001 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – TG-07-11 |  | FM008 |  | 2023-09-16 10:15 | 2023-09-16 11:15 | 2023-09-17 11:15 | 24 | 2023-09-16 10:20 | 2023-09-16 15:35 | 315 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10085552 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 DP3 FILTER ALARM |  | FM008 |  | 2022-01-30 07:23 | 2022-01-30 08:23 | 2022-01-31 08:23 | 24 | 2022-01-30 07:30 | 2022-01-30 08:30 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10201452 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AMCC-AHU-A1110-004 – NEAR BELT TX01-001 |  | FM008 |  | 2022-02-28 08:39 | 2022-02-28 09:39 | 2022-03-01 09:39 | 24 | 2022-02-28 08:48 | 2022-02-28 11:59 | 191 | 183 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | EXTRACT FAN FAULTY | REPAIRED THE FAN | 106973 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10192284 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED |  | FM008 |  | 2022-02-28 10:23 | 2022-02-28 11:23 | 2022-03-01 11:23 | 24 | 2022-02-28 10:30 | 2022-02-28 11:50 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10312358 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004-DP3 FILTER ALARM |  | FM008 |  | 2022-04-02 21:23 | 2022-04-02 22:23 | 2022-04-03 22:23 | 24 | 2022-04-02 21:30 | 2022-04-02 23:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10364417 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 DP 3 FILTER ALARM –EAST BHS GROUND FLOOR |  | FM008 |  | 2022-04-15 20:13 | 2022-04-15 21:13 | 2022-04-16 21:13 | 24 | 2022-04-15 20:20 | 2022-04-15 21:20 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10734835 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2022-06-11 11:06 | 2022-06-11 12:06 | 2022-06-12 12:06 | 24 | 2022-06-11 11:16 | 2022-06-11 16:40 | 324 | 206 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10820016 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - AHU-A1110-004 – EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-07-05 11:08 | 2022-07-05 12:08 | 2022-07-06 12:08 | 24 | 2022-07-05 11:15 | 2022-07-05 12:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10826473 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3-FILTER ALARM -AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2022-07-12 10:44 | 2022-07-12 11:44 | 2022-07-13 11:44 | 24 | 2022-07-12 10:50 | 2022-07-12 13:30 | 160 | 149 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11029809 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM TG-07-02 |  | FM008 |  | 2022-09-17 19:16 | 2022-09-17 20:16 | 2022-09-18 20:16 | 24 | 2022-09-17 19:25 | 2022-09-17 20:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 87807 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11117243 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER ALARM AHU-A1110-004 |  | FM008 |  | 2022-10-21 11:08 | 2022-10-21 12:08 | 2022-10-22 12:08 | 24 | 2022-10-21 11:18 | 2022-10-21 17:30 | 372 | 187 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11177350 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-11-09 21:16 | 2022-11-09 22:16 | 2022-11-10 22:16 | 24 | 2022-11-09 21:20 | 2022-11-09 22:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11523118 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 FILTER DIRTY |  | FM008 |  | 2023-03-06 08:54 | 2023-03-06 09:54 | 2023-03-07 09:54 | 24 | 2023-03-06 09:00 | 2023-03-06 11:50 | 170 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11587491 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | BELT DAMAGED -AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-03-22 21:09 | 2023-03-22 22:09 | 2023-03-23 22:09 | 24 | 2023-03-22 21:19 | 2023-03-22 23:00 | 101 | 202 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11995169 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP1 / |  | FM008 |  | 2023-07-19 13:26 | 2023-07-19 14:26 | 2023-07-20 14:26 | 24 | 2023-07-19 13:35 | 2023-07-19 15:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95216 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12012119 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP1 / |  | FM008 |  | 2023-07-25 02:16 | 2023-07-25 03:16 | 2023-07-26 03:16 | 24 | 2023-07-25 02:25 | 2023-07-25 05:30 | 185 | 215 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12016538 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | WEE BELT DAMAGED - AHU-A1110-004 –TG-07A-02 |  | FM008 |  | 2023-07-29 07:29 | 2023-07-29 08:29 | 2023-07-30 08:29 | 24 | 2023-07-29 07:35 | 2023-07-29 09:55 | 140 | 420 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12097407 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-08-19 20:30 | 2023-08-19 21:30 | 2023-08-20 21:30 | 24 | 2023-08-19 20:40 | 2023-08-19 23:40 | 180 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12114232 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | WEE BELT DAMAGED - AHU-A1110-004 – TG-07-02 - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2023-08-26 00:32 | 2023-08-26 01:32 | 2023-08-27 01:32 | 24 | 2023-08-26 00:40 | 2023-08-26 02:00 | 80 | 240 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12199089 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1110-004 - MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP1 / |  | FM008 |  | 2023-09-19 03:06 | 2023-09-19 04:06 | 2023-09-20 04:06 | 24 | 2023-09-19 03:10 | 2023-09-19 17:55 | 885 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12278162 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-10-10 22:20 | 2023-10-10 23:20 | 2023-10-11 23:20 | 24 | 2023-10-10 22:25 | 2023-10-11 01:30 | 185 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2022-10919212 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004- DP3 FILTER ALARM |  | FM008 |  | 2022-08-09 08:22 | 2022-08-09 09:22 | 2022-08-10 09:22 | 24 | 2022-08-09 08:32 | 2022-08-09 09:20 | 48 | 144 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10953919 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU FILTER ALARM |  | FM008 |  | 2022-08-16 21:02 | 2022-08-16 22:02 | 2022-08-17 22:02 | 24 | 2022-08-16 21:10 | 2022-08-16 23:55 | 165 | 248 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11207163 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004- DUCT INSULATION DAMAGED-TG-07-04-- |  | FM008 |  | 2022-11-20 14:10 | 2022-11-20 15:10 | 2022-11-21 15:10 | 24 | 2022-11-20 14:15 | 2022-11-20 17:00 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 87807 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2023-11332933 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER ALARM -:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-01-01 22:56 | 2023-01-01 23:56 | 2023-01-02 23:56 | 24 | 2023-01-01 23:00 | 2023-01-02 01:30 | 150 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11587141 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER DIRTY - ( AHU-A1110-004) -TG 09 19 |  | FM008 |  | 2023-03-23 00:27 | 2023-03-23 01:27 | 2023-03-24 01:27 | 24 | 2023-03-23 00:35 | 2023-03-23 05:40 | 305 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11684318 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 FILTER ALARM NEAR TX01002 |  | FM008 |  | 2023-04-19 01:47 | 2023-04-19 02:47 | 2023-04-20 02:47 | 24 | 2023-04-19 01:50 | 2023-04-19 04:00 | 130 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-11763722 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS;PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP1 /-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-05-05 12:42 | 2023-05-05 13:42 | 2023-05-06 13:42 | 24 | 2023-05-05 12:50 | 2023-05-05 20:59 | 489 | 243 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11834251 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-05-29 01:39 | 2023-05-29 02:39 | 2023-05-30 02:39 | 24 | 2023-05-29 01:46 | 2023-05-29 08:30 | 404 | 190 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 68485 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - | On-Hold-Access.ASSET CURRENTLY IN USE/OPERATION | BMS
| CM-2023-11901910 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER DIRTY /V BELT DAMAGED -TG-07-02 |  | FM008 |  | 2023-06-22 09:27 | 2023-06-22 10:27 | 2023-06-23 10:27 | 24 | 2023-06-22 09:35 | 2023-06-22 13:00 | 205 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 17573 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2023-12043614 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1110-004 GROUND FLOOR AREA 007 |  | FM008 |  | 2023-08-05 08:22 | 2023-08-05 09:22 | 2023-08-06 09:22 | 24 | 2023-08-05 08:30 | 2023-08-05 16:00 | 450 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | AIRFLOW VALUE MISMATCH | RECTIFIED | 89127 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - | APPROVAL TO ACCESS PENDING BY BHS | E-mail
| CM-2023-12069545 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -GROUND FLOOR AREA 007 |  | FM008 |  | 2023-08-12 23:28 | 2023-08-13 00:28 | 2023-08-14 00:28 | 24 | 2023-08-12 23:35 | 2023-08-13 01:30 | 115 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12114448 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FCU NOT WORKING (FCU-A7211-C4B-L0-006) - TG-07-19 |  | FM008 |  | 2023-08-23 20:15 | 2023-08-23 21:15 | 2023-08-24 21:15 | 24 | 2023-08-23 20:20 | 2023-08-23 21:35 | 75 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 121959 | 17053 |  |  | 123812 | Kannan, Mr. Prakash | N - - - |  | Voice Communication
| CM-2023-12148575 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AC NOT WORKING -BAGGAGE HALL |  | FM008 |  | 2023-09-03 18:19 | 2023-09-03 19:19 | 2023-09-04 19:19 | 24 | 2023-09-03 18:25 | 2023-09-03 23:55 | 330 | 40 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 87807 |  |  | 99335 | Mohammed, Mr. Zuhebuddin | N - - - |  | Voice Communication
| CM-2023-12148645 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-004 – TG 09 19 |  | FM008 |  | 2023-09-04 07:13 | 2023-09-04 08:13 | 2023-09-05 08:13 | 24 | 2023-09-04 07:20 | 2023-09-04 08:50 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12342347 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 FILTE DIRTY TG-07-02 |  | FM008 |  | 2023-11-01 13:32 | 2023-11-01 14:32 | 2023-11-02 14:32 | 24 | 2023-11-01 13:40 | 2023-11-01 16:15 | 155 | 145 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2022-10988381 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER ALARM - AHU-A1110-004 - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-09-01 02:32 | 2022-09-01 03:32 | 2022-09-02 03:32 | 24 | 2022-09-01 02:40 | 2022-09-01 03:40 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11144185 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM AC VENT-TG-07-02 |  | FM008 |  | 2022-10-27 22:36 | 2022-10-27 23:36 | 2022-10-28 23:36 | 24 | 2022-10-27 22:45 | 2022-10-28 01:45 | 180 | 205 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 95217 | 87807 |  |  | 117472 | Parappalil Baby, Mr. Eldhose | N - - - |  | Voice Communication
| CM-2022-11230810 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – AHU-A1110-004 - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-12-01 03:14 | 2022-12-01 04:14 | 2022-12-02 04:14 | 24 | 2022-12-01 03:20 | 2022-12-01 04:20 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11700811 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-04-27 00:40 | 2023-04-27 01:40 | 2023-04-28 01:40 | 24 | 2023-04-27 00:46 | 2023-04-27 05:30 | 284 | 217 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17053 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11801884 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-05-18 14:32 | 2023-05-18 15:32 | 2023-05-19 15:32 | 24 | 2023-05-18 14:37 | 2023-05-18 22:10 | 453 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | 10302 | Thomas J K | N - - - |  | Voice Communication
| CM-2023-11878605 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-004 - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2023-06-13 10:01 | 2023-06-13 11:01 | 2023-06-14 11:01 | 24 | 2023-06-13 10:05 | 2023-06-13 15:35 | 330 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11941170 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-ASD-MTB-GFL007-AHU003 AHU-A1110-004 AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSA |  | FM008 |  | 2023-07-03 13:51 | 2023-07-03 14:51 | 2023-07-04 14:51 | 24 | 2023-07-03 14:00 | 2023-07-03 21:05 | 425 | 188 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-11971351 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 FILTER IS DIRTY |  | FM008 |  | 2023-07-10 18:59 | 2023-07-10 19:59 | 2023-07-11 19:59 | 24 | 2023-07-10 19:05 | 2023-07-10 23:10 | 245 | 97 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12209744 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | V-BELT DAMAGED |  | FM008 |  | 2023-09-22 09:46 | 2023-09-22 10:46 | 2023-09-23 10:46 | 24 | 2023-09-22 09:50 | 2023-09-22 11:00 | 70 | 140 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12365670 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-11-08 10:26 | 2023-11-08 11:26 | 2023-11-09 11:26 | 24 | 2023-11-08 10:35 | 2023-11-08 12:45 | 130 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10081414 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED – TG-07-04 |  | FM008 |  | 2022-01-27 00:09 | 2022-01-27 01:09 | 2022-01-28 01:09 | 24 | 2022-01-27 00:15 | 2022-01-27 01:30 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10080445 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM - BHS G/FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-01-27 00:42 | 2022-01-27 01:42 | 2022-01-28 01:42 | 24 | 2022-01-27 00:50 | 2022-01-27 02:45 | 115 | 155 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 55709 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10225313 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS AHU-A1110-004 |  | FM008 |  | 2022-03-08 13:36 | 2022-03-08 14:36 | 2022-03-09 14:36 | 24 | 2022-03-08 13:46 | 2022-03-08 14:30 | 44 | 88 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10122924 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | FILTER IS DIRTY - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-02-10 11:23 | 2022-02-10 12:23 | 2022-02-11 12:23 | 24 | 2022-02-10 11:30 | 2022-02-10 12:30 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | E-mail
| CM-2022-10777498 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-06-25 21:32 | 2022-06-25 22:32 | 2022-06-26 22:32 | 24 | 2022-06-25 21:40 | 2022-06-26 01:25 | 225 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11063060 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | V BELT DAMAGED-AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2022-09-30 08:34 | 2022-09-30 09:34 | 2022-10-01 09:34 | 24 | 2022-09-30 08:40 | 2022-09-30 09:45 | 65 | 130 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 95217 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2022-11097834 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS- AHU-A1110-004-AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007-PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP1 / |  | FM008 |  | 2022-10-12 23:34 | 2022-10-13 00:34 | 2022-10-14 00:34 | 24 | 2022-10-12 23:40 | 2022-10-13 03:05 | 205 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 95217 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10044224 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM;EAST BHS G/FLOOR NEAR BELT TRANSFER TX-01-002 |  | FM008 |  | 2022-01-11 12:56 | 2022-01-11 13:56 | 2022-01-12 13:56 | 24 | 2022-01-11 13:05 | 2022-01-12 02:00 | 775 | 127 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2022-10158970 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU003 DP3 FILTER ALARM – BHS GROUND GLOOR |  | FM008 |  | 2022-02-22 10:58 | 2022-02-22 11:58 | 2022-02-23 11:58 | 24 | 2022-02-22 11:08 | 2022-02-22 12:15 | 67 | 134 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 106976 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10282781 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 DP3 FILTER ALARM |  | FM008 |  | 2022-03-27 07:26 | 2022-03-27 08:26 | 2022-03-28 08:26 | 24 | 2022-03-27 07:30 | 2022-03-27 09:00 | 90 | 270 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10612140 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -EST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-05-05 09:56 | 2022-05-05 10:56 | 2022-05-06 10:56 | 24 | 2022-05-05 10:06 | 2022-05-05 15:30 | 324 | 134 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | NOT WORKING | FILTER DRIER OBSTRUCTED | CLEARED THE OBSTRUCTION | 106914 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-10661366 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 DP3 FILTER ALARM BHS EAST NEAR BELT TX01-002 |  | FM008 |  | 2022-05-14 08:52 | 2022-05-14 09:52 | 2022-05-15 09:52 | 24 | 2022-05-14 09:00 | 2022-05-14 10:10 | 70 | 210 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 89127 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10675676 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 DUST FILTER ALARM STATUS -FILTERS 756-AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2022-05-19 15:19 | 2022-05-19 16:19 | 2022-05-20 16:19 | 24 | 2022-05-19 15:25 | 2022-05-19 18:05 | 160 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10913537 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ASD-MTB-GFL007-AHU003-FIL756 FILTERS 756-AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP3 / |  | FM008 |  | 2022-08-04 03:18 | 2022-08-04 04:18 | 2022-08-05 04:18 | 24 | 2022-08-04 03:25 | 2022-08-04 12:00 | 515 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94953 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2023-11624739 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | AHU-A1110-004 FILTER DIRTY |  | FM008 |  | 2023-04-07 07:21 | 2023-04-07 08:21 | 2023-04-08 08:21 | 24 | 2023-04-07 07:30 | 2023-04-07 08:30 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 87807 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12155194 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM THE AC - TG 09 34A |  | FM008 |  | 2023-09-06 21:38 | 2023-09-06 22:38 | 2023-09-07 22:38 | 24 | 2023-09-06 21:45 | 2023-09-07 02:08 | 263 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 132112 | 17053 |  |  | 132351 | Masud, Mr. Abdullah Al | N - - - |  | Voice Communication
| CM-2023-12179290 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU004.SYSALM.DP1 / |  | FM008 |  | 2023-09-11 08:24 | 2023-09-11 09:24 | 2023-09-12 09:24 | 24 | 2023-09-11 08:33 | 2023-09-11 10:05 | 92 | 276 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12231183 | ASD-MTB-GFL007-AHU003 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AIR HANDLING UNIT 003 (TAG NO:AHU-A1110-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 007 |  | FM008 |  | 2023-09-27 14:29 | 2023-09-27 15:29 | 2023-09-28 15:29 | 24 | 2023-09-27 14:35 | 2023-09-27 22:35 | 480 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 007 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 119320 | 87807 |  |  | FM10302 | Thomas J K | Y - - - |  | BMS
| CM-2022-10791776 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1110-008 - TG-09-19 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP5.MTB0901.AHU008.SYSALM.DP1 / (CONSTRUCTION AREA- UNDER MTTJV) |  | FM008 |  | 2022-06-29 06:50 | 2022-06-29 07:50 | 2022-06-30 07:50 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING |  |  | 106973 | 87807 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - | ASSET NOT IN SCOPE | BMS
| CM-2022-11077345 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM DUCT -TRANSFER -B EXIT GATE OPP TO T0-09A-14 |  | FM008 |  | 2022-10-04 05:08 | 2022-10-04 05:38 | 2022-10-04 09:38 | 4 | 2022-10-04 05:18 | 2022-10-04 08:40 | 202 | 65 | 3 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 009 | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 124475 | 55709 |  |  | 114502 | Khan, Mr. Mohammadshahjad Mohammadsiraj | N - - - |  | Voice Communication
| CM-2023-11930934 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1110-008 – TG 07 02 |  | FM008 |  | 2023-06-26 18:59 | 2023-06-26 19:59 | 2023-06-27 19:59 | 24 | 2023-06-26 19:06 | 2023-06-26 22:15 | 189 | 186 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11973250 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM AHU-A1110-008 |  | FM008 |  | 2023-07-13 08:37 | 2023-07-13 09:37 | 2023-07-14 09:37 | 24 | 2023-07-13 08:45 | 2023-07-13 11:10 | 145 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-11974027 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | OUTSIDE THIS ROOM TG-06-14 - AC TOO HOT |  | FM008 |  | 2023-07-13 14:43 | 2023-07-13 15:43 | 2023-07-14 15:43 | 24 | 2023-07-13 14:50 | 2023-07-13 18:35 | 225 | 50 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 87807 |  |  | CT11536 | VIGNESH | N - - - |  | Voice Communication
| CM-2023-12245109 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – BHS G/FLOOR |  | FM008 |  | 2023-10-02 06:54 | 2023-10-02 07:54 | 2023-10-03 07:54 | 24 | 2023-10-02 07:00 | 2023-10-02 08:15 | 75 | 150 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | BMS
| CM-2023-11935544 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - TG-09-19 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP5.MTB0901.AHU008.SYSALM.DP1 / |  | FM008 |  | 2023-07-02 01:31 | 2023-07-02 02:31 | 2023-07-03 02:31 | 24 | 2023-07-02 01:40 | 2023-07-02 06:00 | 260 | 275 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17573 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-11145590 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | NEAR T0-09A-14 – LEAKAGE FROM THE AC |  | FM008 |  | 2022-10-28 17:22 | 2022-10-28 18:22 | 2022-10-29 18:22 | 24 | 2022-10-28 17:30 | 2022-10-28 20:15 | 165 | 126 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 105233 | 87807 |  |  | 117472 | Parappalil Baby, Mr. Eldhose | N - - - |  | Voice Communication
| CM-2023-12132262 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED AHU-A1110-008 |  | FM008 |  | 2023-08-30 13:18 | 2023-08-30 14:18 | 2023-08-31 14:18 | 24 | 2023-08-30 13:25 | 2023-08-30 17:40 | 255 | 457 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12773122 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-TG-09-19 |  | FM008 |  | 2024-03-28 11:41 | 2024-03-28 12:41 | 2024-03-29 12:41 | 24 | 2024-03-28 11:50 | 2024-03-28 13:20 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2024-12849877 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -TG-09-19 |  | FM008 |  | 2024-04-24 14:17 | 2024-04-24 15:17 | 2024-04-25 15:17 | 24 | 2024-04-24 14:23 | 2024-04-24 22:34 | 491 | 187 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING | FILTER BLOCKED | CLEAN/REPLACE | 106914 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12464260 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | V BELT DAMAGED - AHU-A1110-008 – TG-09-19 |  | FM008 |  | 2023-12-10 22:16 | 2023-12-10 23:16 | 2023-12-11 23:16 | 24 | 2023-12-10 22:25 | 2023-12-10 23:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12277587 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | AHU-A1110-008 WATER LEAKAGE FROM AHU |  | FM008 |  | 2023-10-11 18:31 | 2023-10-11 19:31 | 2023-10-12 19:31 | 24 | 2023-10-11 18:40 | 2023-10-12 01:02 | 382 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 68485 | 87807 |  |  | 130776 | Ramasekar, Mr. Jaya Sakthivel | N - - - |  | Voice Communication
| CM-2024-12727859 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | WATER LEAKING FROM THE CEILING T0-09A-14 |  | FM008 |  | 2024-03-15 01:05 | 2024-03-15 02:05 | 2024-03-16 02:05 | 24 | 2024-03-15 01:10 | 2024-03-15 05:30 | 260 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68060 | 87807 |  |  | 99304 | Anjum, Mr. Muhammad Qaiser | N - - - |  | Voice Communication
| CM-2024-12821636 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - TG-09-19 |  | FM008 |  | 2024-04-11 00:30 | 2024-04-11 01:30 | 2024-04-12 01:30 | 24 | 2024-04-11 00:40 | 2024-04-11 03:20 | 160 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10118589 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP 1 FILTER ALARM |  | FM008 |  | 2022-02-06 20:32 | 2022-02-06 21:32 | 2022-02-07 21:32 | 24 | 2022-02-06 20:41 | 2022-02-06 23:55 | 194 | 250 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11117609 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | CONCOURSE B - TRANSFER AREA T0-09A-14 -WATER LEAKAGE FROM AC DUCT |  | FM008 |  | 2022-10-21 22:33 | 2022-10-21 23:33 | 2022-10-22 23:33 | 24 | 2022-10-21 22:41 | 2022-10-22 02:00 | 199 | 189 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 17053 |  |  | 114502 | Khan, Mr. Mohammadshahjad Mohammadsiraj | N - - - |  | Voice Communication
| CM-2022-11155869 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM AHU TG-07-19 AHU-A1110-008 |  | FM008 |  | 2022-10-31 14:44 | 2022-10-31 15:44 | 2022-11-01 15:44 | 24 | 2022-10-31 14:55 | 2022-10-31 17:10 | 135 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106972 | 17053 |  |  | CO8001 | DARWIN | N - - - |  | Voice Communication
| CM-2022-9964128 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | AHU-A1110-008-DP1 FILTER ALARM |  | FM008 |  | 2022-01-02 12:57 | 2022-01-02 13:57 | 2022-01-03 13:57 | 24 | 2022-01-02 13:05 | 2022-01-02 15:00 | 115 | 235 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95217 | 55709 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10074541 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | Ahu-A1110-008 DP1 FILTER ALARM |  | FM008 |  | 2022-01-24 07:56 | 2022-01-24 08:56 | 2022-01-25 08:56 | 24 | 2022-01-24 08:05 | 2022-01-24 09:15 | 70 | 140 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10399767 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS |  | FM008 |  | 2022-04-17 11:38 | 2022-04-17 12:38 | 2022-04-18 12:38 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING |  |  | 68060 | 17333 |  |  | FM0459 | Manhandavida, Mr. Shaheel | N - - - | ASSET NOT IN SCOPE/UNDER MTTJV SCOPE | BMS
| CM-2023-11933334 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | BELT DAMAGED - TG-09-04 |  | FM008 |  | 2023-06-27 18:56 | 2023-06-27 19:56 | 2023-06-28 19:56 | 24 | 2023-06-27 19:02 | 2023-06-27 20:32 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12278219 | ASD-MTB-GFL009-AHU007 | AIR HANDLING UNIT-05 | AHU BEARING NOISY – AHU-A1110-008 – TG-09-19 |  | FM008 |  | 2023-10-11 08:32 | 2023-10-11 09:32 | 2023-10-12 09:32 | 24 | 2023-10-11 08:40 | 2023-10-11 11:40 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 133396 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12324233 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2023-10-28 00:19 | 2023-10-28 01:19 | 2023-10-29 01:19 | 24 | 2023-10-28 00:25 | 2023-10-28 05:55 | 330 | 190 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12346451 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-010 – TG-09-19 |  | FM008 |  | 2023-11-04 11:04 | 2023-11-04 12:04 | 2023-11-05 12:04 | 24 | 2023-11-04 11:10 | 2023-11-04 17:10 | 360 | 155 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-12377907 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM - (AHU-A1110-010) - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP5.MTB0901.AHU010.SYSALM.DP1 / |  | FM008 |  | 2023-11-14 02:50 | 2023-11-14 03:50 | 2023-11-15 03:50 | 24 | 2023-11-14 02:55 | 2023-11-14 05:50 | 175 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 133396 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | Y - - - |  | BMS
| CM-2022-11216848 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – TG-09-19 |  | FM008 |  | 2022-11-25 10:56 | 2022-11-25 11:56 | 2022-11-26 11:56 | 24 | 2022-11-25 11:05 | 2022-11-25 12:30 | 85 | 255 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2023-12056944 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | AC TOO WARM - ALL BHS AREA |  | FM008 |  | 2023-08-06 19:38 | 2023-08-06 20:38 | 2023-08-07 20:38 | 24 | 2023-08-06 19:45 | 2023-08-06 21:05 | 80 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 95216 | 17053 |  |  | 115788 | Sudheer, Mr. Sreeraj | N - - - |  | Voice Communication
| CM-2023-12346852 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | BLOWER PAINT FADED - AHU-A1110-010 – TG-09-19 |  | FM008 |  | 2023-11-04 07:07 | 2023-11-04 08:07 | 2023-11-05 08:07 | 24 | 2023-11-04 07:15 | 2023-11-04 09:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 133396 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12422003 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM - (AHU-A1110-010) -PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP5.MTB0901.AHU010.SYSALM.DP1 |  | FM008 |  | 2023-11-27 07:57 | 2023-11-27 08:57 | 2023-11-28 08:57 | 24 | 2023-11-27 08:05 | 2023-11-27 09:05 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | Y - - - |  | BMS
| CM-2023-12132264 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED AHU-A1110-010 |  | FM008 |  | 2023-08-30 13:20 | 2023-08-30 14:20 | 2023-08-31 14:20 | 24 | 2023-08-30 13:27 | 2023-08-30 17:45 | 258 | 368 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106972 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12279293 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP5.MTB0901.AHU010.SYSALM.DP1 / /EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2023-10-13 03:09 | 2023-10-13 04:09 | 2023-10-14 04:09 | 24 | 2023-10-13 03:15 | 2023-10-13 17:20 | 845 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | Y - - - | ASSET CURRENTLY IN USE/OPERATION (AREA BUSY) | BMS
| CM-2023-12298269 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 009-BARING NOISY --MAIN TERMINAL BUILDING-GROUND FLOOR AREA 009 |  | FM008 |  | 2023-10-19 11:11 | 2023-10-19 12:11 | 2023-10-20 12:11 | 24 | 2023-10-19 11:15 | 2023-10-19 14:15 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 77406 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-12458108 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM,AHU-A1110-010,EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2023-12-10 09:46 | 2023-12-10 10:46 | 2023-12-11 10:46 | 24 | 2023-12-10 09:55 | 2023-12-10 13:40 | 225 | 185 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | BMS
| CM-2024-12533756 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS ALARM - EAST BHS GROUND FLOOR NEAR BELT TX01-002 - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP5.MTB0901.AHU010.SYSALM.DP1 / |  | FM008 |  | 2024-01-02 10:35 | 2024-01-02 11:35 | 2024-01-03 11:35 | 24 | 2024-01-02 10:45 | 2024-01-02 13:05 | 140 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 119320 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2023-12166594 | ASD-MTB-GFL009-AHU009 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS (AHU-A1110-010) NEAR BELT TX01-002 |  | FM008 |  | 2023-09-10 04:24 | 2023-09-10 05:24 | 2023-09-11 05:24 | 24 | 2023-09-10 04:35 | 2023-09-10 06:50 | 135 | 245 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 009 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-11037674 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | AHU-A1110-052 – AHU INSIDE LAMP IS NOT ILUINATING |  | FM008 |  | 2022-09-21 00:39 | 2022-09-21 01:39 | 2022-09-22 01:39 | 24 | 2022-09-21 00:48 | 2022-09-21 03:49 | 181 | 188 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-11557720 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2023-03-13 00:27 | 2023-03-13 01:27 | 2023-03-14 01:27 | 24 | 2023-03-13 00:35 | 2023-03-13 03:45 | 190 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2024-12558015 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | DP FILTER DIRTY - AHU-A1110-051 – TG-12-40 |  | FM008 |  | 2024-01-14 09:13 | 2024-01-14 10:13 | 2024-01-15 10:13 | 24 | 2024-01-14 09:20 | 2024-01-14 12:40 | 200 | 71 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | BMS
| CM-2024-12731068 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT ILLUMINATING - AHU-A1110-052 - MECHANICAL ROOM TG-12-40 |  | FM008 |  | 2024-03-13 19:15 | 2024-03-13 20:15 | 2024-03-14 20:15 | 24 | 2024-03-13 19:20 | 2024-03-13 23:59 | 279 | 353 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 17573 | 87807 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2023-12274393 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | BEARING NOISY - AHU-A1110-052 – TG-12-40 |  | FM008 |  | 2023-10-12 08:28 | 2023-10-12 09:28 | 2023-10-13 09:28 | 24 | 2023-10-12 08:35 | 2023-10-12 11:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 106973 | 87807 |  |  | FM9671 | KASUN LAKMAL KM, Mr. | N - - - |  | Voice Communication
| CM-2022-10154366 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | ARRIVALS CUSTOMS BAG SCANNING/NEAR BELT 5 – GROUND FLOOR – AREA TOO HOT/AC NOT COOLING |  | FM008 |  | 2022-02-20 17:29 | 2022-02-20 18:29 | 2022-02-21 18:29 | 24 | 2022-02-20 17:35 | 2022-02-20 18:20 | 45 | 45 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 106976 | 55709 |  |  | 12766 | Shrestha, Mr. Kamal | N - - - |  | Voice Communication
| CM-2022-11289098 | ASD-MTB-GFL012-AHU011 | AIR HANDLING UNIT-05 | MARINE LAMP NOT WORKING |  | FM008 |  | 2022-12-19 10:43 | 2022-12-19 11:43 | 2022-12-20 11:43 | 24 | 2022-12-19 10:53 | 2022-12-19 12:51 | 118 | 236 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 012 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 121959 | 55709 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2022-10207954 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1110-053 - AG-13-36 |  | FM008 |  | 2022-02-28 19:15 | 2022-02-28 20:15 | 2022-03-01 20:15 | 24 | 2022-02-28 19:20 | 2022-02-28 22:00 | 160 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-11159850 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-11-05 07:22 | 2022-11-05 08:22 | 2022-11-06 08:22 | 24 | 2022-11-05 07:30 | 2022-11-05 09:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10953069 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-08-17 20:05 | 2022-08-17 21:05 | 2022-08-18 21:05 | 24 | 2022-08-17 20:10 | 2022-08-17 23:20 | 190 | 380 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11216382 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING |  | FM008 |  | 2022-11-23 13:40 | 2022-11-23 14:40 | 2022-11-24 14:40 | 24 | 2022-11-23 13:45 | 2022-11-23 15:10 | 85 | 170 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11345299 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-053 – TG-13-36 |  | FM008 |  | 2023-01-04 12:45 | 2023-01-04 13:45 | 2023-01-05 13:45 | 24 | 2023-01-04 12:50 | 2023-01-04 14:30 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-11559451 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1110-053 , TG-13-36 |  | FM008 |  | 2023-03-14 00:09 | 2023-03-14 01:09 | 2023-03-15 01:09 | 24 | 2023-03-14 00:15 | 2023-03-14 02:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2023-12097009 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1110-053 – TG-13-36 |  | FM008 |  | 2023-08-18 19:14 | 2023-08-18 20:14 | 2023-08-19 20:14 | 24 | 2023-08-18 19:20 | 2023-08-18 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12097395 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -BG-13-36 |  | FM008 |  | 2023-08-19 19:05 | 2023-08-19 20:05 | 2023-08-20 20:05 | 24 | 2023-08-19 19:10 | 2023-08-19 20:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12099055 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | CABIN LAMP FAULTY TG-13-36 |  | FM008 |  | 2023-08-19 21:20 | 2023-08-19 22:21 | 2023-08-20 22:21 | 24 | 2023-08-19 21:30 | 2023-08-19 21:50 | 20 | 40 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM1141 | Alam Robel, Mr. Kawsar | N - - - |  | Voice Communication
| CM-2023-12114428 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU-A1110-053 AHU CABIN LAMP FAULTY TG-25-19 |  | FM008 |  | 2023-08-23 19:10 | 2023-08-23 20:10 | 2023-08-24 20:10 | 24 | 2023-08-23 19:15 | 2023-08-23 22:40 | 205 | 135 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68485 | 17053 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2023-12410637 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2023-11-25 13:03 | 2023-11-25 14:03 | 2023-11-26 14:03 | 24 | 2023-11-25 13:10 | 2023-11-25 15:40 | 150 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 121959 | 17053 |  |  | FM12241 | SAMEER SATHIK ALI, Mr. | N - - - |  | Voice Communication
| CM-2022-10872857 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | AHU-A1110-053 – DP1 FILTER DIRTY |  | FM008 |  | 2022-07-25 20:24 | 2022-07-25 21:24 | 2022-07-26 21:24 | 24 | 2022-07-25 20:34 | 2022-07-25 22:34 | 120 | 120 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 94953 | 87807 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-10956411 | ASD-MTB-GFL013-AHU012 | AIR HANDLING UNIT-05 | STRAINER BLOCKED-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA AIR HANDLING UNIT-05 |  | FM008 |  | 2022-08-20 00:06 | 2022-08-20 01:06 | 2022-08-21 01:06 | 24 | 2022-08-20 00:13 | 2022-08-20 02:13 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 013 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106914 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10612732 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | NEAR TG-ST2 - AC TOO COLD - STAFF EXIT ARRIVAL -NEAR BELT 9 |  | FM008 |  | 2022-04-30 02:12 | 2022-04-30 03:12 | 2022-05-01 03:12 | 24 | 2022-04-30 02:28 | 2022-04-30 04:20 | 112 | 57 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 87807 | 17053 |  |  | CT13702 | NATHANIEL | N - - - |  | Voice Communication
| CM-2022-10771842 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - AHU-A1110-052 – TG-12-40 |  | FM008 |  | 2022-06-20 13:56 | 2022-06-20 14:56 | 2022-06-21 14:56 | 24 | 2022-06-20 14:05 | 2022-06-20 16:45 | 160 | 155 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-11037673 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | AHU-A1110-051 – AHU INSIDE LAMP IS NOT ILUINATING |  | FM008 |  | 2022-09-21 00:37 | 2022-09-21 01:37 | 2022-09-22 01:37 | 24 | 2022-09-21 00:47 | 2022-09-21 02:16 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12093690 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS-TAG NO:AHU-A1110-051)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 022 -MECHANICAL ROOM TG-22-20 |  | FM008 |  | 2023-08-14 20:20 | 2023-08-14 21:20 | 2023-08-15 21:20 | 24 | 2023-08-14 20:30 | 2023-08-14 23:59 | 209 | 183 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106914 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12202404 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT SWITCH FAULTY - AHU-A1110-051 – TG-22-20 |  | FM008 |  | 2023-09-19 21:50 | 2023-09-19 22:50 | 2023-09-20 22:50 | 24 | 2023-09-19 22:00 | 2023-09-20 00:45 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | NOT WORKING | SUPPLY POWER FAILURE | RESET THE BREAKER | 133396 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-11916555 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | AHU CABIN LIGHTING SWITCH IS DAMAGED |  | FM008 |  | 2023-06-23 10:37 | 2023-06-23 11:37 | 2023-06-24 11:37 | 24 | 2023-06-23 10:40 | 2023-06-23 14:00 | 200 | 239 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12207028 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | FILTER DIRT - AHU-A1110-051 – |  | FM008 |  | 2023-09-23 00:07 | 2023-09-23 01:07 | 2023-09-24 01:07 | 24 | 2023-09-23 00:15 | 2023-09-23 04:15 | 240 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12486612 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FUSED |  | FM008 |  | 2023-12-18 15:08 | 2023-12-18 16:08 | 2023-12-19 16:08 | 24 | 2023-12-18 15:15 | 2023-12-18 18:40 | 205 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68060 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-11582847 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-03-22 10:15 | 2023-03-22 11:15 | 2023-03-23 11:15 | 24 | 2023-03-22 10:24 | 2023-03-22 11:52 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12558013 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | DP FILTER DIRTY - AHU-A1110-051 – TG-22-04 |  | FM008 |  | 2024-01-14 09:12 | 2024-01-14 10:12 | 2024-01-15 10:12 | 24 | 2024-01-14 09:20 | 2024-01-14 12:05 | 165 | 71 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | BMS
| CM-2022-11295510 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | SUPPLY MOTOR FLEXIABLE CONNECTOR DAMAGED AHU-A1110-051 |  | FM008 |  | 2022-12-19 19:06 | 2022-12-19 20:06 | 2022-12-20 20:06 | 24 | 2022-12-19 19:15 | 2022-12-19 22:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | DAMAGED | EXHAUST FAN MOTOR BURNT | REPLACED THE MOTOR | 68485 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12285787 | ASD-MTB-GFL022-AHU010 | AIR HANDLING UNIT-05 | ABNORMAL NOISE FROM BEARING |  | FM008 |  | 2023-10-15 12:43 | 2023-10-15 13:43 | 2023-10-16 13:43 | 24 | 2023-10-15 12:50 | 2023-10-15 15:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 022 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 87807 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2022-10079512 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU-A1110-054 SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-01-26 01:54 | 2022-01-26 02:54 | 2022-01-27 02:54 | 24 | 2022-01-26 02:00 | 2022-01-26 03:40 | 100 | 200 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10207955 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY - AHU-A1110-054 – TG-25-19 |  | FM008 |  | 2022-02-28 19:17 | 2022-02-28 20:17 | 2022-03-01 20:17 | 24 | 2022-02-28 19:25 | 2022-02-28 23:15 | 230 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM2641 | Devabhaktuni, Mr. Narendra | N - - - |  | Voice Communication
| CM-2022-10691946 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU-A1110-054 FILTER DIRTY TG-25-19 |  | FM008 |  | 2022-05-25 19:07 | 2022-05-25 20:07 | 2022-05-26 20:07 | 24 | 2022-05-25 19:15 | 2022-05-25 21:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10954305 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU-A1110-054- STRAINER BLOCKED--- |  | FM008 |  | 2022-08-18 20:29 | 2022-08-18 21:29 | 2022-08-19 21:29 | 24 | 2022-08-18 20:35 | 2022-08-18 22:45 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 94953 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11216607 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING – MEC ROOM TG-25-19 |  | FM008 |  | 2022-11-24 14:12 | 2022-11-24 15:12 | 2022-11-25 15:12 | 24 | 2022-11-24 14:20 | 2022-11-24 15:48 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2024-12555901 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU-A1110-054)-FILTER DIRTY -MAIN TERMINAL BUILDING-GROUND FLOOR AREA 025 |  | FM008 |  | 2024-01-14 09:30 | 2024-01-14 10:30 | 2024-01-15 10:30 | 24 | 2024-01-14 09:40 | 2024-01-14 11:30 | 110 | 65 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 95217 |  |  | FM9912 | Punnakoot, Mr. Pramod Kumar | N - - - |  | Voice Communication
| CM-2023-11841681 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | FILTER DIRTY -TG-25-19 |  | FM008 |  | 2023-06-01 20:44 | 2023-06-01 21:44 | 2023-06-02 21:44 | 24 | 2023-06-01 20:50 | 2023-06-01 22:45 | 115 | 175 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2023-12103095 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY TG-25-19 |  | FM008 |  | 2023-08-20 21:33 | 2023-08-20 22:33 | 2023-08-21 22:33 | 24 | 2023-08-20 21:40 | 2023-08-20 23:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12113156 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU-A1110-054 STRAINER DIRTY -TG-25-19 |  | FM008 |  | 2023-08-22 20:15 | 2023-08-22 21:15 | 2023-08-23 21:15 | 24 | 2023-08-22 20:20 | 2023-08-22 23:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10952940 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-08-17 03:43 | 2022-08-17 04:43 | 2022-08-18 04:43 | 24 | 2022-08-17 03:50 | 2022-08-17 06:45 | 175 | 350 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 55709 |  |  | FM5828 | Gopalakrishnannair, Mr. Jayakrishnan | N - - - |  | Voice Communication
| CM-2023-12109347 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -TG-25-19 |  | FM008 |  | 2023-08-20 20:13 | 2023-08-20 21:13 | 2023-08-21 21:13 | 24 | 2023-08-20 20:20 | 2023-08-20 23:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2022-10709623 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2022-05-30 03:08 | 2022-05-30 04:08 | 2022-05-31 04:08 | 24 | 2022-05-30 03:15 | 2022-05-30 04:45 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | BMS
| CM-2023-11477273 | ASD-MTB-GFL025-AHU013 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM – TG-25-19;MEC ROOM |  | FM008 |  | 2023-02-20 07:14 | 2023-02-20 08:14 | 2023-02-21 08:14 | 24 | 2023-02-20 07:20 | 2023-02-20 11:55 | 275 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 025 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2022-10614641 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM-AHU-A1153-001-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2022-05-03 21:00 | 2022-05-03 22:00 | 2022-05-04 22:00 | 24 | 2022-05-03 21:10 | 2022-05-03 23:40 | 150 | 130 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 17336 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10654402 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY – TG-06A-13 |  | FM008 |  | 2022-05-11 19:39 | 2022-05-11 20:39 | 2022-05-12 20:39 | 24 | 2022-05-11 19:50 | 2022-05-11 22:50 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11061273 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | FILTER DIRTY -CM-2022-04-2002 |  | FM008 |  | 2022-09-25 22:01 | 2022-09-25 23:01 | 2022-09-26 23:01 | 24 | 2022-09-25 22:05 | 2022-09-25 23:58 | 113 | 179 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 76858 | 87807 |  |  | FM1460 | SANTOSH | - - - |  | Voice Communication
| CM-2023-11568668 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001 DP1 FILTER ALARM – TG-06A-13 |  | FM008 |  | 2023-03-17 13:20 | 2023-03-17 14:20 | 2023-03-18 14:20 | 24 | 2023-03-17 13:30 | 2023-03-17 17:10 | 220 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 95217 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2023-11779990 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2023-05-11 21:39 | 2023-05-11 22:39 | 2023-05-12 22:39 | 24 | 2023-05-11 21:45 | 2023-05-11 23:20 | 95 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | AHU TRIP ALARM | RESET UNIT | 121959 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-10877581 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001- FILTER DIRTY |  | FM008 |  | 2022-07-28 13:22 | 2022-07-28 14:22 | 2022-07-29 14:22 | 24 | 2022-07-28 13:30 | 2022-07-28 16:50 | 200 | 85 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11113807 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | FILTER DIRTY-AHU-A1153-001)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06 |  | FM008 |  | 2022-10-20 09:45 | 2022-10-20 10:45 | 2022-10-21 10:45 | 24 | 2022-10-20 09:52 | 2022-10-20 14:30 | 278 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-11363116 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -AHU-A1153-001)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-01-10 19:31 | 2023-01-10 20:31 | 2023-01-11 20:31 | 24 | 2023-01-10 19:35 | 2023-01-10 23:55 | 260 | 695 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11883297 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS ALARM AHU-A1153-001 GROUND FLOOR AREA 06A |  | FM008 |  | 2023-06-13 21:17 | 2023-06-13 22:17 | 2023-06-14 22:17 | 24 | 2023-06-13 21:25 | 2023-06-13 23:30 | 125 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 89127 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12187603 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -TAG NO:AHU-A1153-001)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-09-16 01:04 | 2023-09-16 02:04 | 2023-09-17 02:04 | 24 | 2023-09-16 01:10 | 2023-09-16 04:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2022-11113239 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING,-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2022-10-17 20:04 | 2022-10-17 21:04 | 2022-10-18 21:04 | 24 | 2022-10-17 20:14 | 2022-10-17 21:45 | 91 | 182 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 77406 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11471087 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | PAINT FADED CHILLER WATER LINE - AHU-A1153-001- AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-02-18 20:03 | 2023-02-18 21:03 | 2023-02-19 21:03 | 24 | 2023-02-18 20:10 | 2023-02-18 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 132112 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11480149 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE - AHU-A1153-001 – TG-06A-13 |  | FM008 |  | 2023-02-24 19:14 | 2023-02-24 20:14 | 2023-02-25 20:14 | 24 | 2023-02-24 19:20 | 2023-02-24 22:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 106973 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11827173 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-CABIN LAMP FAULTY --MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-05-28 13:12 | 2023-05-28 14:12 | 2023-05-29 14:12 | 24 | 2023-05-28 13:20 | 2023-05-28 15:38 | 138 | 241 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2024-12633245 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU CAIBIN LIGHT NOT WORKING - TG-06A-13 MECHANICAL ROOM |  | FM008 |  | 2024-02-07 19:20 | 2024-02-07 20:20 | 2024-02-08 20:20 | 24 | 2024-02-07 19:30 | 2024-02-07 22:15 | 165 | 330 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17053 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12363371 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001 CHILLED WATER LINE PAINT FADED – TG-06A-13 |  | FM008 |  | 2023-11-07 12:34 | 2023-11-07 13:34 | 2023-11-08 13:34 | 24 | 2023-11-07 12:40 | 2023-11-07 15:30 | 170 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12423205 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | ABNORMAL SOUND FROM AHU AHU-A1153-001 |  | FM008 |  | 2023-11-28 08:56 | 2023-11-28 09:56 | 2023-11-29 09:56 | 24 | 2023-11-28 09:05 | 2023-11-28 18:00 | 535 | 620 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10214673 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001 - CHILLED WATER LINE PAINT FADED TG-06A-13 |  | FM008 |  | 2022-03-05 19:11 | 2022-03-05 20:11 | 2022-03-06 20:11 | 24 | 2022-03-05 19:20 | 2022-03-05 21:50 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17053 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10063189 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001 – COIL IS DIRTY – TG-06A-13 |  | FM008 |  | 2022-01-19 00:06 | 2022-01-19 01:06 | 2022-01-20 01:06 | 24 | 2022-01-19 00:15 | 2022-01-19 03:00 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94954 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10214731 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU FILTER BLOCK |  | FM008 |  | 2022-03-06 02:20 | 2022-03-06 03:20 | 2022-03-07 03:20 | 24 | 2022-03-06 02:25 | 2022-03-06 04:55 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 106972 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10085144 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | COOLING COILD DIRTY -AIR HANDLING UNIT 168 (TAG NO:AHU-A1153-001)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2022-01-29 14:47 | 2022-01-29 15:47 | 2022-01-30 15:47 | 24 | 2022-01-29 14:50 | 2022-01-29 18:30 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10699571 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001 – SUPPLY DUCT CANVAS AIR LEAKAGE – TG-06A-13 |  | FM008 |  | 2022-05-28 19:16 | 2022-05-28 20:16 | 2022-05-29 20:16 | 24 | 2022-05-28 19:20 | 2022-05-28 22:20 | 180 | 535 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11950899 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU-A1153-001 – CHILLED WATER LINE PAINT FADED – TG-06A-013 |  | FM008 |  | 2023-07-07 13:20 | 2023-07-07 14:20 | 2023-07-08 14:20 | 24 | 2023-07-07 13:25 | 2023-07-07 16:25 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 94954 | 87807 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2024-12770023 | ASD-MTB-GFL06A-AHU168 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - TG-06A-30 |  | FM008 |  | 2024-03-25 13:24 | 2024-03-25 14:24 | 2024-03-26 14:24 | 24 | 2024-03-25 13:30 | 2024-03-25 17:30 | 240 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17053 | 17053 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2022-10225398 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | NEAR T1-06A-03 WATER LEAKAGE FROM CEILING |  | FM008 |  | 2022-03-09 01:22 | 2022-03-09 02:22 | 2022-03-10 02:22 | 24 | 2022-03-09 01:30 | 2022-03-09 05:30 | 240 | 115 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 17154 | 17053 |  |  | C08732 | KHADGA | N - - - |  | Voice Communication
| CM-2022-10614627 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DP2 FILTER ALARM - AHU-A1153-002 – TG-06A-13 |  | FM008 |  | 2022-05-03 17:38 | 2022-05-03 18:38 | 2022-05-04 18:38 | 24 | 2022-05-03 17:45 | 2022-05-03 23:35 | 350 | 130 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10903647 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU-A1153-002 FILTER ALARM |  | FM008 |  | 2022-08-01 15:00 | 2022-08-01 16:00 | 2022-08-02 16:00 | 24 | 2022-08-01 15:08 | 2022-08-01 18:15 | 187 | 220 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 76858 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11998706 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | FFL1 SEATING AREA AC TOO COLD |  | FM008 |  | 2023-07-23 03:51 | 2023-07-23 04:51 | 2023-07-24 04:51 | 24 | 2023-07-23 03:55 | 2023-07-23 04:50 | 55 | 45 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 89127 | 17053 |  |  | 127062 | Ronoh, Ms. Sarah Chepchumba | N - - - |  | Voice Communication
| CM-2023-12383732 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | UNUSUAL SOUND - AHU-1153-002 – TG-06A-13 |  | FM008 |  | 2023-11-15 08:34 | 2023-11-15 09:35 | 2023-11-16 09:35 | 24 | 2023-11-15 08:40 | 2023-11-15 12:30 | 230 | 455 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106973 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12597394 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC VENT DIRTY - FFL1 CORRIDOR AREA |  | FM008 |  | 2024-01-28 02:14 | 2024-01-28 03:14 | 2024-01-29 03:14 | 24 | 2024-01-28 02:20 | 2024-01-28 05:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11039101 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DP1 FILTER DIRTY |  | FM008 |  | 2022-09-23 00:55 | 2022-09-23 01:55 | 2022-09-24 01:55 | 24 | 2022-09-23 01:00 | 2022-09-23 03:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11176234 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED AHU-A1153-002 |  | FM008 |  | 2022-11-09 02:31 | 2022-11-09 03:31 | 2022-11-10 03:31 | 24 | 2022-11-09 02:40 | 2022-11-09 04:30 | 110 | 330 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11471088 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CHILLER WATER LINE PAINT FADED - AHU-A1153-002 - AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-02-18 20:05 | 2023-02-18 21:05 | 2023-02-19 21:05 | 24 | 2023-02-18 20:10 | 2023-02-18 23:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 132112 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11866891 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DP2 RELIEF FILTER STATUS -GROUND FLOOR AREA 06A |  | FM008 |  | 2023-06-08 19:27 | 2023-06-08 20:27 | 2023-06-09 20:27 | 24 | 2023-06-08 19:35 | 2023-06-08 21:55 | 140 | 105 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12007633 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC TEMPERATURE IS TOO COLD- A1-FFL1-31 |  | FM008 |  | 2023-07-26 07:15 | 2023-07-26 08:15 | 2023-07-27 08:15 | 24 | 2023-07-26 07:20 | 2023-07-26 09:35 | 135 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | COOLING FANS PROBLEM | REPAIR/REPLACE | 106914 | 17053 |  |  | FM7722 | PATRICK | N - - - |  | Voice Communication
| CM-2023-12013933 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-07-27 09:45 | 2023-07-27 10:45 | 2023-07-28 10:45 | 24 | 2023-07-27 09:50 | 2023-07-27 12:35 | 165 | 130 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM8380 | Sahani, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-12112052 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DP 3 FILTER DIRTY AHU-A1153-002 TG-06A-33 |  | FM008 |  | 2023-08-23 14:46 | 2023-08-23 15:46 | 2023-08-24 15:46 | 24 | 2023-08-23 14:55 | 2023-08-23 17:30 | 155 | 465 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-12383636 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | STRONG BURNING SMELL - SN-1000, A1 BOARDING GATE & SN-1047 |  | FM008 |  | 2023-11-14 23:36 | 2023-11-15 00:06 | 2023-11-15 04:06 | 4 | 2023-11-14 23:45 | 2023-11-15 00:45 | 60 | 60 | 1 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 06A | N | BADSMELL | CLOGGED AIR FILTER | CLEANED/REPLACED | 17573 | 87807 |  |  | 106948 | Sitasis, Mr. Dukha | N - - - |  | Voice Communication
| CM-2023-12378178 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU-A1153-002 -BELT DAMAGE --MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-11-15 01:01 | 2023-11-15 02:01 | 2023-11-16 02:01 | 24 | 2023-11-15 01:10 | 2023-11-15 04:30 | 200 | 179 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 87807 |  |  | FM3619 | JOSEPH RAJU, | N - - - |  | Voice Communication
| CM-2023-12512938 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-12-27 21:06 | 2023-12-27 22:06 | 2023-12-28 22:06 | 24 | 2023-12-27 21:15 | 2023-12-27 22:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12629381 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED-:AHU-A1153-002)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2024-02-06 00:36 | 2024-02-06 01:36 | 2024-02-07 01:36 | 24 | 2024-02-06 00:40 | 2024-02-06 03:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2022-11206262 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | RETURN MOTOR FLEXIBLE CONDUIT DAMAGED- TG-06A-13 |  | FM008 |  | 2022-11-20 15:38 | 2022-11-20 16:38 | 2022-11-21 16:38 | 24 | 2022-11-20 15:48 | 2022-11-20 17:16 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11615972 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | FILTER DIRTY ,AHU-A1153-002, TG-06A-13 |  | FM008 |  | 2023-04-04 09:01 | 2023-04-04 10:01 | 2023-04-05 10:01 | 24 | 2023-04-04 09:10 | 2023-04-04 11:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM7343 | Ansari, Mr. Azad Hussain | N - - - |  | Voice Communication
| CM-2023-11806354 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM THE CEILING.-CEILING INFRONT OF T1 08A 29-SOUTH NODE NEAR TO SERVICE ANIMAL AREA |  | FM008 |  | 2023-05-19 02:09 | 2023-05-19 03:09 | 2023-05-20 03:09 | 24 | 2023-05-19 02:20 | 2023-05-19 05:40 | 200 | 245 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 17336 | 17053 |  |  | FM11004 | Ali, Mr. Mir Asraf | N - - - |  | Voice Communication
| CM-2023-11823055 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | FILTER BLOCKED – TG-06A-13 |  | FM008 |  | 2023-05-24 21:31 | 2023-05-24 22:31 | 2023-05-25 22:31 | 24 | 2023-05-24 21:40 | 2023-05-24 23:58 | 138 | 171 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 105233 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11822979 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CABIN LAMP NOT WORKING – (AHU-A1153-002)- TG 06A 13 |  | FM008 |  | 2023-05-24 16:34 | 2023-05-24 17:34 | 2023-05-25 17:34 | 24 | 2023-05-24 16:40 | 2023-05-24 17:30 | 50 | 100 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 132112 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11885001 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC VENTS DUSTY, OPEN AREA IN FRONT OF BAR COUNTER- FFL1 |  | FM008 |  | 2023-06-15 13:34 | 2023-06-15 14:34 | 2023-06-16 14:34 | 24 | 2023-06-15 13:40 | 2023-06-16 04:00 | 860 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 124475 | 87807 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | E-mail
| CM-2023-11913865 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU NOISY |  | FM008 |  | 2023-06-25 07:08 | 2023-06-25 08:08 | 2023-06-26 08:08 | 24 | 2023-06-25 07:15 | 2023-06-25 11:15 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-12002072 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | FFL1 & FFL2 SEATING AREA – AC TOO HOT |  | FM008 |  | 2023-07-23 13:31 | 2023-07-23 14:31 | 2023-07-24 14:31 | 24 | 2023-07-23 13:40 | 2023-07-23 14:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 105233 | 17053 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-12112192 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC TOO HOT FFL2 ADMIN OFFICE |  | FM008 |  | 2023-08-24 05:46 | 2023-08-24 06:46 | 2023-08-25 06:46 | 24 | 2023-08-24 05:50 | 2023-08-24 06:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 17053 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2024-12851664 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2024-04-29 00:25 | 2024-04-29 01:25 | 2024-04-30 01:25 | 24 | 2024-04-29 00:35 | 2024-04-29 03:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106972 | 87807 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2023-12441181 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC TEMPERATURE TOO COLD IN MAIN DINING AREA |  | FM008 |  | 2023-12-04 03:17 | 2023-12-04 04:17 | 2023-12-05 04:17 | 24 | 2023-12-04 03:25 | 2023-12-04 04:00 | 35 | 35 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106914 | 17053 |  |  | 82773 | Nefzi, Mr. Ahmed | N - - - |  | Voice Communication
| CM-2024-12778901 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | FFL1 AC TOO COLD FFL1 DINING AREA |  | FM008 |  | 2024-03-29 13:04 | 2024-03-29 14:04 | 2024-03-30 14:04 | 24 | 2024-03-29 13:10 | 2024-03-29 14:10 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 17053 |  |  | 63260 | Kasibante, Mr. Macknon | N - - - |  | Voice Communication
| CM-2023-12363372 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED- TG-06A-13 |  | FM008 |  | 2023-11-07 12:36 | 2023-11-07 13:36 | 2023-11-08 13:36 | 24 | 2023-11-07 12:40 | 2023-11-07 15:30 | 170 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 106914 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2022-10202355 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS - AHU-A1153-002 - TG-06A-13 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1153.GNDP3.SBW03.AHU002.SYSALM.DP1 / |  | FM008 |  | 2022-02-28 16:28 | 2022-02-28 17:28 | 2022-03-01 17:28 | 24 | 2022-02-28 16:35 | 2022-02-28 18:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | BMS
| CM-2022-10237792 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-TG-06A-13 |  | FM008 |  | 2022-03-12 19:42 | 2022-03-12 20:42 | 2022-03-13 20:42 | 24 | 2022-03-12 19:50 | 2022-03-12 22:20 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106914 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10313474 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1153-002 – TG-06A-13 |  | FM008 |  | 2022-04-02 19:20 | 2022-04-02 20:20 | 2022-04-03 20:20 | 24 | 2022-04-02 19:25 | 2022-04-02 23:00 | 215 | 645 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10362010 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU-A1153-002 DP2 FILTER ALARM |  | FM008 |  | 2022-04-14 06:59 | 2022-04-14 07:59 | 2022-04-15 07:59 | 24 | 2022-04-14 07:05 | 2022-04-14 14:30 | 445 | 245 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10707612 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU-A1153-002- SUPPLY DUCT CANVAS AIR LEAKAGE – TG-06A-13 |  | FM008 |  | 2022-05-29 21:50 | 2022-05-29 22:50 | 2022-05-30 22:50 | 24 | 2022-05-29 21:55 | 2022-05-29 23:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17154 | 55709 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2022-10832301 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC IS TOO COLD- FFL1 RECEPTION |  | FM008 |  | 2022-07-16 10:16 | 2022-07-16 11:16 | 2022-07-17 11:16 | 24 | 2022-07-16 10:25 | 2022-07-16 11:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 87807 | 95217 |  |  | 90044 | Hanini, Mr. Abdelkebir | N - - - |  | Voice Communication
| CM-2022-11112287 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT NOT WORKING – MEC ROOM TG-06A-13 |  | FM008 |  | 2022-10-17 20:07 | 2022-10-17 21:07 | 2022-10-18 21:07 | 24 | 2022-10-17 20:10 | 2022-10-17 23:20 | 190 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 105233 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11197786 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – AHU-A1153-002 – TG-06A-13 |  | FM008 |  | 2022-11-19 07:44 | 2022-11-19 08:44 | 2022-11-20 08:44 | 24 | 2022-11-19 07:55 | 2022-11-19 09:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11362935 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU-A1153-002) -RETURN DUCT CANVAS AIR LEAKAGE -TG-06A-13 |  | FM008 |  | 2023-01-13 07:20 | 2023-01-13 08:20 | 2023-01-14 08:20 | 24 | 2023-01-13 07:30 | 2023-01-13 10:30 | 180 | 720 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11355818 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-01-09 19:53 | 2023-01-09 20:53 | 2023-01-10 20:53 | 24 | 2023-01-09 20:00 | 2023-01-09 22:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 95216 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11918595 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2023-06-25 10:49 | 2023-06-25 11:49 | 2023-06-26 11:49 | 24 | 2023-06-25 10:55 | 2023-06-25 20:30 | 575 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2023-11950900 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AHU-A1153-002 - CHILLED WATER LINE PAINT FADED – TG-06A-013 |  | FM008 |  | 2023-07-07 13:23 | 2023-07-07 14:23 | 2023-07-08 14:23 | 24 | 2023-07-07 13:30 | 2023-07-07 17:30 | 240 | 365 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 94954 | 87807 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2024-12749076 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | AC TOO COLD – ENTIRE FFL1 LOUNGE |  | FM008 |  | 2024-03-19 08:40 | 2024-03-19 09:40 | 2024-03-20 09:40 | 24 | 2024-03-19 08:45 | 2024-03-19 12:05 | 200 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 95217 |  |  | 103922 | Istiak, Mr. Shamim | N - - - |  | Voice Communication
| CM-2024-12769353 | ASD-MTB-GFL06A-AHU169 | AIR HANDLING UNIT-05 | A1-FFL1-31 AC VENT MISALIGNED |  | FM008 |  | 2024-03-27 02:42 | 2024-03-27 03:42 | 2024-03-28 03:42 | 24 | 2024-03-27 02:50 | 2024-03-27 06:35 | 225 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | VIBRATION OF EQUIPMENT DUE TO LOOSE PARTS | RECTIFIED | 89127 | 95217 |  |  | FM7722 | Onyango, Mr. Patrick | N - - - |  | Voice Communication
| CM-2022-10066323 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-01-19 14:44 | 2022-01-19 15:44 | 2022-01-20 15:44 | 24 | 2022-01-19 14:50 | 2022-01-19 17:30 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | BMS
| CM-2022-10262529 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED-TG-06A-13 |  | FM008 |  | 2022-03-19 19:08 | 2022-03-19 20:08 | 2022-03-20 20:08 | 24 | 2022-03-19 19:15 | 2022-03-19 21:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 106914 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10830826 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DINING AREA FFL 2 - AC TOO COLD |  | FM008 |  | 2022-07-14 02:41 | 2022-07-14 03:41 | 2022-07-15 03:41 | 24 | 2022-07-14 02:45 | 2022-07-14 08:00 | 315 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 95217 |  |  | 109304 | Mahajani, Mr. Amit Ravindra | N - - - |  | Voice Communication
| CM-2022-11061272 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | FILTER DIRTY -CM-2022-04-2001 |  | FM008 |  | 2022-09-25 22:01 | 2022-09-25 23:01 | 2022-09-26 23:01 | 24 | 2022-09-25 22:05 | 2022-09-25 23:00 | 55 | 165 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 76858 | 87807 |  |  | FM1460 | SANTOSH | - - - |  | Voice Communication
| CM-2023-11471927 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AHU-A1153-003 CHILL WATER LINE PAINT FADED TG-06A-13 |  | FM008 |  | 2023-02-19 19:55 | 2023-02-19 20:55 | 2023-02-20 20:55 | 24 | 2023-02-19 20:00 | 2023-02-19 23:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 87807 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11764329 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1153-003 - TG-06A-13 |  | FM008 |  | 2023-05-04 15:08 | 2023-05-04 16:08 | 2023-05-05 16:08 | 24 | 2023-05-04 15:15 | 2023-05-04 17:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11862279 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS - AHU-A1153-003 |  | FM008 |  | 2023-06-07 23:10 | 2023-06-08 00:10 | 2023-06-09 00:10 | 24 | 2023-06-07 23:15 | 2023-06-08 00:05 | 50 | 95 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11961878 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-07-09 08:53 | 2023-07-09 09:53 | 2023-07-10 09:53 | 24 | 2023-07-09 09:00 | 2023-07-09 12:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 68060 | 87807 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2023-11970782 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | FFL2 ADMIN OFFICE AC VENT DIRTY |  | FM008 |  | 2023-07-13 13:12 | 2023-07-13 14:12 | 2023-07-14 14:12 | 24 | 2023-07-13 13:20 | 2023-07-14 03:30 | 850 | 185 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 89127 | 87807 |  |  | FM7799 | Mugambi, Mr. Antony | N - - - |  | Voice Communication
| CM-2023-12256245 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO COLD - QUITE AREA - FFL2 |  | FM008 |  | 2023-10-07 06:56 | 2023-10-07 07:56 | 2023-10-08 07:56 | 24 | 2023-10-07 07:05 | 2023-10-07 10:05 | 180 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 119320 | 87807 |  |  | FM6955 | Okech, Ms. Sarah Adhiambo | N - - - |  | Voice Communication
| CM-2024-12798062 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC NOT WORKING - A2-FFL2-13 |  | FM008 |  | 2024-04-06 00:45 | 2024-04-06 01:45 | 2024-04-07 01:45 | 24 | 2024-04-06 00:50 | 2024-04-06 05:00 | 250 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | FM7722 | PATRICK | N - - - |  | Voice Communication
| CM-2022-11113806 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1153-003)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2022-10-20 09:43 | 2022-10-20 10:43 | 2022-10-21 10:43 | 24 | 2022-10-20 09:50 | 2022-10-20 12:30 | 160 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2023-11367067 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1153-003 – TG-06A-13 |  | FM008 |  | 2023-01-14 07:33 | 2023-01-14 08:33 | 2023-01-15 08:33 | 24 | 2023-01-14 07:40 | 2023-01-14 11:40 | 240 | 960 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 55709 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11486491 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO WARM |  | FM008 |  | 2023-02-24 10:36 | 2023-02-24 11:36 | 2023-02-25 11:36 | 24 | 2023-02-24 10:45 | 2023-02-24 14:10 | 205 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 87807 |  |  | 128703 | Nacionales, Mr. Menecio Balinas | N - - - |  | Voice Communication
| CM-2023-11840790 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO HOT IN FFL 2 DINING AREA |  | FM008 |  | 2023-05-31 06:34 | 2023-05-31 07:34 | 2023-06-01 07:34 | 24 | 2023-05-31 06:40 | 2023-05-31 10:00 | 200 | 60 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106914 | 87807 |  |  | 121010 | Muthirakalayil, Mr. Sobith Raj | N - - - |  | Voice Communication
| CM-2023-11877745 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC NOT WORKING FFL2 ADMIN OFFICE NEAR A2-FFL2-01 |  | FM008 |  | 2023-06-13 23:35 | 2023-06-14 00:35 | 2023-06-15 00:35 | 24 | 2023-06-13 23:45 | 2023-06-14 00:45 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 68485 | 87807 |  |  | FM11747 | Wanyama, Mr. Andrew | N - - - |  | Voice Communication
| CM-2023-11969795 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO HOT – FFL2 SEATING AREA |  | FM008 |  | 2023-07-12 18:24 | 2023-07-12 19:24 | 2023-07-13 19:24 | 24 | 2023-07-12 18:30 | 2023-07-12 20:00 | 90 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | 133277 | Abubakkar, Mr. Abrar Ahamed | N - - - |  | Voice Communication
| CM-2023-12187604 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -AG NO:AHU-A1153-003)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-09-16 01:07 | 2023-09-16 02:07 | 2023-09-17 02:07 | 24 | 2023-09-16 01:10 | 2023-09-16 04:10 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM7252 | Arcie Gingco Anquillano, | N - - - |  | Voice Communication
| CM-2023-12231870 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | WALL AC VENT WITH ACUMINATED DUST -T1-06A-04 |  | FM008 |  | 2023-09-29 15:03 | 2023-09-29 16:03 | 2023-09-30 16:03 | 24 | 2023-09-29 15:10 | 2023-09-30 01:28 | 618 | 181 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM5770 | Khan, Mr. Md Ratan | N - - - |  | Voice Communication
| CM-2023-12302322 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM THE CEILING – A2-FFL2-01 ,PANTRY |  | FM008 |  | 2023-10-19 16:27 | 2023-10-19 16:57 | 2023-10-19 20:57 | 4 | 2023-10-19 16:36 | 2023-10-19 19:55 | 199 | 174 | 4 | HVAC |  | Closed | Urgent | GROUND FLOOR AREA 06A | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 105233 | 87807 |  |  | FM7722 | PATRICK | N - - - |  | Voice Communication
| CM-2024-12576347 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO COLD -FFL2 |  | FM008 |  | 2024-01-19 09:13 | 2024-01-19 10:13 | 2024-01-20 10:13 | 24 | 2024-01-19 09:20 | 2024-01-19 13:15 | 235 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 17053 |  |  | 20960 | Limpaiboon, Ms. Sukanya | N - - - |  | Voice Communication
| CM-2022-11112673 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | FILTER BLOCKED - AHU-A1153-003 |  | FM008 |  | 2022-10-19 12:30 | 2022-10-19 13:30 | 2022-10-20 13:30 | 24 | 2022-10-19 12:40 | 2022-10-19 15:20 | 160 | 340 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11215697 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT ILLUMINATING - AHU-A1153-003 - MECHANICAL ROOM TG-06A-13 |  | FM008 |  | 2022-11-24 16:02 | 2022-11-24 17:02 | 2022-11-25 17:02 | 24 | 2022-11-24 16:10 | 2022-11-24 17:38 | 88 | 176 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 17573 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11267157 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1153-003 – TG-06A-13 |  | FM008 |  | 2022-12-12 07:52 | 2022-12-12 08:52 | 2022-12-13 08:52 | 24 | 2022-12-12 08:00 | 2022-12-12 11:20 | 200 | 600 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-11356938 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | SUPPLY DUCT CANVAS AIR LEAKAGE |  | FM008 |  | 2023-01-09 07:51 | 2023-01-09 08:51 | 2023-01-10 08:51 | 24 | 2023-01-09 07:56 | 2023-01-09 11:00 | 184 | 614 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 17053 |  |  | FM1947 | Prasanth, Mr. Bhuvanendran | N - - - |  | Voice Communication
| CM-2023-11459861 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DINING AREA AC TEMPERATURE TOO WARM-FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-02-15 23:21 | 2023-02-16 00:21 | 2023-02-17 00:21 | 24 | 2023-02-15 23:30 | 2023-02-16 00:30 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LOW COOLING | NO PROPER CHILLED WATER SUPPLY | CHECK THE CHILLED WATER SUPPLY AND RECTIFY | 77406 | 87807 |  |  | 129477 | Chathankandath Alavarssi, Mr. Prasanth | N - - - |  | Voice Communication
| CM-2024-12555651 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | FFL2 ADMIN OFFICE – AC VENT DIRTY |  | FM008 |  | 2024-01-12 20:40 | 2024-01-12 21:40 | 2024-01-13 21:40 | 24 | 2024-01-12 20:45 | 2024-01-12 23:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2024-12623674 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING – TG-06A-13 |  | FM008 |  | 2024-02-05 20:12 | 2024-02-05 21:12 | 2024-02-06 21:12 | 24 | 2024-02-05 20:20 | 2024-02-06 01:25 | 305 | 333 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106914 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2023-12362175 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-11-08 13:20 | 2023-11-08 14:20 | 2023-11-09 14:20 | 24 | 2023-11-08 13:25 | 2023-11-08 17:00 | 215 | 310 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM0599 | Saklain, Mr. Mohammad | N - - - |  | Voice Communication
| CM-2023-12426014 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGE -- AG-06A-13 |  | FM008 |  | 2023-11-28 23:07 | 2023-11-29 00:07 | 2023-11-30 00:07 | 24 | 2023-11-28 23:15 | 2023-11-29 01:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 87807 |  |  | FM12447 | Murugaiyan, Mr. Vijayakumar | N - - - |  | Voice Communication
| CM-2024-12564958 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC GRILL COVER DETACHED A2-FFL2-02 |  | FM008 |  | 2024-01-15 03:15 | 2024-01-15 04:15 | 2024-01-16 04:15 | 24 | 2024-01-15 03:20 | 2024-01-15 06:35 | 195 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LOOSE | DUCT SUPPORT LOOSE | RECTIFIED | 106972 | 95217 |  |  | FM7799 | Mugambi, Mr. Antony Mutwiri | N - - - |  | Voice Communication
| CM-2023-12384931 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO COLD – A2-FFL2-01 |  | FM008 |  | 2023-11-16 06:51 | 2023-11-16 07:51 | 2023-11-17 07:51 | 24 | 2023-11-16 06:55 | 2023-11-16 17:05 | 610 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 106973 | 87807 |  |  | 112295 | Shaikh, Mr. Mohin Wahid Ahmed | N - - - |  | Voice Communication
| CM-2023-12431104 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO COLD - FFL2 OPEN AREA |  | FM008 |  | 2023-12-03 02:37 | 2023-12-03 03:37 | 2023-12-04 03:37 | 24 | 2023-12-03 02:45 | 2023-12-03 04:00 | 75 | 65 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 119320 | 17053 |  |  | 83643 | Vazhayil Kandoth, Mr. Safran | N - - - |  | Voice Communication
| CM-2024-12629584 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2024-02-06 19:27 | 2024-02-06 20:27 | 2024-02-07 20:27 | 24 | 2024-02-06 19:35 | 2024-02-06 22:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 95217 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12845942 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO COLD - FL2 QUIET AREA |  | FM008 |  | 2024-04-22 23:32 | 2024-04-23 00:32 | 2024-04-24 00:32 | 24 | 2024-04-22 23:40 | 2024-04-23 00:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2022-10121005 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | COIL DIRTY |  | FM008 |  | 2022-02-09 03:39 | 2022-02-09 04:39 | 2022-02-10 04:39 | 24 | 2022-02-09 03:45 | 2022-02-09 06:30 | 165 | 495 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10201561 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – TG-06A-13 |  | FM008 |  | 2022-03-01 03:54 | 2022-03-01 04:54 | 2022-03-02 04:54 | 24 | 2022-03-01 04:00 | 2022-03-01 05:30 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10790814 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AHU-A1153-003-FILTER BLOCKED |  | FM008 |  | 2022-06-29 21:00 | 2022-06-29 22:00 | 2022-06-30 22:00 | 24 | 2022-06-29 21:10 | 2022-06-29 23:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 95217 | 95217 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11135699 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO HOT - QUIET AREA - FFL 2 |  | FM008 |  | 2022-10-26 18:46 | 2022-10-26 19:46 | 2022-10-27 19:46 | 24 | 2022-10-26 18:55 | 2022-10-26 20:00 | 65 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17154 | 87807 |  |  | 87522 | Ouacif, Mr. Isslam | N - - - |  | Voice Communication
| CM-2022-11179133 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY |  | FM008 |  | 2022-11-09 19:40 | 2022-11-09 20:40 | 2022-11-10 20:40 | 24 | 2022-11-09 19:45 | 2022-11-09 23:30 | 225 | 900 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-11197785 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED – AHU-A1153-003 – TG-06A-13 |  | FM008 |  | 2022-11-19 07:43 | 2022-11-19 08:43 | 2022-11-20 08:43 | 24 | 2022-11-19 07:50 | 2022-11-19 09:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 124475 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11447520 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO HOT - BACK OF THE HOUSE - AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-02-11 21:58 | 2023-02-11 22:58 | 2023-02-12 22:58 | 24 | 2023-02-11 22:05 | 2023-02-11 23:00 | 55 | 55 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 132112 | 17053 |  |  | 85528 | Ramos, Mr. Jay Conrad Austria | N - - - |  | Voice Communication
| CM-2023-11608953 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM |  | FM008 |  | 2023-03-30 02:06 | 2023-03-30 03:06 | 2023-03-31 03:06 | 24 | 2023-03-30 02:15 | 2023-03-30 04:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11469735 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC IS TOO COLD -DINING AREA FFL2 -FREQUENT FLYER LOUNGE 2 |  | FM008 |  | 2023-02-18 23:46 | 2023-02-19 00:46 | 2023-02-20 00:46 | 24 | 2023-02-18 23:55 | 2023-02-19 01:20 | 85 | 64 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 17053 |  |  | 124352 | Navarro, Ms. Patricia Carretero | N - - - |  | Voice Communication
| CM-2023-11932278 | ASD-MTB-GFL06A-AHU170 | AIR HANDLING UNIT-05 | AC TOO WARM - FFL2 DINING & BAR SEATING AREA |  | FM008 |  | 2023-06-26 18:57 | 2023-06-26 19:57 | 2023-06-27 19:57 | 24 | 2023-06-26 19:05 | 2023-06-26 20:05 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 132979 | Mohommed, Mr. Faizanul Majid | N - - - |  | Voice Communication
| CM-2022-10308846 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 SUPPLY DUCT ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-03-30 12:10 | 2022-03-30 13:10 | 2022-03-31 13:10 | 24 | 2022-03-30 12:15 | 2022-03-30 16:00 | 225 | 620 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 55709 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-11039075 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 FILTER DIRTY |  | FM008 |  | 2022-09-22 21:17 | 2022-09-22 22:17 | 2022-09-23 22:17 | 24 | 2022-09-22 21:25 | 2022-09-22 23:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-11250700 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 171 -DP1 FILTER ALARM .MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2022-12-04 20:18 | 2022-12-04 21:18 | 2022-12-05 21:18 | 24 | 2022-12-04 20:30 | 2022-12-04 23:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 77406 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11345621 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | SUPPLY FAN FAIL ALARM - AHU-A1153-004 |  | FM008 |  | 2023-01-06 04:47 | 2023-01-06 05:47 | 2023-01-07 05:47 | 24 | 2023-01-06 04:50 | 2023-01-06 05:00 | 10 | 10 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | CIRCUIT TRIP DUE TO OVERLOAD | RESET THE BREAKER | 133396 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | Voice Communication
| CM-2023-11365175 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 RETURN DUCT INSUALTION DAMAGED |  | FM008 |  | 2023-01-12 02:10 | 2023-01-12 03:10 | 2023-01-13 03:10 | 24 | 2023-01-12 02:20 | 2023-01-12 06:00 | 220 | 355 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 55709 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11471928 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004- CHILL WATER LINE PAINT FADED TG-06A-13 |  | FM008 |  | 2023-02-19 19:56 | 2023-02-19 20:56 | 2023-02-20 20:56 | 24 | 2023-02-19 20:00 | 2023-02-19 23:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 87807 | 17053 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2023-11803973 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004- DP3 FILTER ALARM- - |  | FM008 |  | 2023-05-17 23:16 | 2023-05-18 00:16 | 2023-05-19 00:16 | 24 | 2023-05-17 23:25 | 2023-05-18 01:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11805257 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004)-FILTER BLOCKED-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-05-21 21:30 | 2023-05-21 22:30 | 2023-05-22 22:30 | 24 | 2023-05-21 21:37 | 2023-05-21 23:58 | 141 | 167 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-12024226 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004-ABNORMAL SOUND -MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-07-30 12:39 | 2023-07-30 13:39 | 2023-07-31 13:39 | 24 | 2023-07-30 12:45 | 2023-07-30 16:00 | 195 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 77406 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12545539 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM RETURN SIDE, AHU-A1153-004, TG-06A-13 |  | FM008 |  | 2024-01-08 09:11 | 2024-01-08 10:11 | 2024-01-09 10:11 | 24 | 2024-01-08 09:15 | 2024-01-08 12:00 | 165 | 660 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | LOOSE MOUNTING | CHECK AND TIGHTENED THE UNIT | 124475 | 17053 |  |  | FM1449 | Gopinathan Nair, Mr. Nidheesh | N - - - |  | Voice Communication
| CM-2024-12628959 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | ABNORMAL SOUND COMING FROM AHU-A1153-004 |  | FM008 |  | 2024-02-06 07:44 | 2024-02-06 08:44 | 2024-02-07 08:44 | 24 | 2024-02-06 07:50 | 2024-02-06 16:00 | 490 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68485 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2023-12488972 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 RIGHT HAND SIDE BELT WOBBLY -- AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2023-12-21 20:38 | 2023-12-21 21:38 | 2023-12-22 21:38 | 24 | 2023-12-21 20:45 | 2023-12-22 | 195 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 138627 | 87807 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2024-12537120 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | SUPPLY DUCT INSULATION DAMAGED - AHU-A1153-004 – TG-06A-13 |  | FM008 |  | 2024-01-07 07:53 | 2024-01-07 08:53 | 2024-01-08 08:53 | 24 | 2024-01-07 08:00 | 2024-01-07 12:30 | 270 | 275 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 133396 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12541163 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY -TG-06A-13 |  | FM008 |  | 2024-01-08 08:05 | 2024-01-08 09:05 | 2024-01-09 09:05 | 24 | 2024-01-08 08:10 | 2024-01-08 16:30 | 500 | 325 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17333 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2024-12592521 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | ABNORMAL NOISE -TAG NO:AHU-A1153-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2024-01-26 07:20 | 2024-01-26 08:20 | 2024-01-27 08:20 | 24 | 2024-01-26 07:25 | 2024-01-26 14:00 | 395 | 585 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 17336 | 17053 |  |  | FM12499 | Joy, Mr. Aneesh | N - - - |  | Voice Communication
| CM-2024-12707985 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU ABNORMAL NOISE |  | FM008 |  | 2024-03-05 08:39 | 2024-03-05 09:39 | 2024-03-06 09:39 | 24 | 2024-03-05 08:45 | 2024-03-05 12:15 | 210 | 840 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 17333 | 17053 |  |  | FM8044 | Janardhanan Chettiyar, Mr. Rajesh | N - - - |  | Voice Communication
| CM-2022-11063559 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | FILTER BLOCKED - TG-06A-13 |  | FM008 |  | 2022-09-28 00:59 | 2022-09-28 01:59 | 2022-09-29 01:59 | 24 | 2022-09-28 01:05 | 2022-09-28 02:00 | 55 | 110 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2023-11877698 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 AHU CABIN LAMP NOT WORKING TG-06A-13 |  | FM008 |  | 2023-06-13 18:58 | 2023-06-13 19:58 | 2023-06-14 19:58 | 24 | 2023-06-13 19:05 | 2023-06-14 01:20 | 375 | 265 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 89127 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12131868 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -TG-06A-13 |  | FM008 |  | 2023-08-28 20:49 | 2023-08-28 21:49 | 2023-08-29 21:49 | 24 | 2023-08-28 20:55 | 2023-08-29 00:10 | 195 | 125 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2024-12609946 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | QA2 BLUE RESORT – AC TOO HOT |  | FM008 |  | 2024-02-01 19:14 | 2024-02-01 20:14 | 2024-02-02 20:14 | 24 | 2024-02-01 19:20 | 2024-02-01 21:00 | 100 | 65 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 105233 | 17053 |  |  | 45778 | Nichani, Ms. Shilpa Ramesh | Y - - - |  | Voice Communication
| CM-2024-12827129 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 FILTER DIRTY - AIR HANDLING UNIT 171 (TAG NO:AHU-A1153-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2024-04-15 19:17 | 2024-04-15 20:17 | 2024-04-16 20:17 | 24 | 2024-04-15 19:25 | 2024-04-15 21:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12827130 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | SUPPLY BELT WOBLING - AIR HANDLING UNIT 171 (TAG NO:AHU-A1153-004)-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 06A |  | FM008 |  | 2024-04-15 19:19 | 2024-04-15 20:19 | 2024-04-16 20:19 | 24 | 2024-04-15 19:25 | 2024-04-15 21:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 119320 | 17053 |  |  | FM12499 | ANEESH JOY, | N - - - |  | Voice Communication
| CM-2024-12672464 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT LIGHTING SWITCH NOT WORKING |  | FM008 |  | 2024-02-21 19:06 | 2024-02-21 20:06 | 2024-02-22 20:06 | 24 | 2024-02-21 19:15 | 2024-02-21 23:29 | 254 | 343 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 95216 | 17053 |  |  | FM11198 | Mallick, Mr. Aamir | N - - - |  | Voice Communication
| CM-2022-10261635 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT DAMAGED |  | FM008 |  | 2022-03-20 19:20 | 2022-03-20 20:20 | 2022-03-21 20:20 | 24 | 2022-03-20 19:30 | 2022-03-20 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | CHILLED WATER ACTUATOR DAMAGE | RECTIFIED | 95216 | 87807 |  |  | FM2969 | Marri, Mr. Vinod Rajayya | N - - - |  | Voice Communication
| CM-2022-10886154 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1153.GNDP2.SBW01.AHU004.SYSALM.DP1 / /TG-06A-13 |  | FM008 |  | 2022-07-30 10:48 | 2022-07-30 11:48 | 2022-07-31 11:48 | 24 | 2022-07-30 10:55 | 2022-07-30 18:15 | 440 | 85 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 87807 |  |  | FM0459 | Manhandavida, Mr. Shaheel | Y - - - |  | BMS
| CM-2022-11112596 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | FILTER DIRTY -TG-06A-13 |  | FM008 |  | 2022-10-19 08:16 | 2022-10-19 09:16 | 2022-10-20 09:16 | 24 | 2022-10-19 08:20 | 2022-10-19 11:00 | 160 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106914 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10217822 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1153-004 – TG-06A-13 |  | FM008 |  | 2022-03-07 14:13 | 2022-03-07 15:13 | 2022-03-08 15:13 | 24 | 2022-03-07 14:20 | 2022-03-07 16:30 | 130 | 390 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM1460 | Parapurathu Divakaran , Mr. Santosh | N - - - |  | Voice Communication
| CM-2022-10364362 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | CHILL WATER LINE PIPE PAINT IA FADED - AHU-A1153-004 – TG-06A-13 |  | FM008 |  | 2022-04-15 12:55 | 2022-04-15 13:55 | 2022-04-16 13:55 | 24 | 2022-04-15 13:05 | 2022-04-15 16:00 | 175 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17573 | 17053 |  |  | FM3316 | Jose, Mr. Bibin | N - - - |  | Voice Communication
| CM-2022-10568903 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-004 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-04-21 12:54 | 2022-04-21 13:54 | 2022-04-22 13:54 | 24 | 2022-04-21 13:05 | 2022-04-21 18:45 | 340 | 365 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 17053 |  |  | FM0599 | Mohammad Saklain, Mr. | N - - - |  | Voice Communication
| CM-2022-10781727 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | AHU-A1153-403;DP 1FILTER ALARM – T4-06A-04 |  | FM008 |  | 2022-06-26 15:19 | 2022-06-26 16:19 | 2022-06-27 16:19 | 24 | 2022-06-26 15:25 | 2022-06-26 17:00 | 95 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2023-12189598 | ASD-MTB-GFL06A-AHU171 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED:AHU-A1153-004 |  | FM008 |  | 2023-09-16 19:40 | 2023-09-16 20:40 | 2023-09-17 20:40 | 24 | 2023-09-16 19:45 | 2023-09-16 22:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 06A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM8380 | Jitendra Kumar Sahani, | N - - - |  | Voice Communication
| CM-2022-11196671 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU-A1154-001- MARINE LIGHT NOT WORKING – TG-07-14 |  | FM008 |  | 2022-11-20 00:23 | 2022-11-20 01:23 | 2022-11-21 01:23 | 24 | 2022-11-20 00:30 | 2022-11-20 03:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17154 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11353152 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY-(AHU-1154-001)-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-01-06 20:50 | 2023-01-06 21:50 | 2023-01-07 21:50 | 24 | 2023-01-06 21:00 | 2023-01-06 23:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM2118 | Rumandla, Mr. Gangadas | N - - - |  | Voice Communication
| CM-2023-11808692 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT WORKING - AHU-A1154-001 – TG-07A-14 |  | FM008 |  | 2023-05-21 13:11 | 2023-05-21 14:11 | 2023-05-22 14:11 | 24 | 2023-05-21 13:20 | 2023-05-21 15:50 | 150 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 17573 | 17053 |  |  | FM4743 | Kalam Rashid Ahmed, Mr. Shaikh | N - - - |  | Voice Communication
| CM-2023-12018125 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU-A1154-001 FILTER DIRTY |  | FM008 |  | 2023-07-29 11:13 | 2023-07-29 12:13 | 2023-07-30 12:13 | 24 | 2023-07-29 11:20 | 2023-07-29 13:50 | 150 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12140806 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT INSOLATION DAMAGED, AHU-A1154-001, TG-07A-14 |  | FM008 |  | 2023-09-02 10:38 | 2023-09-02 11:38 | 2023-09-03 11:38 | 24 | 2023-09-02 10:45 | 2023-09-02 13:45 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 124475 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12188309 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | WATER LEAKAGE FROM CEILING QDF SUBSTORE TG-07A-07 |  | FM008 |  | 2023-09-15 09:35 | 2023-09-15 10:35 | 2023-09-16 10:35 | 24 | 2023-09-15 09:40 | 2023-09-15 14:00 | 260 | 165 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 17053 |  |  | C9837 | FRANK | N - - - |  | Voice Communication
| CM-2023-12322424 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1154-001 - MECHANICAL ROOM TG-07A-14 |  | FM008 |  | 2023-10-27 13:18 | 2023-10-27 14:18 | 2023-10-28 14:18 | 24 | 2023-10-27 13:25 | 2023-10-27 14:55 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12390408 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU-A1154-001 – COOLING COIL DIRTY - TG-07A-14 |  | FM008 |  | 2023-11-19 16:06 | 2023-11-19 17:06 | 2023-11-20 17:06 | 24 | 2023-11-19 16:10 | 2023-11-19 18:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 95217 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-11155797 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU SUPPLY FLOW LOW ALARM AHU-A1154-001 TG-07A-14 |  | FM008 |  | 2022-10-31 11:17 | 2022-10-31 12:17 | 2022-11-01 12:17 | 24 | 2022-10-31 11:20 | 2022-10-31 14:30 | 190 | 570 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2023-11629789 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-04-07 12:55 | 2023-04-07 13:55 | 2023-04-08 13:55 | 24 | 2023-04-07 13:05 | 2023-04-07 15:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12403028 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU-A1154-001 FILTER DIRTY |  | FM008 |  | 2023-11-20 13:27 | 2023-11-20 14:27 | 2023-11-21 14:27 | 24 | 2023-11-20 13:35 | 2023-11-20 16:35 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2024-12667229 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU-A1154-001 AHU CABIN LIGHT NOT WORKING - AIR HANDLING UNIT 175-AIRSIDE-SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2024-02-20 19:05 | 2024-02-20 20:05 | 2024-02-21 20:05 | 24 | 2024-02-20 19:15 | 2024-02-20 21:59 | 164 | 328 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 119320 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2024-12647416 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | AHU-A1154-001 FILTER DIRTY |  | FM008 |  | 2024-02-13 11:17 | 2024-02-13 12:17 | 2024-02-14 12:17 | 24 | 2024-02-13 11:25 | 2024-02-13 13:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM0473 | Balan Nair, Mr. Sreejesh | N - - - |  | Voice Communication
| CM-2022-11135542 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-10-26 08:23 | 2022-10-26 09:23 | 2022-10-27 09:23 | 24 | 2022-10-26 08:30 | 2022-10-26 10:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11193728 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2022-11-17 21:33 | 2022-11-17 22:33 | 2022-11-18 22:33 | 24 | 2022-11-17 21:40 | 2022-11-17 23:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2022-10793232 | ASD-MTB-GFL07A-AHU175 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM -TG-07A-14-AIR HANDLING UNIT 175-AIRSIDE-SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2022-07-03 11:05 | 2022-07-03 12:05 | 2022-07-04 12:05 | 24 | 2022-07-03 11:15 | 2022-07-03 13:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10192143 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | TERMINAL BOX FLEXIBLE CONNECTOR DAMAGED -TG-07A-14 |  | FM008 |  | 2022-02-27 15:04 | 2022-02-27 16:04 | 2022-02-28 16:04 | 24 | 2022-02-27 15:10 | 2022-02-27 16:36 | 86 | 172 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 17333 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10310810 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2022-04-02 20:17 | 2022-04-02 21:17 | 2022-04-03 21:17 | 24 | 2022-04-02 20:25 | 2022-04-02 23:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | BMS
| CM-2022-11188833 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU INSIDE LIGHT FUSED |  | FM008 |  | 2022-11-14 00:44 | 2022-11-14 01:44 | 2022-11-15 01:44 | 24 | 2022-11-14 00:50 | 2022-11-14 04:30 | 220 | 135 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 68060 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11206772 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU-11154-002 RETURN MOTOR ISOLATION SPRING DAMAGED |  | FM008 |  | 2022-11-22 07:42 | 2022-11-22 08:42 | 2022-11-23 08:42 | 24 | 2022-11-22 07:50 | 2022-11-22 09:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68485 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-11483593 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -TG-07-14 |  | FM008 |  | 2023-02-23 09:33 | 2023-02-23 10:33 | 2023-02-24 10:33 | 24 | 2023-02-23 09:40 | 2023-02-23 13:00 | 200 | 235 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12110855 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1154-002 – TG-07A-14 |  | FM008 |  | 2023-08-23 13:08 | 2023-08-23 14:08 | 2023-08-24 14:08 | 24 | 2023-08-23 13:15 | 2023-08-23 15:00 | 105 | 210 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 17573 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | BMS
| CM-2023-12405145 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | FILTER DIRTY - AIR HANDLING UNIT 176-AIRSIDE-SADDLE BAG EAST-GROUND FLOOR AREA 07A - TG-07A-14 |  | FM008 |  | 2023-11-21 15:03 | 2023-11-21 16:03 | 2023-11-22 16:03 | 24 | 2023-11-21 15:10 | 2023-11-21 17:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12405265 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU CABIN LIGHT NOT ILLUMINATING - AHU-A1154-002 – TG-07A-14 |  | FM008 |  | 2023-11-22 00:30 | 2023-11-22 01:30 | 2023-11-23 01:30 | 24 | 2023-11-22 00:35 | 2023-11-22 02:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 17573 | 87807 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12486531 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -TG-07A-14 |  | FM008 |  | 2023-12-18 09:49 | 2023-12-18 10:49 | 2023-12-19 10:49 | 24 | 2023-12-18 09:55 | 2023-12-18 12:30 | 155 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 17053 |  |  | FM1183 | Hetaukar, Mr. Irfan Dawood | N - - - |  | Voice Communication
| CM-2022-11233783 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU-A1154-002 COOLING COIL DIRTY - TG-09A-14 |  | FM008 |  | 2022-12-03 22:10 | 2022-12-03 23:10 | 2022-12-04 23:10 | 24 | 2022-12-03 22:15 | 2022-12-04 01:45 | 210 | 630 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106972 | 17053 |  |  | FM5553 | Mohamad Haneef Abdul Hameed, Mr. Majgaonkar | N - - - |  | Voice Communication
| CM-2023-11836308 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | AHU-A1154-002 COOLING COIL DIRTY |  | FM008 |  | 2023-05-29 08:03 | 2023-05-29 09:03 | 2023-05-30 09:03 | 24 | 2023-05-29 08:10 | 2023-05-29 12:10 | 240 | 480 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 87807 |  |  | FM5553 | MOHAMAD HANEEF ABDUL HAMEED MAJGAONKAR, | N - - - |  | Voice Communication
| CM-2023-12058383 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | SUPPLY AIR FLOW LEAKAGE FROM ACCESS DOOR AND COVER ALL TEST POINT PROPERLY – TG-07A-14 MECHANICAL ROOM |  | FM008 |  | 2023-08-07 15:16 | 2023-08-07 16:16 | 2023-08-08 16:16 | 24 | 2023-08-07 15:25 | 2023-08-07 17:00 | 95 | 285 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17573 | 87807 |  |  | 79794 | Naseer, Mr. Tahir | N - - - |  | E-mail
| CM-2023-12140805 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | DRAIN LINE INSOLATION DAMAGED, AHU-A1154-002 , TG-07A-14 |  | FM008 |  | 2023-09-02 10:34 | 2023-09-02 11:34 | 2023-09-03 11:34 | 24 | 2023-09-02 10:40 | 2023-09-02 13:10 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 87807 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12199008 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1154-002 – TG-07A-14 |  | FM008 |  | 2023-09-18 20:39 | 2023-09-18 21:39 | 2023-09-19 21:39 | 24 | 2023-09-18 20:45 | 2023-09-18 22:45 | 120 | 480 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12390410 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | PRESSURE DUCT INSULATION DAMGAED - TG-07A-14 |  | FM008 |  | 2023-11-19 16:09 | 2023-11-19 17:09 | 2023-11-20 17:09 | 24 | 2023-11-19 16:15 | 2023-11-19 18:50 | 155 | 335 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 95217 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2023-12395426 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-20 22:19 | 2023-11-20 23:19 | 2023-11-21 23:19 | 24 | 2023-11-20 22:30 | 2023-11-21 00:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12690179 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | TG-07A-14 DUCT INSULATION DAMAGE 33621856 |  | FM008 |  | 2024-03-01 10:27 | 2024-03-01 11:27 | 2024-03-02 11:27 | 24 | 2024-03-01 10:35 | 2024-03-01 12:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 138627 | 17053 |  |  | FM0473 | Balan Nair, Mr. Sreejesh | N - - - |  | Voice Communication
| CM-2022-11081503 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | FILTER IS BLOCKED |  | FM008 |  | 2022-10-09 07:36 | 2022-10-09 08:36 | 2022-10-10 08:36 | 24 | 2022-10-09 07:45 | 2022-10-09 10:45 | 180 | 185 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 68060 | 95217 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12403026 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM BLOWER |  | FM008 |  | 2023-11-20 13:22 | 2023-11-20 14:22 | 2023-11-21 14:22 | 24 | 2023-11-20 13:30 | 2023-11-20 16:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 68485 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-12399190 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | MOTOR PULLY MISALIGNED, AHU-A1154-002, TG-07A-14 |  | FM008 |  | 2023-11-22 08:01 | 2023-11-22 09:01 | 2023-11-23 09:01 | 24 | 2023-11-22 08:10 | 2023-11-22 11:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | PULLEY DAMAGE | REPLACED THE PULLEY | 124475 | 87807 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2022-10208190 | ASD-MTB-GFL07A-AHU176 | AIR HANDLING UNIT-05 | FILTER DIRTY AHU-A1154-002 TG-07A-14 |  | FM008 |  | 2022-03-02 08:06 | 2022-03-02 09:06 | 2022-03-03 09:06 | 24 | 2022-03-02 08:10 | 2022-03-02 11:00 | 170 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 85125 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10976379 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | AC TOO HOT - T2-09A-08 |  | FM008 |  | 2022-08-28 14:20 | 2022-08-28 15:20 | 2022-08-29 15:20 | 24 | 2022-08-28 14:25 | 2022-08-28 15:25 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 55709 |  |  | 96986 | Katugampola, Mr. Chamidu Hiranga | N - - - |  | Voice Communication
| CM-2022-11188796 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | RETURN MOTOR FAN DAMAGED -TG-07A-14 |  | FM008 |  | 2022-11-13 18:53 | 2022-11-13 19:53 | 2022-11-14 19:53 | 24 | 2022-11-13 19:00 | 2022-11-13 21:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | RETURN FAN MOTOR BURNT | REPLACED THE MOTOR | 17333 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11211058 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | AHU-A1154-003 AHU CABIN LIGHT NOT WORKING TG-07A-14 |  | FM008 |  | 2022-11-22 19:12 | 2022-11-22 20:12 | 2022-11-23 20:12 | 24 | 2022-11-22 19:17 | 2022-11-22 21:17 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 87807 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11618340 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY-SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-04-05 10:00 | 2023-04-05 11:00 | 2023-04-06 11:00 | 24 | 2023-04-05 10:10 | 2023-04-05 13:30 | 200 | 600 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12486532 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED -TG-07A-14 |  | FM008 |  | 2023-12-18 09:51 | 2023-12-18 10:51 | 2023-12-19 10:51 | 24 | 2023-12-18 09:55 | 2023-12-18 13:00 | 185 | 365 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17333 | 17053 |  |  | FM1183 | Hetaukar, Mr. Irfan Dawood | N - - - |  | Voice Communication
| CM-2023-11823361 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | FILTER DIRTY – TG-07A-14 |  | FM008 |  | 2023-05-23 01:29 | 2023-05-23 02:29 | 2023-05-24 02:29 | 24 | 2023-05-23 01:35 | 2023-05-23 03:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12322425 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1154-003 - MECHANICAL ROOM TG-07A-14 |  | FM008 |  | 2023-10-27 13:21 | 2023-10-27 14:21 | 2023-10-28 14:21 | 24 | 2023-10-27 13:30 | 2023-10-27 18:00 | 270 | 545 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12395428 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-20 22:20 | 2023-11-20 23:20 | 2023-11-21 23:20 | 24 | 2023-11-20 22:30 | 2023-11-20 23:30 | 60 | 180 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12406512 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1154-003 – TG-07A-14 |  | FM008 |  | 2023-11-22 20:55 | 2023-11-22 21:55 | 2023-11-23 21:55 | 24 | 2023-11-22 21:05 | 2023-11-22 23:55 | 170 | 680 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 133396 | 17053 |  |  | FM12539 | Jayaraj, Mr. Sowmesh | N - - - |  | Voice Communication
| CM-2024-12692006 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | SUPPLY DUCT ACCESS DOOR LEAKAGE - T1-09A-31 |  | FM008 |  | 2024-02-29 11:50 | 2024-02-29 12:50 | 2024-03-01 12:50 | 24 | 2024-02-29 12:00 | 2024-02-29 13:30 | 90 | 270 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 121959 | 17053 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2022-11197825 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | AC TOO COLD - TRANSFER - B ALL AREA |  | FM008 |  | 2022-11-19 09:50 | 2022-11-19 10:50 | 2022-11-20 10:50 | 24 | 2022-11-19 10:00 | 2022-11-19 11:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 124475 | 87807 |  |  | MOI | KHALID | N - - - |  | Voice Communication
| CM-2022-10989689 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | AHU SUPPLY BLOWER PAINT IS FDED - AHU-A1154-003 - MECHANICAL ROOM TG-07A-14 |  | FM008 |  | 2022-08-29 13:10 | 2022-08-29 14:10 | 2022-08-30 14:10 | 24 | 2022-08-29 13:20 | 2022-08-29 16:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 17573 | 55709 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2022-11135543 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-10-26 08:25 | 2022-10-26 09:25 | 2022-10-27 09:25 | 24 | 2022-10-26 08:30 | 2022-10-26 11:30 | 180 | 260 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11342460 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-01-03 20:31 | 2023-01-03 21:31 | 2023-01-04 21:31 | 24 | 2023-01-03 20:40 | 2023-01-03 23:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12138824 | ASD-MTB-GFL07A-AHU177 | AIR HANDLING UNIT-05 | AIR LEAKAGE FROM SUPPLY AIR DUCT ACCESS DOOR -SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-09-02 16:28 | 2023-09-02 17:28 | 2023-09-03 17:28 | 24 | 2023-09-02 16:35 | 2023-09-02 18:35 | 120 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17336 | 105233 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-11149355 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU-A1154-004 RETURN DUCT CANVASS DAMAGED TG-07A-14 |  | FM008 |  | 2022-10-30 07:51 | 2022-10-30 08:51 | 2022-10-31 08:51 | 24 | 2022-10-30 08:00 | 2022-10-30 13:00 | 300 | 565 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 89127 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11780316 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | FILTER DIRTY – TG 04 14 |  | FM008 |  | 2023-05-09 09:14 | 2023-05-09 10:14 | 2023-05-10 10:14 | 24 | 2023-05-09 09:20 | 2023-05-09 11:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 106972 |  |  | FM3102 | ASHTAMAN, Mr. RAJAN | N - - - |  | Voice Communication
| CM-2023-11801060 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | RAD OPEN FAIL ALARM AIR HANDLING UNIT 178-AIRSIDE-SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-05-17 16:48 | 2023-05-17 17:48 | 2023-05-18 17:48 | 24 | 2023-05-17 16:55 | 2023-05-17 17:30 | 35 | 35 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11887625 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | BAC3.SADDLE BAG EAST.SBE GROUND FLOOR TG-07A-14.SBE DDC-A1154-AHU-004+001.DDC-A1154-AHU-004 |  | FM008 |  | 2023-06-17 19:03 | 2023-06-17 20:03 | 2023-06-18 20:03 | 24 | 2023-06-17 19:10 | 2023-06-17 22:30 | 200 | 125 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | ATUACTOR DAMAGE | REPLACED THE COIL | 124475 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12319092 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | RETURN DUCT AIR LEAKAGE -SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-10-23 13:59 | 2023-10-23 14:59 | 2023-10-24 14:59 | 24 | 2023-10-23 14:05 | 2023-10-23 18:35 | 270 | 810 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 17336 | 87807 |  |  | FM1450 | Kani Abdullah, Mr. Nagoor | N - - - |  | Voice Communication
| CM-2022-11189547 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU INSIDE FEXIBLE COPEX DAMAGED AHU-A1154-004 |  | FM008 |  | 2022-11-13 19:13 | 2022-11-13 20:13 | 2022-11-14 20:13 | 24 | 2022-11-13 19:20 | 2022-11-13 22:20 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 124475 | 87807 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-11249852 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED T4-07A-03 |  | FM008 |  | 2022-12-06 13:10 | 2022-12-06 14:10 | 2022-12-07 14:10 | 24 | 2022-12-06 13:15 | 2022-12-06 16:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95216 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11699721 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | Global Signal Status alarm A1154-AHU-004 TG-07A-14 |  | FM008 |  | 2023-04-27 03:41 | 2023-04-27 04:41 | 2023-04-28 04:41 | 24 | 2023-04-27 03:45 | 2023-04-27 04:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 89127 | 87807 |  |  |  | Thomas J K | N - - - |  | BMS
| CM-2023-12016356 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | FILTER DIRTY -AHU-A1154-004 |  | FM008 |  | 2023-07-28 13:01 | 2023-07-28 14:01 | 2023-07-29 14:01 | 24 | 2023-07-28 13:10 | 2023-07-28 18:15 | 305 | 440 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-12111221 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | RETURN FAN MOTOR FLEXIBLE CONNECTOR DAMAGED - TG-07A-14 |  | FM008 |  | 2023-08-24 15:57 | 2023-08-24 16:57 | 2023-08-25 16:57 | 24 | 2023-08-24 16:05 | 2023-08-24 18:45 | 160 | 320 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | RETURN FAN FAULTY | REPAIRED THE FAN | 105233 | 17053 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | Voice Communication
| CM-2023-12322706 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | UNUSUAL SOUND FROM BLOWER - AHU-A1154-004 – TG-07A-14 |  | FM008 |  | 2023-10-25 07:25 | 2023-10-25 08:25 | 2023-10-26 08:25 | 24 | 2023-10-25 07:30 | 2023-10-25 11:30 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 133396 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12325992 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | BLOWER PAINT FADED -FM1218 |  | FM008 |  | 2023-10-28 11:02 | 2023-10-28 12:02 | 2023-10-29 12:02 | 24 | 2023-10-28 11:10 | 2023-10-28 15:10 | 240 | 720 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | BLOWER DAMAGE | REPAIRED THE BLOWER | 95216 | 87807 |  |  | FM12184 | Bishwakarma, Mr. Narayan | N - - - |  | Voice Communication
| CM-2023-12390409 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU-A1154-004 – COOLING COIL DIRTY - TG-07A-14 |  | FM008 |  | 2023-11-19 16:07 | 2023-11-19 17:07 | 2023-11-20 17:07 | 24 | 2023-11-19 16:10 | 2023-11-19 18:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 105233 | 95217 |  |  | FM5385 | Sankar Yadav, Mr. Prem | N - - - |  | Voice Communication
| CM-2022-11081501 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | SUPPLY BELT IS DAMAGED |  | FM008 |  | 2022-10-09 07:35 | 2022-10-09 08:35 | 2022-10-10 08:35 | 24 | 2022-10-09 07:40 | 2022-10-09 09:10 | 90 | 180 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 95217 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-11801089 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS AHU-A1154-004; ASD-MTB-GFL07A-AHU178-FIL931 TG-07A-14 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1154.GNDP2.SBE01.AHU004.SYSALM.DP1 / May/17/2023 8:41:00 PM |  | FM008 |  | 2023-05-17 21:14 | 2023-05-17 22:14 | 2023-05-18 22:14 | 24 | 2023-05-17 21:20 | 2023-05-18 01:00 | 220 | 122 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2023-11885589 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | Supply Fan Fail Alarm Ahu-A1154-004 |  | FM008 |  | 2023-06-16 13:08 | 2023-06-16 14:08 | 2023-06-17 14:08 | 24 | 2023-06-16 13:15 | 2023-06-16 14:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | WARNING | AHU TRIP ALARM | RESET UNIT | 95216 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12097504 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | TUBE FOUNTAIN AREA WATER LEAKING FROM CEILING NEAR T3-QA1-96 |  | FM008 |  | 2023-08-17 00:23 | 2023-08-17 01:23 | 2023-08-18 01:23 | 24 | 2023-08-17 00:30 | 2023-08-19 15:00 | 3750 | 1265 | 8 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 106972 | 17053 |  |  | FM9647 | Basnet, Ms. Abhishek | N - - - | On-Hold-Access.APPROVAL TO ACCESS PENDING BY QA LOUNGES | Voice Communication
| CM-2023-12319761 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | DUCTING INSULATION DAMAGING: - AIR HANDLING UNIT 178-AIRSIDE-SADDLE BAG EAST-GROUND FLOOR AREA 07A |  | FM008 |  | 2023-10-24 08:49 | 2023-10-24 09:49 | 2023-10-25 09:49 | 24 | 2023-10-24 08:55 | 2023-10-24 17:30 | 515 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 138627 | 87807 |  |  | FM3122 | Moideenkoya, Mr. Vayalasseri | N - - - |  | Voice Communication
| CM-2023-12339128 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - TG-09-14 |  | FM008 |  | 2023-10-31 19:55 | 2023-10-31 20:55 | 2023-11-01 20:55 | 24 | 2023-10-31 20:00 | 2023-10-31 23:00 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 87807 |  |  | FM5553 | Mohamad Haneef Abdul Hameed, Mr. Majgaonkar | N - - - |  | Voice Communication
| CM-2023-12408839 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULT- (AHU-A1154-004) – DG 07A 14 |  | FM008 |  | 2023-11-24 08:11 | 2023-11-24 09:11 | 2023-11-25 09:11 | 24 | 2023-11-24 08:15 | 2023-11-24 15:15 | 420 | 305 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 132112 | 17053 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2024-12700309 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU-A1154-004 FILTER DIRTY TG-07A-14 |  | FM008 |  | 2024-03-06 10:09 | 2024-03-06 11:09 | 2024-03-07 11:09 | 24 | 2024-03-06 10:15 | 2024-03-06 12:15 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM0473 | Balan Nair, Mr. Sreejesh | N - - - |  | Voice Communication
| CM-2024-12709114 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU-A1154-004 TG-07A-14 COOLING COIL DIRTY |  | FM008 |  | 2024-03-08 10:26 | 2024-03-08 11:26 | 2024-03-09 11:26 | 24 | 2024-03-08 10:35 | 2024-03-08 13:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12341644 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1154-004 - MECHANICAL ROOM TG-07A-14 |  | FM008 |  | 2023-10-29 22:02 | 2023-10-29 23:02 | 2023-10-30 23:02 | 24 | 2023-10-29 22:10 | 2023-10-30 00:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17573 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2024-12692362 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED AHU-A1154-004 |  | FM008 |  | 2024-02-29 15:10 | 2024-02-29 16:10 | 2024-03-01 16:10 | 24 | 2024-02-29 15:15 | 2024-02-29 17:00 | 105 | 315 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106972 | 17053 |  |  | FM1183 | Hetaukar, Mr. Irfan Dawood | N - - - |  | Voice Communication
| CM-2022-10067357 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | RETURN AIR LOW ALARM AHU-A1154-004 TG-07A-14 |  | FM008 |  | 2022-01-20 14:19 | 2022-01-20 15:19 | 2022-01-21 15:19 | 24 | 2022-01-20 14:29 | 2022-01-20 15:58 | 89 | 178 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | DAMAGED | SENSOR DAMAGED | REPLACED/REPAIRED | 85125 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10194170 | ASD-MTB-GFL07A-AHU178 | AIR HANDLING UNIT-05 | AC TOO COLD - QA1 ENTIRE LOUNGE |  | FM008 |  | 2022-02-28 04:39 | 2022-02-28 05:39 | 2022-03-01 05:39 | 24 | 2022-02-28 04:48 | 2022-02-28 05:40 | 52 | 52 | 1 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 07A | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 87807 |  |  | 103886 | Hossain, Mr. Md Al-Ekram | N - - - |  | Voice Communication
| CM-2023-11784373 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | MOTOR ABNORMAL SOUND – AHU-E1192-1190-001 – MECHANICAL ROOM TG-23A-03 |  | FM008 |  | 2023-05-11 15:13 | 2023-05-11 16:13 | 2023-05-12 16:13 | 24 | 2023-05-11 15:20 | 2023-05-11 17:50 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 17053 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-12066080 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING, AHU-E1190-001, TG-23A-03 |  | FM008 |  | 2023-08-12 03:49 | 2023-08-12 04:49 | 2023-08-13 04:49 | 24 | 2023-08-12 03:55 | 2023-08-12 06:25 | 150 | 300 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 124475 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12198767 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2023-09-18 00:15 | 2023-09-18 01:15 | 2023-09-19 01:15 | 24 | 2023-09-18 00:20 | 2023-09-18 03:00 | 160 | 480 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12404393 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU BLOWER FRAME RUSTED,AHU-E1190-001,TG-23A-03 |  | FM008 |  | 2023-11-21 07:18 | 2023-11-21 08:18 | 2023-11-22 08:18 | 24 | 2023-11-21 07:20 | 2023-11-21 11:00 | 220 | 660 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 124475 | 87807 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-11128209 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU COIL DIRTY |  | FM008 |  | 2022-10-23 19:27 | 2022-10-23 20:27 | 2022-10-24 20:27 | 24 | 2022-10-23 19:35 | 2022-10-23 21:35 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-11158163 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU-E1190-001 GRILL DIRTY |  | FM008 |  | 2022-11-01 03:27 | 2022-11-01 04:27 | 2022-11-02 04:27 | 24 | 2022-11-01 03:30 | 2022-11-01 05:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-11403204 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -BUS PAVILION |  | FM008 |  | 2023-01-25 03:14 | 2023-01-25 04:14 | 2023-01-26 04:14 | 24 | 2023-01-25 03:20 | 2023-01-25 06:20 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-11478496 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU-E1190-001 COOLING COIL DIRTY - BUS PAVILION |  | FM008 |  | 2023-02-20 20:22 | 2023-02-20 21:22 | 2023-02-21 21:22 | 24 | 2023-02-20 20:25 | 2023-02-20 23:00 | 155 | 620 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 89127 | 17053 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12114424 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-08-23 19:02 | 2023-08-23 20:02 | 2023-08-24 20:02 | 24 | 2023-08-23 19:10 | 2023-08-23 22:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12405457 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU SUSPENSION SPRING RUSTY,AHU-E1190-001, TG-23A-03 |  | FM008 |  | 2023-11-22 14:52 | 2023-11-22 15:52 | 2023-11-23 15:52 | 24 | 2023-11-22 14:55 | 2023-11-22 17:30 | 155 | 275 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DAMAGED | SPRING ISOLATOR DAMAGED | REPLACED | 124475 | 87807 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-11167803 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU RETURN AIR GRILL DIRTY |  | FM008 |  | 2022-11-06 13:52 | 2022-11-06 14:52 | 2022-11-07 14:52 | 24 | 2022-11-06 13:55 | 2022-11-06 15:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2024-12597479 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY E1190-001 TG-23A-03 |  | FM008 |  | 2024-01-28 08:37 | 2024-01-28 09:37 | 2024-01-29 09:37 | 24 | 2024-01-28 08:45 | 2024-01-28 11:15 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 138627 | 17053 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10282656 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY – AHU-E1190-001 – TG-23A-03 |  | FM008 |  | 2022-03-27 00:10 | 2022-03-27 01:10 | 2022-03-28 01:10 | 24 | 2022-03-27 00:15 | 2022-03-27 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 55709 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-11697569 | LSD-BSP-GFL23A-AHU200 | AIR HANDLING UNIT-05 | AHU-E1190-001-COOLING COIL DIRTY |  | FM008 |  | 2023-04-22 19:41 | 2023-04-22 20:41 | 2023-04-23 20:41 | 24 | 2023-04-22 19:45 | 2023-04-22 23:45 | 240 | 480 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 23A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95217 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-10074703 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU COIL DIRTY - PUBLIC MOSQUE MECHANICAL ROOM - 05 |  | FM008 |  | 2022-01-24 21:38 | 2022-01-24 22:38 | 2022-01-25 22:38 | 24 | 2022-01-24 21:45 | 2022-01-24 23:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17053 | 55709 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2022-11117963 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU COIL DIRTY -AHU-A1300-001)-LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2022-10-22 19:22 | 2022-10-22 20:22 | 2022-10-23 20:22 | 24 | 2022-10-22 19:30 | 2022-10-22 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-11118314 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU-A1300-001 DUCT INSULATION DAMAGED |  | FM008 |  | 2022-10-23 08:00 | 2022-10-23 09:00 | 2022-10-24 09:00 | 24 | 2022-10-23 08:05 | 2022-10-23 09:05 | 60 | 180 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 89127 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2022-11190793 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AC IS TOO HOT -NOT WORKING -FEMALE SIDE UPSTAIRS -LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2022-11-15 14:15 | 2022-11-15 15:15 | 2022-11-16 15:15 | 24 | 2022-11-15 14:20 | 2022-11-15 15:50 | 90 | 35 | 1 | HVAC |  | Closed | Normal | BUILDING | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 87807 |  |  | 17770 | Anjum, Ms. Maha Jabeen | N - - - |  | Voice Communication
| CM-2023-11999906 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU-FILTER DIRTY AHU-A1300-001) |  | FM008 |  | 2023-07-22 20:29 | 2023-07-22 21:29 | 2023-07-23 21:29 | 24 | 2023-07-22 20:40 | 2023-07-22 23:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12423520 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AC VENTS NOISY - WOMEN'S PRAYER HALL))-LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-11-29 19:28 | 2023-11-29 20:28 | 2023-11-30 20:28 | 24 | 2023-11-29 19:35 | 2023-11-29 23:40 | 245 | 125 | 3 | HVAC |  | Closed | Normal | BUILDING | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 87807 |  |  | FM12904 | Saiyed, Mr. Mohemmed Arif Mohemmed Alam | N - - - |  | Voice Communication
| CM-2024-12609647 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | CHILL WATER SUPPLY LINE INSULATION DAMAGED – AHU-A1300-001 - PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2024-01-31 14:48 | 2024-01-31 15:48 | 2024-02-01 15:48 | 24 | 2024-01-31 14:55 | 2024-01-31 17:25 | 150 | 300 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17573 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2023-11398444 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU COOLING COIL DIRTY -PUBLIC MOSQUE |  | FM008 |  | 2023-01-23 21:58 | 2023-01-23 22:58 | 2023-01-24 22:58 | 24 | 2023-01-23 22:05 | 2023-01-24 01:30 | 205 | 615 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-11886807 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | FILTER DIRTY - AHU-A1300-001 – VCN PARKING C PUMP ROOM05 |  | FM008 |  | 2023-06-17 11:20 | 2023-06-17 12:20 | 2023-06-18 12:20 | 24 | 2023-06-17 11:30 | 2023-06-17 14:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 132112 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-12152805 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU BELT DAMAGED - AHU-A1300-001 - MECHANICAL ROOM 05 (PUBLIC MOSQUE) |  | FM008 |  | 2023-09-03 22:54 | 2023-09-03 23:54 | 2023-09-04 23:54 | 24 | 2023-09-03 22:58 | 2023-09-03 23:58 | 60 | 120 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-12188526 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | DUCT INSULATION DAMAGED-(TAG NO:AHU-A1300-001)-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-09-16 00:47 | 2023-09-16 01:47 | 2023-09-17 01:47 | 24 | 2023-09-16 00:50 | 2023-09-16 03:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17336 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-12409189 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | DUCT INSULATION DAMAGED |  | FM008 |  | 2023-11-25 14:01 | 2023-11-25 15:01 | 2023-11-26 15:01 | 24 | 2023-11-25 14:05 | 2023-11-25 16:35 | 150 | 450 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 95216 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2022-11162440 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | RETURN DUCT INSULATION DAMAGED - PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2022-11-06 09:21 | 2022-11-06 10:21 | 2022-11-07 10:21 | 24 | 2022-11-06 09:30 | 2022-11-06 11:30 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 121959 | 87807 |  |  | FM10798 | Manakkatthekkepurayil, Mr. Muhamed Sherif | N - - - |  | Voice Communication
| CM-2022-11208849 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU INSIDE LIGHT IS FUSED |  | FM008 |  | 2022-11-21 18:59 | 2022-11-21 19:59 | 2022-11-22 19:59 | 24 | 2022-11-21 19:08 | 2022-11-21 21:08 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68060 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2023-11694120 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | COOLING COIL DIRTY -AIR HANDLING UNIT 202 (TAG NO:AHU-A1300-001)-LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-04-23 19:35 | 2023-04-23 20:35 | 2023-04-24 20:35 | 24 | 2023-04-23 19:40 | 2023-04-23 22:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-11878929 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | A/C IS TOO HOT IN ENTIRE MOSQUE-BUILDING |  | FM008 |  | 2023-06-14 14:37 | 2023-06-14 15:37 | 2023-06-15 15:37 | 24 | 2023-06-14 14:45 | 2023-06-14 15:15 | 30 | 30 | 1 | HVAC |  | Closed | Normal | BUILDING | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68060 | 87807 |  |  | 60832 | El Mallaoui, Mr. Mohssine | N - - - |  | E-mail
| CM-2023-12407797 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU CABIN LIGHT FLEXIBLE CONNECTOR DAMAGED -05 PUBLIC MOSQUE |  | FM008 |  | 2023-11-24 01:36 | 2023-11-24 02:36 | 2023-11-25 02:36 | 24 | 2023-11-24 01:45 | 2023-11-24 04:30 | 165 | 330 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | COPEX CABLE DETARCHED/DAMAGED | RECTIFIED/REPLACED | 17333 | 17053 |  |  | FM8715 | Joriken Villondo Torino, | N - - - |  | Voice Communication
| CM-2023-12408738 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU COOLING COIL DIRTY - AIR HANDLING UNIT 202 (TAG NO:AHU-A1300-001)-LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-11-23 23:04 | 2023-11-24 00:04 | 2023-11-25 00:04 | 24 | 2023-11-23 23:10 | 2023-11-24 02:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 119320 | 17053 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2022-10031454 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | RETURN AIR DUCT ACCESS DOOR RUSTY – VCN PUBLIC MOSQUE C005 |  | FM008 |  | 2022-01-06 14:59 | 2022-01-06 15:59 | 2022-01-07 15:59 | 24 | 2022-01-06 15:05 | 2022-01-06 17:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10956435 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU-A1300-001 – RETURN DUCT INSULATION DAMAGED-- |  | FM008 |  | 2022-08-20 04:03 | 2022-08-20 05:03 | 2022-08-21 05:03 | 24 | 2022-08-20 04:10 | 2022-08-20 06:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 55709 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2022-11001161 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | COMMERCIAL CAR PARK C SLOT # C009 AC DUCT WATER LEAKAGE |  | FM008 |  | 2022-09-07 01:13 | 2022-09-07 02:13 | 2022-09-08 02:13 | 24 | 2022-09-07 01:20 | 2022-09-07 02:20 | 60 | 60 | 1 | HVAC |  | Closed | Normal | BUILDING | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 87807 |  |  | R12250 | Igbom, Mr. Fortunatus Chidozie | N - - - |  | Voice Communication
| CM-2023-11483078 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | COOLING COIL DIRTY - AHU-A1300-001 – VCN PUBLIC MOSQUE |  | FM008 |  | 2023-02-24 21:35 | 2023-02-24 22:35 | 2023-02-25 22:35 | 24 | 2023-02-24 21:45 | 2023-02-25 00:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12158601 | LSD-PMS-BUI-AHU202 | AIR HANDLING UNIT-01 | AHU FILTER DIRTY, AHU-A1300-001, PUMP ROOM -05 |  | FM008 |  | 2023-09-05 22:58 | 2023-09-05 23:58 | 2023-09-06 23:58 | 24 | 2023-09-05 23:10 | 2023-09-06 02:00 | 170 | 510 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 124475 | 87807 |  |  | FM10037 | CHETHAN | N - - - |  | Voice Communication
| CM-2022-10661468 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002 - AHU COIL DIRTY -STCP PUBLIC MOSQUE |  | FM008 |  | 2022-05-14 19:19 | 2022-05-14 20:19 | 2022-05-15 20:19 | 24 | 2022-05-14 19:25 | 2022-05-14 21:30 | 125 | 375 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 17053 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2022-10951902 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002-DRAIN LINE BLOCKED |  | FM008 |  | 2022-08-15 13:49 | 2022-08-15 14:49 | 2022-08-16 14:49 | 24 | 2022-08-15 13:55 | 2022-08-15 15:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 95217 | 55709 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-11210831 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | MARINE LIGHT FUSED |  | FM008 |  | 2022-11-21 21:44 | 2022-11-21 22:44 | 2022-11-22 22:44 | 24 | 2022-11-21 21:50 | 2022-11-21 23:50 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12115752 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | CHILLED WATER FAIL-ALARM - AHU-A1300-002 - PROJECT4.LOGICALVIEW:LOGICAL.BAC6.A1310.LVL001.DDC001.AHU002.FAILALARM.CHWFAIL / |  | FM008 |  | 2023-08-25 20:41 | 2023-08-25 21:41 | 2023-08-26 21:41 | 24 | 2023-08-25 20:50 | 2023-08-25 23:55 | 185 | 25 | 1 | HVAC |  | Closed | Normal | BUILDING | N | WARNING | OPERATIONAL ALARM | ACKNOWLEDGED/RECTIFIED | 133396 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | Y - - - |  | BMS
| CM-2023-12367882 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002 COOLING COIL DIRTY – LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-11-10 20:23 | 2023-11-10 21:23 | 2023-11-11 21:23 | 24 | 2023-11-10 20:30 | 2023-11-10 23:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 17053 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2024-12685281 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | DUCT INSOLATION DAMAGED,AHU-A1300-002, PUBLIC MOSQUE |  | FM008 |  | 2024-02-26 13:02 | 2024-02-26 14:02 | 2024-02-27 14:02 | 24 | 2024-02-26 13:10 | 2024-02-26 15:00 | 110 | 185 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM10798 | Manakkatthekkepurayil, Mr. Muhamed Sherif | N - - - |  | Voice Communication
| CM-2023-11459086 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU WEE BELT DAMAGED - AHU-A1300-002 - PUBLIC MOSQUE-BUILDING PARKING C AREA |  | FM008 |  | 2023-02-13 13:20 | 2023-02-13 14:20 | 2023-02-14 14:20 | 24 | 2023-02-13 13:25 | 2023-02-13 15:25 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17573 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2023-12198693 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002 FILTER DIRTY |  | FM008 |  | 2023-09-17 22:09 | 2023-09-17 23:09 | 2023-09-18 23:09 | 24 | 2023-09-17 22:15 | 2023-09-17 23:55 | 100 | 200 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-12202319 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU COOLING COIL DIRTY - AHU-A1300-002 – PARKING C, VCN, PUBLIC MOSQUE |  | FM008 |  | 2023-09-19 14:33 | 2023-09-19 15:33 | 2023-09-20 15:33 | 24 | 2023-09-19 14:40 | 2023-09-19 17:40 | 180 | 540 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-12280637 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU MOTOR BEARING NOISY - AIR HANDLING UNIT 203 (TAG NO:AHU-A1300-002)-LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-10-12 13:05 | 2023-10-12 14:05 | 2023-10-13 14:05 | 24 | 2023-10-12 13:15 | 2023-10-12 17:15 | 240 | 545 | 3 | HVAC |  | Closed | Normal | BUILDING | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 119320 | 87807 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-11072227 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002-AHU BELT DAMAGED |  | FM008 |  | 2022-10-03 22:24 | 2022-10-03 23:24 | 2022-10-04 23:24 | 24 | 2022-10-03 22:30 | 2022-10-03 23:30 | 60 | 180 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95217 | 55709 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2022-11149996 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002 DRAIN LINE INSULATION DAMAGED |  | FM008 |  | 2022-11-01 00:44 | 2022-11-01 01:44 | 2022-11-02 01:44 | 24 | 2022-11-01 00:50 | 2022-11-01 02:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-11372226 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002-AHU COOLING COIL DIRTY |  | FM008 |  | 2023-01-16 00:04 | 2023-01-16 01:04 | 2023-01-17 01:04 | 24 | 2023-01-16 00:10 | 2023-01-16 02:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95217 | 55709 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-11446819 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | COOLING COIL DIRTY -AHU-A1300-002)-LANDSIDE-PUBLIC MOSQUE-BUILDING |  | FM008 |  | 2023-02-10 20:15 | 2023-02-10 21:15 | 2023-02-11 21:15 | 24 | 2023-02-10 20:20 | 2023-02-10 23:20 | 180 | 720 | 4 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 17053 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2024-12623665 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | COOLING COIL DIRTY |  | FM008 |  | 2024-02-05 19:22 | 2024-02-05 20:22 | 2024-02-06 20:22 | 24 | 2024-02-05 19:30 | 2024-02-05 21:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95216 | 17053 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2024-12655624 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | CHILLED WATER SUPPLY LINE INSULATION DAMAGED - AHU-A1300-002 – VCN |  | FM008 |  | 2024-02-18 13:16 | 2024-02-18 14:16 | 2024-02-19 14:16 | 24 | 2024-02-18 13:20 | 2024-02-18 16:00 | 160 | 455 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 87807 |  |  | FM8604 | Nagoor Pichchai, Mr. Mansoor | N - - - |  | Voice Communication
| CM-2022-10862411 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | SUPPLY DUCT INSULATION DAMAGED -PUBLIC MOSQUE |  | FM008 |  | 2022-07-22 15:23 | 2022-07-22 16:23 | 2022-07-23 16:23 | 24 | 2022-07-22 15:30 | 2022-07-22 16:30 | 60 | 120 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17333 | 95217 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-11113907 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU COIL DIRTY -PUBLIC MOSQUE |  | FM008 |  | 2022-10-20 21:42 | 2022-10-20 22:42 | 2022-10-21 22:42 | 24 | 2022-10-20 21:45 | 2022-10-20 23:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-11624035 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AC VENTS DIRTY M2-210 FEMALE ABLUTION |  | FM008 |  | 2023-04-07 16:38 | 2023-04-07 17:38 | 2023-04-08 17:38 | 24 | 2023-04-07 16:45 | 2023-04-07 20:55 | 250 | 395 | 5 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | 118414 | Psuwura, Ms. Ingidzayi | N - - - |  | Voice Communication
| CM-2022-10122611 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | SUPPLY DUCT INSULATION DAMAGED - VCN,STCP MOSQUE BUILDING |  | FM008 |  | 2022-02-09 15:13 | 2022-02-09 16:13 | 2022-02-10 16:13 | 24 | 2022-02-09 15:20 | 2022-02-09 17:00 | 100 | 200 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 105233 | 55709 |  |  | FM8604 | Nagoor Pichchai, Mr. Mansoor | N - - - |  | Voice Communication
| CM-2022-10160458 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | AHU-A1300-002-AHU SUPPLY DUCT INSULATION DAMAGED |  | FM008 |  | 2022-02-21 19:35 | 2022-02-21 20:35 | 2022-02-22 20:35 | 24 | 2022-02-21 19:40 | 2022-02-21 21:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | BUILDING | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 55709 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10694410 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | PANEL FILTER ALARM – MECHANICAL ROOM 09 .PUBLIC MOSQUE |  | FM008 |  | 2022-05-25 09:02 | 2022-05-25 10:02 | 2022-05-26 10:02 | 24 | 2022-05-25 09:10 | 2022-05-25 11:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | BUILDING | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11459601 | LSD-PMS-BUI-AHU203 | AIR HANDLING UNIT-01 | ISOLATOR SWITCH NOT WORKING PROPERLY - AHU-A1300-002 MECHNICAL ROOM 09 PUBLIC MOSQUE |  | FM008 |  | 2023-02-14 10:05 | 2023-02-14 11:05 | 2023-02-15 11:05 | 24 | 2023-02-14 10:14 | 2023-02-14 12:12 | 118 | 236 | 2 | HVAC |  | Closed | Normal | BUILDING | N | NOT WORKING | CONTACTOR FAULTY | REPLACED THE CONTACTOR | 133396 | 95217 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11783154 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | TAXI PAVILION AC NOT WORKING/HOT |  | FM008 |  | 2023-05-10 12:29 | 2023-05-10 13:29 | 2023-05-11 13:29 | 24 | 2023-05-10 12:35 | 2023-05-10 16:40 | 245 | 40 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 89127 | 106972 |  |  | R12250 | Igbom, Mr. Fortunatus Chidozie | N - - - |  | Voice Communication
| CM-2023-12007804 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | FILTER DIRTY –TAXI PAVILION-GROUND FLOOR AREA |  | FM008 |  | 2023-07-26 19:23 | 2023-07-26 20:23 | 2023-07-27 20:23 | 24 | 2023-07-26 19:30 | 2023-07-26 22:00 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 17053 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2023-12116730 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - TAXI PAVILION AREA |  | FM008 |  | 2023-08-26 19:10 | 2023-08-26 20:10 | 2023-08-27 20:10 | 24 | 2023-08-26 19:15 | 2023-08-26 21:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 17053 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-12408915 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | TG-26A-02-AHU BLOWER FRAME RUSTY -AIR HANDLING UNIT 201 (TAG NO:AHU-E1192-001)-TAXI PAVILION-GROUND FLOOR AREA 26A |  | FM008 |  | 2023-11-24 13:50 | 2023-11-24 14:50 | 2023-11-25 14:50 | 24 | 2023-11-24 14:00 | 2023-11-24 17:00 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 17336 | 17053 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-11176114 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | RETUNE AIR GRILL IS DIRTY – AHU-E1192-001 – TAXI PAVILION-GROUND FLOOR AREA 26A |  | FM008 |  | 2022-11-08 14:50 | 2022-11-08 15:50 | 2022-11-09 15:50 | 24 | 2022-11-08 14:55 | 2022-11-08 16:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-11189510 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | INTAKE AIR DUCT ACCESS DOOR DAMAGED -AHU-E1192-001)-LANDSIDE-TAXI PAVILION-GROUND FLOOR AREA 26A |  | FM008 |  | 2022-11-13 15:36 | 2022-11-13 16:36 | 2022-11-14 16:36 | 24 | 2022-11-13 15:40 | 2022-11-13 17:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17336 | 87807 |  |  | FM10724 | Subburaj, Mr. Ganesan | N - - - |  | Voice Communication
| CM-2023-11785166 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU-E1192-001 – COIL DIRTY- |  | FM008 |  | 2023-05-11 02:25 | 2023-05-11 03:25 | 2023-05-12 03:25 | 24 | 2023-05-11 02:30 | 2023-05-11 05:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 94953 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-12199784 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AHU-A1192-001 – TAXI PAVILION TG-26-02 |  | FM008 |  | 2023-09-18 07:18 | 2023-09-18 08:18 | 2023-09-19 08:18 | 24 | 2023-09-18 07:25 | 2023-09-18 09:45 | 140 | 215 | 4 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106973 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2024-12748763 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - AIR HANDLING UNIT 201 (TAG NO:AHU-E1192-001)-LANDSIDE-TAXI PAVILION-GROUND FLOOR AREA 26A |  | FM008 |  | 2024-03-20 08:10 | 2024-03-20 09:10 | 2024-03-21 09:10 | 24 | 2024-03-20 08:15 | 2024-03-20 10:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 119320 | 17053 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2024-12772811 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | RETURN AIR GRILL DIRTY |  | FM008 |  | 2024-03-29 16:03 | 2024-03-29 17:03 | 2024-03-30 17:03 | 24 | 2024-03-29 16:10 | 2024-03-29 18:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2023-11974310 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AC TOO HOT TG-26A-11 |  | FM008 |  | 2023-07-14 18:16 | 2023-07-14 19:16 | 2023-07-15 19:16 | 24 | 2023-07-14 18:20 | 2023-07-14 20:00 | 100 | 60 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 68485 | 87807 |  |  | 17860 | Sahoo, Mr. Jitendra Kumar | N - - - |  | Voice Communication
| CM-2023-12278943 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU ABNORMAL NOISY – AHU -E1192-001 - MECHANICAL ROOM TG-26A-02 |  | FM008 |  | 2023-10-11 14:58 | 2023-10-11 15:58 | 2023-10-12 15:58 | 24 | 2023-10-11 15:10 | 2023-10-11 18:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10079477 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU COIL DIRTY |  | FM008 |  | 2022-01-25 22:52 | 2022-01-25 23:52 | 2022-01-26 23:52 | 24 | 2022-01-25 23:00 | 2022-01-26 01:00 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 68485 | 55709 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2022-10307265 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY AHU-E1192-001 TG-26A-02 |  | FM008 |  | 2022-03-28 19:07 | 2022-03-28 20:07 | 2022-03-29 20:07 | 24 | 2022-03-28 19:12 | 2022-03-28 21:12 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | COOLING COIL DIRTY | CLEANED | 85125 | 55709 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-10708628 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU AHU-E1192-001 BELT IS DAMAGED |  | FM008 |  | 2022-05-30 00:14 | 2022-05-30 01:14 | 2022-05-31 01:14 | 24 | 2022-05-30 00:20 | 2022-05-30 02:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 55709 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2022-11182135 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU INSIDE FLEXIBLE COPEX IS DAMAGED |  | FM008 |  | 2022-11-13 01:10 | 2022-11-13 02:10 | 2022-11-14 02:10 | 24 | 2022-11-13 01:15 | 2022-11-13 04:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DAMAGED | COPEX CABLE DETARCHED/DAMAGED | RECTIFIED/REPLACED | 68060 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10569191 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | SUPPLY GRILL DIRTY TG-26A-20 |  | FM008 |  | 2022-04-24 02:05 | 2022-04-24 03:05 | 2022-04-25 03:05 | 24 | 2022-04-24 02:10 | 2022-04-24 04:10 | 120 | 360 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68485 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2023-11403168 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU COOLING COIL DIRTY - AHU-E1192-001 – TG-26A-02 |  | FM008 |  | 2023-01-25 00:04 | 2023-01-25 01:04 | 2023-01-26 01:04 | 24 | 2023-01-25 00:10 | 2023-01-25 03:10 | 180 | 540 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-12140621 | LSD-TXP-GFL26A-AHU201 | AIR HANDLING UNIT-05 | AHU-E1192-001 SUPPLY AIR DUCT INSULATION DAMAGED TAXI PAVILION |  | FM008 |  | 2023-09-01 20:48 | 2023-09-01 21:48 | 2023-09-02 21:48 | 24 | 2023-09-01 20:55 | 2023-09-02 01:35 | 280 | 370 | 3 | HVAC |  | Closed | Normal | GROUND FLOOR AREA 26A | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 89127 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10085302 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 COOLING COIL DIRTY |  | FM008 |  | 2022-01-29 21:32 | 2022-01-29 22:32 | 2022-01-30 22:32 | 24 | 2022-01-29 21:40 | 2022-01-29 23:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 55709 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | BMS
| CM-2022-10310805 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101-COOLING COIL DIRTY-VCN AREA |  | FM008 |  | 2022-04-02 19:14 | 2022-04-02 20:14 | 2022-04-03 20:14 | 24 | 2022-04-02 19:20 | 2022-04-02 21:30 | 130 | 260 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 95217 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2022-11138878 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 – COIL DIRTY- - |  | FM008 |  | 2022-10-29 22:19 | 2022-10-29 23:19 | 2022-10-30 23:19 | 24 | 2022-10-29 22:25 | 2022-10-29 23:40 | 75 | 150 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 94953 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2022-11178241 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | PRESSURE DUCT INSULATION IS DAMAGED – AHU-A1180-101 – VCN, GROUND LEVEL |  | FM008 |  | 2022-11-09 16:01 | 2022-11-09 17:01 | 2022-11-10 17:01 | 24 | 2022-11-09 16:05 | 2022-11-09 18:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94954 | 87807 |  |  | FM10798 | Manakkatthekkepurayil, Mr. Muhamed Sherif | N - - - |  | Voice Communication
| CM-2022-11183280 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 – SUPPLY DUCT ACCESS DOOR AIR LEAKAGE |  | FM008 |  | 2022-11-13 11:07 | 2022-11-13 12:07 | 2022-11-14 12:07 | 24 | 2022-11-13 11:10 | 2022-11-13 13:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 94953 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-11777156 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | WATER LEAKING FROM THE MECHANICAL ROOM NO 108 |  | FM008 |  | 2023-05-08 13:43 | 2023-05-08 14:43 | 2023-05-09 14:43 | 24 | 2023-05-08 13:50 | 2023-05-08 17:45 | 235 | 250 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 106914 | 87807 |  |  | GSS9146 | Zakari | N - - - |  | Voice Communication
| CM-2023-11811092 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 FILTER IS DIRTY |  | FM008 |  | 2023-05-24 01:46 | 2023-05-24 02:46 | 2023-05-25 02:46 | 24 | 2023-05-24 01:50 | 2023-05-24 04:20 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-11918196 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS |  | FM008 |  | 2023-06-24 16:30 | 2023-06-24 17:30 | 2023-06-25 17:30 | 24 | 2023-06-24 16:40 | 2023-06-24 20:00 | 200 | 170 | 4 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68060 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12068550 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU CABIN LAMP NOT WORKING - AHU-A1180-101 – VCN EAST 108 |  | FM008 |  | 2023-08-12 18:55 | 2023-08-12 19:55 | 2023-08-13 19:55 | 24 | 2023-08-12 19:05 | 2023-08-12 21:35 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106973 | 87807 |  |  | FM11198 | Aamir Mallick Shakil Ahmad, Mr. | N - - - |  | BMS
| CM-2023-12084436 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | COIL DIRTY -LANDSIDE-VERTICAL CIRCULATION NODE-FIRST FLOOR |  | FM008 |  | 2023-08-14 04:12 | 2023-08-14 05:12 | 2023-08-15 05:12 | 24 | 2023-08-14 04:20 | 2023-08-14 06:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106914 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2024-12691184 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY |  | FM008 |  | 2024-03-01 11:21 | 2024-03-01 12:21 | 2024-03-02 12:21 | 24 | 2024-03-01 11:28 | 2024-03-01 14:00 | 152 | 304 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 106972 | 17053 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2023-11780185 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | DRAIN LINE BLOCKED- AHU-A1180-101- VCN 108 MECHNICAL ROOM (DUPLICATE COPY OF CM-2023-11777156) |  | FM008 |  | 2023-05-08 15:45 | 2023-05-08 16:45 | 2023-05-09 16:45 | 24 |  |  |  |  | 0 | HVAC |  | Cancelled | Normal | FIRST FLOOR | N | DAMAGED |  |  | 132112 | 95217 |  |  | FM10724 | Subburaj, Mr. Ganesan | N - - - | DUPLICATE CM WORK ORDER - MATAR FRC ERROR | Voice Communication
| CM-2023-11842398 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY,AHU-A1180-101,VCN, MECHANICAL ROOM -108 |  | FM008 |  | 2023-06-01 19:57 | 2023-06-01 20:57 | 2023-06-02 20:57 | 24 | 2023-06-01 20:05 | 2023-06-01 22:05 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 124475 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-11973068 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS//PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1180.1FLRP1.MTBE101.AHU001.SYSALM.DP1 / /MECHANICAL ROOM 108 (VCN EAST) |  | FM008 |  | 2023-07-12 17:15 | 2023-07-12 18:15 | 2023-07-13 18:15 | 24 | 2023-07-12 17:24 | 2023-07-12 22:00 | 276 | 546 | 4 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 105233 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12196459 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - VCN G/LVL MEC ROOM 108 |  | FM008 |  | 2023-09-17 14:44 | 2023-09-17 15:44 | 2023-09-18 15:44 | 24 | 2023-09-17 14:50 | 2023-09-17 17:30 | 160 | 480 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-12230351 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AC TOO HOT – VCN WEST GROUND LEVEL MOI TRAFFIC COUNTER |  | FM008 |  | 2023-09-28 10:10 | 2023-09-28 11:10 | 2023-09-29 11:10 | 24 | 2023-09-28 10:15 | 2023-09-28 11:15 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 132112 | 87807 |  |  | FM9754 | Macharia, Mr. John Gakuru | N - - - |  | Voice Communication
| CM-2023-12280024 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU MOTOR BEARING NOISY – VCN G/LEVEL |  | FM008 |  | 2023-10-12 23:01 | 2023-10-13 00:01 | 2023-10-14 00:01 | 24 | 2023-10-12 23:10 | 2023-10-13 02:40 | 210 | 420 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOISY | BEARING PROBLEM | REPLACED THE BEARING | 105233 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-11480341 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1180-101 – VCN MECHANICAL ROOM |  | FM008 |  | 2023-02-25 21:36 | 2023-02-25 22:36 | 2023-02-26 22:36 | 24 | 2023-02-25 21:40 | 2023-02-25 23:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-11588437 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101- DUCT INSULATION DAMAGED |  | FM008 |  | 2023-03-25 21:48 | 2023-03-25 22:48 | 2023-03-26 22:48 | 24 | 2023-03-25 21:55 | 2023-03-25 23:55 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 17154 | 94954 |  |  | FM8604 | Nagoor Pichchai, Mr. Mansoor | N - - - |  | Voice Communication
| CM-2023-12099079 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY, AHU-A1180-101, MECHANICAL ROOM 108 |  | FM008 |  | 2023-08-20 00:10 | 2023-08-20 01:10 | 2023-08-21 01:10 | 24 | 2023-08-20 00:15 | 2023-08-20 02:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 17053 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-12187211 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | DUCT INSULATION DAMAGED - AHU-A1180-101 – VCN MECHANICAL ROOM 108 |  | FM008 |  | 2023-09-14 03:05 | 2023-09-14 04:05 | 2023-09-15 04:05 | 24 | 2023-09-14 03:10 | 2023-09-14 05:40 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 106973 | 17053 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2024-12756269 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | COOLING COIL IS DIRTY |  | FM008 |  | 2024-03-23 19:30 | 2024-03-23 20:30 | 2024-03-24 20:30 | 24 | 2024-03-23 19:40 | 2024-03-23 21:40 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68060 | 17053 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2024-12834026 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY :AHU-A1180-101) |  | FM008 |  | 2024-04-20 22:08 | 2024-04-20 23:08 | 2024-04-21 23:08 | 24 | 2024-04-20 22:15 | 2024-04-20 23:55 | 100 | 300 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-12497070 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY; AHU-A1180-101 – VCN MEC ROOM 108 |  | FM008 |  | 2023-12-24 23:33 | 2023-12-25 00:33 | 2023-12-26 00:33 | 24 | 2023-12-24 23:40 | 2023-12-25 01:40 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10057742 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 INTACT AIR INSULATION DAMAGED V 108 |  | FM008 |  | 2022-01-16 14:03 | 2022-01-16 15:03 | 2022-01-17 15:03 | 24 | 2022-01-16 14:10 | 2022-01-16 16:10 | 120 | 355 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | AIR DUCT CANVASS DAMAGED | REPAIRED/REPLACED | 17154 | 55709 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10772126 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU COIL DIRTY – AHU-A1180-101 – VCN MECHANICAL ROOM 108 |  | FM008 |  | 2022-06-22 00:11 | 2022-06-22 01:11 | 2022-06-23 01:11 | 24 | 2022-06-22 00:15 | 2022-06-22 02:15 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 106973 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10777406 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AC IS TOO HOT -NOT WORKING-VCN CHECK IN ROW 11 AREA-VERTICAL CIRCULATION NODE-FIRST FLOOR |  | FM008 |  | 2022-06-25 16:29 | 2022-06-25 17:29 | 2022-06-26 17:29 | 24 | 2022-06-25 16:40 | 2022-06-25 17:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 17336 | 87807 |  |  | 38664 | Catana, Ms. Anna Francesca Yulo | N - - - |  | Voice Communication
| CM-2022-10951955 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU PRE FILTER IS DIRTY - AHU-A1180-101 - MECHANICAL ROOM 108 (VCN EAST) |  | FM008 |  | 2022-08-15 19:45 | 2022-08-15 20:45 | 2022-08-16 20:45 | 24 | 2022-08-15 19:50 | 2022-08-15 21:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17573 | 55709 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2022-10032056 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT ACCESS DOOR LEAKAGE |  | FM008 |  | 2022-01-07 16:27 | 2022-01-07 17:27 | 2022-01-08 17:27 | 24 | 2022-01-07 16:30 | 2022-01-07 17:30 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 68485 | 55709 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-10103906 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | FILTER IS DIRTY |  | FM008 |  | 2022-02-03 15:20 | 2022-02-03 16:20 | 2022-02-04 16:20 | 24 | 2022-02-03 15:25 | 2022-02-03 17:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | BMS
| CM-2022-10361546 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 DP1 FILTER ALARM |  | FM008 |  | 2022-04-12 17:21 | 2022-04-12 18:21 | 2022-04-13 18:21 | 24 | 2022-04-12 17:25 | 2022-04-12 20:00 | 155 | 190 | 4 | HVAC |  | Closed | Normal | FIRST FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10699570 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101- FITTER DIRTY – VCN- |  | FM008 |  | 2022-05-28 19:14 | 2022-05-28 20:14 | 2022-05-29 20:14 | 24 | 2022-05-28 19:20 | 2022-05-28 21:20 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-11404446 | LSD-VCN-FFL-AHU198 | AIR HANDLING UNIT-05 | AHU-A1180-101 COOLING COIL DIRTY |  | FM008 |  | 2023-01-28 22:34 | 2023-01-28 23:34 | 2023-01-29 23:34 | 24 | 2023-01-28 22:40 | 2023-01-29 01:10 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 68485 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-10062948 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU-A1180-102 - COIL DIRTY - VCN AREA MECHANICAL ROOM 109 |  | FM008 |  | 2022-01-17 19:13 | 2022-01-17 20:13 | 2022-01-18 20:13 | 24 | 2022-01-17 19:20 | 2022-01-17 21:20 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17053 | 55709 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2022-10729674 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AC NOT WORKING - CAR RENTAL AREA |  | FM008 |  | 2022-06-06 13:22 | 2022-06-06 14:22 | 2022-06-07 14:22 | 24 | 2022-06-06 13:30 | 2022-06-06 17:30 | 240 | 30 | 1 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 95216 | 17053 |  |  | CT11060 | BENON | N - - - |  | Voice Communication
| CM-2022-11177562 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | SUPPLY DUCT AIR ACCESS DOOR LEAKING - VCN |  | FM008 |  | 2022-11-10 16:56 | 2022-11-10 17:56 | 2022-11-11 17:56 | 24 | 2022-11-10 17:00 | 2022-11-10 18:45 | 105 | 315 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 17333 | 87807 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2022-11270714 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU-A1180-102- DRAIN LINE INSULATION DAMAGED |  | FM008 |  | 2022-12-14 08:20 | 2022-12-14 09:20 | 2022-12-15 09:20 | 24 | 2022-12-14 08:30 | 2022-12-14 11:25 | 175 | 525 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | DRAIN LINE DAMAGED | REPAIRED/REPLACED | 94953 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2023-11996916 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1180-102 – VCN GROUND FLOOR MECHANICAL ROOM V-109 |  | FM008 |  | 2023-07-18 19:14 | 2023-07-18 20:14 | 2023-07-19 20:14 | 24 | 2023-07-18 19:15 | 2023-07-18 21:55 | 160 | 480 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106973 | 87807 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2023-12380817 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY – AHU-A1180-102 – VCN GROUND FLOOR MECHANICAL ROOM 109 |  | FM008 |  | 2023-11-13 13:35 | 2023-11-13 14:35 | 2023-11-14 14:35 | 24 | 2023-11-13 13:40 | 2023-11-13 16:00 | 140 | 365 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2024-12603351 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -LANDSIDE-VERTICAL CIRCULATION NODE-FIRST FLOOR |  | FM008 |  | 2024-01-28 20:56 | 2024-01-28 21:56 | 2024-01-29 21:56 | 24 | 2024-01-28 21:02 | 2024-01-29 02:00 | 298 | 248 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-12115152 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU-A1180-102-FILTER DIRTY-VERTICAL CIRCULATION NODE-FIRST FLOOR |  | FM008 |  | 2023-08-25 20:49 | 2023-08-25 21:49 | 2023-08-26 21:49 | 24 | 2023-08-25 21:00 | 2023-08-25 23:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 77406 | 17053 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-12276963 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY-AIR HANDLING UNIT 199 (TAG NO:AHU-A1180-102) |  | FM008 |  | 2023-10-09 19:25 | 2023-10-09 20:25 | 2023-10-10 20:25 | 24 | 2023-10-09 19:30 | 2023-10-09 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17336 | 87807 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12378565 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU-A1180-102-AHU MOTOR NOISY |  | FM008 |  | 2023-11-16 23:19 | 2023-11-17 00:19 | 2023-11-18 00:19 | 24 | 2023-11-16 23:25 | 2023-11-17 02:25 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95217 | 87807 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-12407524 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | CHILLED WATER LINE PAINT FADED |  | FM008 |  | 2023-11-25 09:58 | 2023-11-25 10:58 | 2023-11-26 10:58 | 24 | 2023-11-25 10:00 | 2023-11-25 12:30 | 150 | 450 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | CHILLED WATER LINE INSULATION PAINT FADED | REPAINTED | 121959 | 17053 |  |  | FM8604 | Mr. Mansoor Nagoor Pichchai, | N - - - |  | Voice Communication
| CM-2022-11026271 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | RETURN AIR DUCT INSULATION DAMAGED |  | FM008 |  | 2022-09-17 16:57 | 2022-09-17 17:58 | 2022-09-18 17:58 | 24 | 2022-09-17 17:05 | 2022-09-17 18:35 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 95216 | 87807 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2022-11113682 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -V-109 |  | FM008 |  | 2022-10-19 21:42 | 2022-10-19 22:42 | 2022-10-20 22:42 | 24 | 2022-10-19 21:50 | 2022-10-19 23:50 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM3426 | Ahamed, Mr. Khadeer | N - - - |  | Voice Communication
| CM-2023-11367536 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU-A1180-102 – COOLING COIL DIRTY V-109 |  | FM008 |  | 2023-01-14 22:16 | 2023-01-14 23:16 | 2023-01-15 23:16 | 24 | 2023-01-14 22:30 | 2023-01-15 01:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17154 | 55709 |  |  | FM10724 | Ganesan Subburaj, Mr. | N - - - |  | Voice Communication
| CM-2023-11680853 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - VCN MECHANICAL ROOM #109 |  | FM008 |  | 2023-04-17 19:25 | 2023-04-17 20:25 | 2023-04-18 20:25 | 24 | 2023-04-17 19:30 | 2023-04-17 22:30 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 121959 | 87807 |  |  | FM4046 | Pitchai, Mr. Ajmalkhan Mohaideen | N - - - |  | Voice Communication
| CM-2023-12085456 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | COIL DIRTY ? AHU-A1180-102-VERTICAL CIRCULATION NODE-FIRST FLOOR(CM-2023-02-0688) |  | FM008 |  | 2023-08-14 02:10 | 2023-08-14 03:10 | 2023-08-15 03:10 | 24 | 2023-08-14 02:15 | 2023-08-14 03:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 87807 | 17053 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | - - - |  | Voice Communication
| CM-2024-12730543 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY -VCN-109 |  | FM008 |  | 2024-03-13 11:25 | 2024-03-13 12:25 | 2024-03-14 12:25 | 24 | 2024-03-13 11:30 | 2024-03-13 13:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 87807 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-10028402 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | SUPPLY AIR DUCT INSULATION DAMAGED ; AHU-A1180-102 – VCN,ROOM 109 |  | FM008 |  | 2022-01-05 17:58 | 2022-01-05 18:58 | 2022-01-06 18:58 | 24 | 2022-01-05 18:02 | 2022-01-05 18:55 | 53 | 106 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 55709 |  |  | FM1948 | Thomas Joju, Mr. Chiramal | N - - - |  | Voice Communication
| CM-2022-10262573 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY –MECHANICAL ROOM 109 |  | FM008 |  | 2022-03-19 21:39 | 2022-03-19 22:39 | 2022-03-20 22:39 | 24 | 2022-03-19 21:45 | 2022-03-19 23:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 87807 |  |  | FM10724 | Subburaj, Mr. Ganesan | N - - - |  | Voice Communication
| CM-2022-10122730 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | RETURN AIR DUCT ACCESS DOOR LEAKAGE AHU-A1180-102 |  | FM008 |  | 2022-02-10 04:16 | 2022-02-10 05:16 | 2022-02-11 05:16 | 24 | 2022-02-10 04:20 | 2022-02-10 05:45 | 85 | 170 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 55709 |  |  | FM10724 | Subburaj, Mr. Ganesan | N - - - |  | Voice Communication
| CM-2022-10752824 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AC TOO HOT VCN CHECKIN COUNTERS |  | FM008 |  | 2022-06-18 11:44 | 2022-06-18 12:44 | 2022-06-19 12:44 | 24 | 2022-06-18 11:45 | 2022-06-18 12:45 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68485 | 87807 |  |  | 117605 | Abbasi, Mr. Sher Afgan | N - - - |  | Voice Communication
| CM-2022-11161388 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | RETURN DUCT INSULATION DAMAGED – VCN,1ST FLOOR |  | FM008 |  | 2022-11-05 12:48 | 2022-11-05 13:48 | 2022-11-06 13:48 | 24 | 2022-11-05 12:55 | 2022-11-05 14:55 | 120 | 360 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 105233 | 87807 |  |  | FM10798 | Muhamed Sherif Manakkatthekkepurayil, Mr. | N - - - |  | Voice Communication
| CM-2023-11549848 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | COOLING COIL DIRTY - AHU-A1180-102 – MECHANICAL ROOM 109 (VCN EAST) |  | FM008 |  | 2023-03-11 20:28 | 2023-03-11 21:28 | 2023-03-12 21:28 | 24 | 2023-03-11 20:35 | 2023-03-11 23:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 17573 | 87807 |  |  | FM4035 | Pathan, Mr. Maqsood Khan | N - - - |  | Voice Communication
| CM-2023-12166478 | LSD-VCN-FFL-AHU199 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-09-09 20:26 | 2023-09-09 21:26 | 2023-09-10 21:26 | 24 | 2023-09-09 20:30 | 2023-09-09 23:30 | 180 | 540 | 3 | HVAC |  | Closed | Normal | FIRST FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10724 | Subburaj, Mr. Ganesan | N - - - |  | Voice Communication
| CM-2022-10085553 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006 DP3 FILTER ALARM |  | FM008 |  | 2022-01-30 07:25 | 2022-01-30 08:25 | 2022-01-31 08:25 | 24 | 2022-01-30 07:35 | 2022-01-30 09:20 | 105 | 140 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10242839 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006- BELT DAMAGED |  | FM008 |  | 2022-03-13 11:58 | 2022-03-13 12:58 | 2022-03-14 12:58 | 24 | 2022-03-13 12:07 | 2022-03-13 14:58 | 171 | 181 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 94953 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10613027 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006 DP3 FILTER ALARM BHS AREA NEAR BELT TX01-002 |  | FM008 |  | 2022-05-01 08:01 | 2022-05-01 09:01 | 2022-05-02 09:01 | 24 | 2022-05-01 08:10 | 2022-05-01 09:10 | 60 | 120 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10652554 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | BELT DAMAGED-AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2022-05-12 00:13 | 2022-05-12 01:13 | 2022-05-13 01:13 | 24 | 2022-05-12 00:20 | 2022-05-12 01:55 | 95 | 190 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11253329 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006- CHILLED WATER INSULATION DAMAGED-- |  | FM008 |  | 2022-12-07 08:19 | 2022-12-07 09:19 | 2022-12-08 09:19 | 24 | 2022-12-07 08:25 | 2022-12-07 11:45 | 200 | 400 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 94953 | 17053 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2023-11806324 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006 – DP1 FILTR ALARM |  | FM008 |  | 2023-05-19 00:36 | 2023-05-19 01:36 | 2023-05-20 01:36 | 24 | 2023-05-19 00:45 | 2023-05-19 04:45 | 240 | 125 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12013734 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | THERMOSTAT DISCONNECTED - AHU-A1110-006 – EAST BHS GROUND FLOOR NEAR BELT TX01002 |  | FM008 |  | 2023-07-26 16:55 | 2023-07-26 17:55 | 2023-07-27 17:55 | 24 | 2023-07-26 17:00 | 2023-07-26 18:13 | 73 | 91 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NO CONNECTION | BMS COMMUNICATION ERROR | RECTIFIED | 132112 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12083526 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM-PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU006.SYSALM.DP1 / GROUND FLOOR AREA 07 |  | FM008 |  | 2023-08-14 09:03 | 2023-08-14 10:03 | 2023-08-15 10:03 | 24 | 2023-08-14 09:10 | 2023-08-14 16:05 | 415 | 125 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - | ASSET CURRENTLY IN USE/OPERATION | BMS
| CM-2023-12162736 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006 COOLING COIL DIRTY |  | FM008 |  | 2023-09-06 07:09 | 2023-09-06 08:09 | 2023-09-07 08:09 | 24 | 2023-09-06 07:15 | 2023-09-06 10:15 | 180 | 540 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | COOLING COIL DIRTY | CLEANED | 68485 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12199744 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2023-09-18 03:40 | 2023-09-18 04:40 | 2023-09-19 04:40 | 24 | 2023-09-18 03:45 | 2023-09-18 15:30 | 705 | 365 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10914862 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 FILTER ALARM -NEAR BELT NO TX 01-002 |  | FM008 |  | 2022-08-06 07:00 | 2022-08-06 08:00 | 2022-08-07 08:00 | 24 | 2022-08-06 07:10 | 2022-08-06 08:40 | 90 | 270 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-11160134 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FILTER ALARM – AHU-A1110-006 - EAST BHS GROUND FLOOR NEAR BELT - TX-01-002 |  | FM008 |  | 2022-11-03 14:22 | 2022-11-03 15:22 | 2022-11-04 15:22 | 24 | 2022-11-03 14:30 | 2022-11-03 18:00 | 210 | 185 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 124475 | 87807 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11255602 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | WATER LEAKAGE FROM CEILING IN FRONT OF ARRIVAL IMMIGRATION LANE 12 COUNTER 24-25 & COUNTER 17-19 |  | FM008 |  | 2022-12-08 15:38 | 2022-12-08 16:08 | 2022-12-08 20:08 | 4 | 2022-12-08 15:45 | 2022-12-08 23:45 | 480 | 27 | 2 | MECHANICAL |  | Closed | Urgent | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 89127 | 17053 |  |  | T25580 | Mahadik, Mr. Yahya Mehboob | N - - - |  | Voice Communication
| CM-2023-11567683 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | WATER LEAKGE FROM AIR HANDLING UNIT PIPES - AHU-A1110-006 - NEAREST DOOR NUMBER (TG 07 01) |  | FM008 |  | 2023-03-16 08:56 | 2023-03-16 09:56 | 2023-03-17 09:56 | 24 | 2023-03-16 09:00 | 2023-03-16 11:55 | 175 | 525 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 133396 | 17053 |  |  | R15805 | Tariniganti, Mr. Santosh Kumar | N - - - |  | E-mail
| CM-2023-11898951 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM - MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2023-06-21 02:37 | 2023-06-21 03:37 | 2023-06-22 03:37 | 24 | 2023-06-21 02:45 | 2023-06-21 04:10 | 85 | 125 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 121959 | 133396 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11941917 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM - AHU-A1110-006 - GROUND FLOOR AREA 07 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU006.SYSALM.DP1 / |  | FM008 |  | 2023-07-04 00:21 | 2023-07-04 01:21 | 2023-07-05 01:21 | 24 | 2023-07-04 00:30 | 2023-07-04 05:10 | 280 | 125 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11999983 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 DUST FILTER STATUS - MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2023-07-23 06:27 | 2023-07-23 07:27 | 2023-07-24 07:27 | 24 | 2023-07-23 06:35 | 2023-07-23 08:15 | 100 | 230 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 121959 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12013040 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006 DP3 DUST FILTER STATUS |  | FM008 |  | 2023-07-28 17:37 | 2023-07-28 18:37 | 2023-07-29 18:37 | 24 | 2023-07-28 17:40 | 2023-07-28 21:35 | 235 | 275 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68485 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12043307 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | BELT DAMAGED-AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2023-08-04 09:40 | 2023-08-04 10:40 | 2023-08-05 10:40 | 24 | 2023-08-04 09:45 | 2023-08-04 10:45 | 60 | 180 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12044109 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FILTER ALARM - AHU-A1110-006 – EAST BHS GROUND FLOOR NEAR BELT TX-01-002 |  | FM008 |  | 2023-08-03 22:15 | 2023-08-03 23:15 | 2023-08-04 23:15 | 24 | 2023-08-03 22:20 | 2023-08-03 23:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2023-12132129 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM - AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2023-08-29 21:37 | 2023-08-29 22:37 | 2023-08-30 22:37 | 24 | 2023-08-29 21:45 | 2023-08-29 23:15 | 90 | 180 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 132112 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-12207072 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | HEAVY WATER LEAKAGE – (AHU-A1110-006) – TG 07 01 |  | FM008 |  | 2023-09-23 02:46 | 2023-09-23 03:16 | 2023-09-23 07:16 | 4 | 2023-09-23 02:50 | 2023-09-23 06:40 | 230 | 275 | 4 | HVAC |  | Closed | Urgent | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 132112 | 17053 |  |  | CBG159 | JOHN PETER | N - - - |  | Voice Communication
| CM-2023-12383701 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM - AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2023-11-15 06:32 | 2023-11-15 07:32 | 2023-11-16 07:32 | 24 | 2023-11-15 06:40 | 2023-11-15 15:40 | 540 | 185 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | BMS
| CM-2022-11115021 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006- DP1 FILTER ALARM -NEAR BELT TX-01-002 |  | FM008 |  | 2022-10-22 02:57 | 2022-10-22 03:57 | 2022-10-23 03:57 | 24 | 2022-10-22 03:05 | 2022-10-22 04:20 | 75 | 150 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 87807 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11220223 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FILTER ALARM - AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2022-11-27 08:48 | 2022-11-27 09:48 | 2022-11-28 09:48 | 24 | 2022-11-27 08:55 | 2022-11-27 12:30 | 215 | 185 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2022-11249582 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | FILTER ALARM - AHU-A1110-006 – BHS NEAR BELT TX01-002 |  | FM008 |  | 2022-12-05 10:05 | 2022-12-05 11:05 | 2022-12-06 11:05 | 24 | 2022-12-05 10:10 | 2022-12-05 16:45 | 395 | 126 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106973 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-11332898 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | FILTER DIRTY - AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 tx01-002 |  | FM008 |  | 2023-01-01 20:11 | 2023-01-01 21:11 | 2023-01-02 21:11 | 24 | 2023-01-01 20:15 | 2023-01-01 21:15 | 60 | 180 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11995266 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM, AHU-A1110-006,GROUND FLOOR AREA 07 |  | FM008 |  | 2023-07-20 00:20 | 2023-07-20 01:20 | 2023-07-21 01:20 | 24 | 2023-07-20 00:25 | 2023-07-20 04:10 | 225 | 465 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 124475 | 94954 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12162846 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | MOTOR BEARING NOISY |  | FM008 |  | 2023-09-06 13:43 | 2023-09-06 14:43 | 2023-09-07 14:43 | 24 | 2023-09-06 13:50 | 2023-09-06 18:35 | 285 | 855 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 106972 | 17053 |  |  | FM10649 | Khalasi, Mr. Dhanesh Arvindbhai | N - - - |  | Voice Communication
| CM-2024-12537016 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | SUPPLY BLOWER NOISY - TG-07-01 |  | FM008 |  | 2024-01-06 15:42 | 2024-01-06 16:42 | 2024-01-07 16:42 | 24 | 2024-01-06 15:50 | 2024-01-06 18:45 | 175 | 525 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | NOISY | VIBRATION DUE TO LOOSE PARTS OR BROKEN COMPONENTS | RECTIFIED | 105233 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12254517 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FINAL FILTER STATUS ALARM - AHU-A1110-006 - GROUND FLOOR AREA 07 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU006.SYSALM.DP1 / |  | FM008 |  | 2023-10-05 12:19 | 2023-10-05 13:19 | 2023-10-06 13:19 | 24 | 2023-10-05 12:25 | 2023-10-05 22:10 | 585 | 185 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106973 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10208044 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 FILTER ALARM AHU-A1110-006 BHS GROUND FLOOR NEAR BELT TX-01-02 |  | FM008 |  | 2022-03-01 11:19 | 2022-03-01 12:19 | 2022-03-02 12:19 | 24 | 2022-03-01 11:26 | 2022-03-01 12:56 | 90 | 180 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 85125 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10251408 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | FILTER IS DIRTY - AHU-A1110-006 – TG-07-04 |  | FM008 |  | 2022-03-14 08:09 | 2022-03-14 09:09 | 2022-03-15 09:09 | 24 | 2022-03-14 08:18 | 2022-03-14 10:30 | 132 | 190 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10275929 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP 3 FILTER ALARM -BHS GROUND FLOOR |  | FM008 |  | 2022-03-24 07:08 | 2022-03-24 08:08 | 2022-03-25 08:08 | 24 | 2022-03-24 07:15 | 2022-03-24 08:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17333 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10122921 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | V BELT CRECKED;AHU-A1110-006 - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-02-10 11:19 | 2022-02-10 12:19 | 2022-02-11 12:19 | 24 | 2022-02-10 11:28 | 2022-02-10 12:30 | 62 | 124 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 55709 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | E-mail
| CM-2022-10122923 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | FILTER IS DIRTY - EAST BHS GROUND FLOOR NEAR BELT TX01-002 |  | FM008 |  | 2022-02-10 11:22 | 2022-02-10 12:22 | 2022-02-11 12:22 | 24 | 2022-02-10 11:30 | 2022-02-10 13:30 | 120 | 125 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 105233 | 55709 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | E-mail
| CM-2022-10872050 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 FILTER ALARM |  | FM008 |  | 2022-07-26 20:16 | 2022-07-26 21:16 | 2022-07-27 21:16 | 24 | 2022-07-26 20:25 | 2022-07-26 23:40 | 195 | 230 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 87807 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10932623 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006- DP1 FILTER ALARM -EAST BHS GROUND NEAR BELT TX01-002 |  | FM008 |  | 2022-08-11 21:11 | 2022-08-11 22:12 | 2022-08-12 22:12 | 24 | 2022-08-11 21:16 | 2022-08-11 23:55 | 159 | 184 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 87807 | 55709 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11067361 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 FILTER ALARM |  | FM008 |  | 2022-10-01 09:25 | 2022-10-01 10:25 | 2022-10-02 10:25 | 24 | 2022-10-01 09:30 | 2022-10-01 11:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11135684 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP1 FILTER ALARM |  | FM008 |  | 2022-10-26 16:55 | 2022-10-26 17:55 | 2022-10-27 17:55 | 24 | 2022-10-26 17:04 | 2022-10-26 18:30 | 86 | 172 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10044853 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 DUST FILTER STATUS AHU-A1110-006 (ASD-MTB-GFL-AHU204) TG-07-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU006.SYSALM.DP3 / Jan/10/2022 12:40:25 AM |  | FM008 |  | 2022-01-10 03:17 | 2022-01-10 04:17 | 2022-01-11 04:17 | 24 | 2022-01-10 03:25 | 2022-01-10 08:00 | 275 | 130 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 94953 | 55709 |  |  | FM6385 | BRIONES, Ms. BRENDA | N - - - |  | BMS
| CM-2022-10331484 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 DUST FILTER STATUS;AIR HANDLING UNIT 204-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07;PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.GNDP3.MTB0701.AHU006.SYSALM.DP3 / |  | FM008 |  | 2022-04-07 10:01 | 2022-04-07 11:01 | 2022-04-08 11:01 | 24 | 2022-04-07 10:10 | 2022-04-07 18:30 | 500 | 130 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 105233 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10351753 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | SUPPLY V BELT DAMAGED- AHU-A1110-006-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2022-04-12 08:55 | 2022-04-12 09:55 | 2022-04-13 09:55 | 24 | 2022-04-12 09:05 | 2022-04-12 10:05 | 60 | 180 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 17053 |  |  | FM2852 | Rajesh, Mr. Ramakrishnan | N - - - |  | Voice Communication
| CM-2022-10694910 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 FILTER ALARM |  | FM008 |  | 2022-05-28 09:06 | 2022-05-28 10:06 | 2022-05-29 10:06 | 24 | 2022-05-28 09:15 | 2022-05-28 11:15 | 120 | 125 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 55709 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10731822 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU-A1110-006 SUPPLY FAN BELT DAMAGED TG-07-02 |  | FM008 |  | 2022-06-09 19:02 | 2022-06-09 20:02 | 2022-06-10 20:02 | 24 | 2022-06-09 19:10 | 2022-06-09 20:30 | 80 | 160 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10778373 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | WATER LEAKING FROM AHU IN TG-07-19 |  | FM008 |  | 2022-06-23 18:07 | 2022-06-23 19:07 | 2022-06-24 19:07 | 24 | 2022-06-23 18:10 | 2022-06-23 18:40 | 30 | 30 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 106914 | 87807 |  |  | 72521 | Apostol, Mr. Cloyd John Tesoro | N - - - |  | Voice Communication
| CM-2022-10781904 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 DUST FILTER STATUS AHU-A1110-006 |  | FM008 |  | 2022-06-27 14:44 | 2022-06-27 15:44 | 2022-06-28 15:44 | 24 | 2022-06-27 14:50 | 2022-06-27 18:00 | 190 | 65 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2022-10824816 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | DP3 FILTER ALARM TO AHU-A1110-006-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR AREA 07 |  | FM008 |  | 2022-07-08 07:11 | 2022-07-08 08:11 | 2022-07-09 08:11 | 24 | 2022-07-08 07:15 | 2022-07-08 08:45 | 90 | 270 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 95217 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11478429 | ASD-MTB-GFL-AHU204 | AIR HANDLING UNIT-01 | AHU FILTER DIRTY AND V BELT DAMAGED - BHS AREA - TG-07-04 |  | FM008 |  | 2023-02-21 22:46 | 2023-02-21 23:46 | 2023-02-22 23:46 | 24 | 2023-02-21 22:55 | 2023-02-22 01:00 | 125 | 250 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-MAIN TERMINAL BUILDING-GROUND FLOOR | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17053 | 87807 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2022-10121186 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | FILTER DIRTY-AIR HANDLING UNIT 0205-AIRSIDE-CONCOURSE B-BASEMENT AREA 17A |  | FM008 |  | 2022-02-09 12:30 | 2022-02-09 13:30 | 2022-02-10 13:30 | 24 | 2022-02-09 12:35 | 2022-02-09 15:35 | 180 | 360 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17336 | 55709 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10608041 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 FILTER ALARM -CONCOURSE B-BASEMENT AREA 17A |  | FM008 |  | 2022-05-03 22:02 | 2022-05-03 23:02 | 2022-05-04 23:02 | 24 | 2022-05-03 22:05 | 2022-05-03 23:55 | 110 | 220 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17336 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10710954 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | BB-17-04 AC NOT COOLING |  | FM008 |  | 2022-05-31 20:30 | 2022-05-31 21:30 | 2022-06-01 21:30 | 24 | 2022-05-31 20:35 | 2022-06-01 | 205 | 35 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | NOT WORKING | TOO HOT | ADJUSTED TEMPERATURE SETTING | 87807 | 55709 |  |  |  | ARNARAJ | N - - - |  | Voice Communication
| CM-2022-10992273 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 FILTER ALARM |  | FM008 |  | 2022-08-30 07:27 | 2022-08-30 08:27 | 2022-08-31 08:27 | 24 | 2022-08-30 07:35 | 2022-08-30 09:35 | 120 | 360 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11134700 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 DIRTY FILTER STATUS AIR HANDLING UNIT 0205-AIRSIDE-CONCOURSE B-BASEMENT AREA 17A |  | FM008 |  | 2022-10-25 22:42 | 2022-10-25 23:42 | 2022-10-26 23:42 | 24 | 2022-10-25 22:50 | 2022-10-26 05:10 | 380 | 540 | 5 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17154 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-11156413 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU FILTER IS DIRTY - C3114 AHU-A1157-K9-B02 - IBF EAST BASEMENT AREA 017A |  | FM008 |  | 2022-10-31 11:50 | 2022-10-31 12:50 | 2022-11-01 12:50 | 24 | 2022-10-31 11:55 | 2022-10-31 18:40 | 405 | 365 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11765513 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 DIRTY FILTER STATUS,PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.CONB.DDC001.AHUCHW.SYSALM.DP3 -AIR HANDLING UNIT 0205-AIRSIDE-CONCOURSE B-BASEMENT AREA 17A. |  | FM008 |  | 2023-05-06 14:30 | 2023-05-06 15:30 | 2023-05-07 15:30 | 24 | 2023-05-06 14:35 | 2023-05-06 16:00 | 85 | 85 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | WARNING | AHU TRIP ALARM | RESET UNIT | 77406 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | E-mail
| CM-2023-11901922 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 FINAL FILTER STATUS |  | FM008 |  | 2023-06-22 09:52 | 2023-06-22 10:52 | 2023-06-23 10:52 | 24 | 2023-06-22 10:00 | 2023-06-22 12:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 17573 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-11933865 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | FILTER DIRTY - AHU-A1157-K9-B02 |  | FM008 |  | 2023-06-30 08:08 | 2023-06-30 09:08 | 2023-07-01 09:08 | 24 | 2023-06-30 08:15 | 2023-06-30 11:15 | 180 | 360 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12012684 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | FILTER DIRTY -B-BASEMENT AREA 17A |  | FM008 |  | 2023-07-26 19:00 | 2023-07-26 20:00 | 2023-07-27 20:00 | 24 | 2023-07-26 19:05 | 2023-07-26 22:05 | 180 | 540 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2023-12322674 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | FILTER DIRTY-AIR HANDLING UNIT 0205-AIRSIDE-CONCOURSE B-BASEMENT AREA 17A |  | FM008 |  | 2023-10-25 00:08 | 2023-10-25 01:08 | 2023-10-26 01:08 | 24 | 2023-10-25 00:15 | 2023-10-25 03:15 | 180 | 260 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17336 | 87807 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11652780 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU FILTER FRAME MISALIGNED - AHU-A1157-K9-B02 – NEAR BB-17-02 |  | FM008 |  | 2023-04-12 10:48 | 2023-04-12 11:48 | 2023-04-13 11:48 | 24 | 2023-04-12 10:55 | 2023-04-12 13:55 | 180 | 540 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 106973 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12113155 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU FILTER DIRTY |  | FM008 |  | 2023-08-22 20:15 | 2023-08-22 21:15 | 2023-08-23 21:15 | 24 | 2023-08-22 20:20 | 2023-08-22 23:00 | 160 | 640 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 95216 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12308756 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AC TOO COLD -BB-17-12 |  | FM008 |  | 2023-10-23 00:32 | 2023-10-23 01:32 | 2023-10-24 01:32 | 24 | 2023-10-23 00:40 | 2023-10-23 02:00 | 80 | 65 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17333 | 87807 |  |  | R13122 | Ghani, Mr. Usman | N - - - |  | Voice Communication
| CM-2023-12429815 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | UNUSUAL SOUND FROM RETURN MOTOR -AIRSIDE-CONCOURSE B-BASEMENT AREA 17A |  | FM008 |  | 2023-12-02 14:27 | 2023-12-02 15:27 | 2023-12-03 15:27 | 24 | 2023-12-02 14:35 | 2023-12-02 17:35 | 180 | 720 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 106914 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11077822 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 DIRTY FILTER STATUS PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1157.CONB.DDC001.AHUCHW.SYSALM.DP3 / |  | FM008 |  | 2022-10-06 11:22 | 2022-10-06 12:22 | 2022-10-07 12:22 | 24 | 2022-10-06 11:30 | 2022-10-06 13:00 | 90 | 270 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2023-11625009 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AC IS TOO COLD-DOG SNIFFING AREA-BB-17-10-CONCOURSE B-BASEMENT AREA 017 |  | FM008 |  | 2023-04-08 11:31 | 2023-04-08 12:31 | 2023-04-09 12:31 | 24 | 2023-04-08 11:40 | 2023-04-08 12:40 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17336 | 17053 |  |  | MOI | ROHAN | N - - - |  | Voice Communication
| CM-2023-11652778 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU FILTER FRAME MISALIGNED |  | FM008 |  | 2023-04-12 10:39 | 2023-04-12 11:39 | 2023-04-13 11:39 | 24 | 2023-04-12 10:45 | 2023-04-12 13:45 | 180 | 540 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 87807 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11786203 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-12 19:15 | 2023-05-12 20:15 | 2023-05-13 20:15 | 24 | 2023-05-12 19:25 | 2023-05-12 21:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2024-12825169 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | FILTER DIRTY AHU-A1157-K9-B02 |  | FM008 |  | 2024-04-13 00:06 | 2024-04-13 01:06 | 2024-04-14 01:06 | 24 | 2024-04-13 00:10 | 2024-04-13 02:25 | 135 | 405 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106972 | 87807 |  |  | FM11837 | Md Zafar Iqbal Ansari, Mr. | N - - - |  | Voice Communication
| CM-2023-12428692 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | SUPPLY MOTOR ABNORMAL SOUND |  | FM008 |  | 2023-12-02 09:34 | 2023-12-02 10:34 | 2023-12-03 10:34 | 24 | 2023-12-02 09:40 | 2023-12-02 13:40 | 240 | 960 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | BEARING DAMAGE | REPLACED THE BEARING | 17333 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2024-12769582 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU FILTER DIRTY - AHU-A1157-K9-B02 - BB-17-01 |  | FM008 |  | 2024-03-27 21:18 | 2024-03-27 22:18 | 2024-03-28 22:18 | 24 | 2024-03-27 21:25 | 2024-03-27 23:25 | 120 | 360 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 133396 | 95217 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2024-12851305 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | HEAVY WATER LEAKAGE FROM AC CHILLING UNIT NEAR BB-17-02 |  | FM008 |  | 2024-04-27 13:02 | 2024-04-27 13:32 | 2024-04-27 17:32 | 4 | 2024-04-27 13:10 | 2024-04-27 14:30 | 80 | 240 | 3 | HVAC |  | Closed | Urgent | HAMAD INTERNATIONAL AIRPORT | N | WATER LEAKAGE | LEAK DUE TO CONDENSATION | RECTIFIED | 133396 | 87807 |  |  | 126689 | Rajkumar, Mr. Vinothkumar | N - - - |  | Voice Communication
| CM-2022-10121090 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | AHU-A1157-K9-B02 - FLEXIBLE CABLE CONNECTOR IS DAMAGED – BIF BB-01-17A |  | FM008 |  | 2022-02-09 08:45 | 2022-02-09 09:45 | 2022-02-10 09:45 | 24 | 2022-02-09 08:55 | 2022-02-09 10:24 | 89 | 178 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 17573 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | Voice Communication
| CM-2022-10170101 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 DIRTY FILTER STATUS AHU-A1157-K9-B02 IBF EAST ROOM NO: BB-17-07 |  | FM008 |  | 2022-02-23 11:10 | 2022-02-23 12:10 | 2022-02-24 12:10 | 24 | 2022-02-23 11:16 | 2022-02-23 15:10 | 234 | 244 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 89127 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10368629 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | DP3 FILTER ALARM -IBF BASEMENT AREA 017A |  | FM008 |  | 2022-04-17 06:35 | 2022-04-17 07:35 | 2022-04-18 07:35 | 24 | 2022-04-17 06:45 | 2022-04-17 08:30 | 105 | 180 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | BLOCKED | DRAIN CLOGGED | CLEANED THE DRAIN | 17333 | 17053 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2022-10237679 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | FILTER DIRTY |  | FM008 |  | 2022-03-12 14:37 | 2022-03-12 15:37 | 2022-03-13 15:37 | 24 | 2022-03-12 14:45 | 2022-03-12 16:45 | 120 | 360 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM5373 | MURUGAN PAKSHI RAJAN, | N - - - |  | Voice Communication
| CM-2023-11639535 | ASD-COB-BAS17A-AHU205 | AIR HANDLING UNIT-04 | BELT DAMAGED - AHU-A1157-K9-B02 – BB-17A |  | FM008 |  | 2023-04-09 12:17 | 2023-04-09 13:17 | 2023-04-10 13:17 | 24 | 2023-04-09 12:25 | 2023-04-09 18:30 | 365 | 325 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 133396 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10141140 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | PULLY MISALIGNED-AHU-A1110-450-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-02-14 08:42 | 2022-02-14 09:42 | 2022-02-15 09:42 | 24 | 2022-02-14 08:50 | 2022-02-14 10:00 | 70 | 210 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ACCIDENT DUE TO MISHANDLING | REPLACED/REPAIRED | 106914 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11276350 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2022-12-17 09:45 | 2022-12-17 10:45 | 2022-12-18 10:45 | 24 | 2022-12-17 09:55 | 2022-12-17 11:50 | 115 | 345 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11824183 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY |  | FM008 |  | 2023-05-26 10:39 | 2023-05-26 11:39 | 2023-05-27 11:39 | 24 | 2023-05-26 10:45 | 2023-05-26 17:05 | 380 | 277 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 121959 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12179955 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | DP2 DUST FILTER STATUS |  | FM008 |  | 2023-09-11 14:23 | 2023-09-11 15:23 | 2023-09-12 15:23 | 24 | 2023-09-11 14:30 | 2023-09-11 20:00 | 330 | 187 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 17333 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2022-11064527 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU-A1110-450- DP3 FILTER DIRTY T4-08-04 |  | FM008 |  | 2022-09-29 00:06 | 2022-09-29 01:06 | 2022-09-30 01:06 | 24 | 2022-09-29 00:10 | 2022-09-29 03:20 | 190 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 87807 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-11103146 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU-A1110-450 BELT DAMAGED |  | FM008 |  | 2022-10-16 07:28 | 2022-10-16 08:28 | 2022-10-17 08:28 | 24 | 2022-10-16 07:35 | 2022-10-16 10:10 | 155 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 55709 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-12462052 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | V BELT DAMAGED |  | FM008 |  | 2023-12-11 20:37 | 2023-12-11 21:37 | 2023-12-12 21:37 | 24 | 2023-12-11 20:45 | 2023-12-11 23:50 | 185 | 275 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2022-10966111 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU-A1110-450-CONDENSATE DRAIN LINE INSULATION DAMAGED |  | FM008 |  | 2022-08-23 07:44 | 2022-08-23 08:44 | 2022-08-24 08:44 | 24 | 2022-08-23 07:50 | 2022-08-23 09:00 | 70 | 140 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 95217 | 55709 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2022-11276153 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU BELT IS DAMAGED |  | FM008 |  | 2022-12-16 08:26 | 2022-12-16 09:26 | 2022-12-17 09:26 | 24 | 2022-12-16 08:30 | 2022-12-16 11:00 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 121959 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11973742 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU-A1110-450 BELT DAMAGED T4-08-04 |  | FM008 |  | 2023-07-15 00:09 | 2023-07-15 01:09 | 2023-07-16 01:09 | 24 | 2023-07-15 00:16 | 2023-07-15 04:10 | 234 | 246 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10569001 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU-A1110-450 T4-08-04 FILTER DIRTY |  | FM008 |  | 2022-04-22 19:12 | 2022-04-22 20:12 | 2022-04-23 20:12 | 24 | 2022-04-22 19:20 | 2022-04-22 21:10 | 110 | 220 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10569036 | ASD-MTB-FOF008-AHU207 | AIR HANDLING UNIT-05 | AHU-A1110-450 SUPPLY BELT DAMAGED T4-08-04 |  | FM008 |  | 2022-04-23 00:05 | 2022-04-23 01:05 | 2022-04-24 01:05 | 24 | 2022-04-23 00:10 | 2022-04-23 01:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 89127 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10147593 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AM5 MALE WASHROOM – AC NOT COOLING/WASHROOM TOO HOT |  | FM008 |  | 2022-02-20 06:49 | 2022-02-20 07:49 | 2022-02-21 07:49 | 24 | 2022-02-20 07:00 | 2022-02-20 08:00 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | NOT WORKING | TEMP HOT IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 106976 | 55709 |  |  | FM7799 | Mugambi, Mr. Antony Mutwiri | N - - - |  | Voice Communication
| CM-2023-11912108 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | DP1 FINAL FILTER STATUS -T1-09A-41 |  | FM008 |  | 2023-06-22 09:52 | 2023-06-22 10:52 | 2023-06-23 10:52 | 24 | 2023-06-22 10:00 | 2023-06-22 12:00 | 120 | 240 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 17333 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12134154 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | FILTER DIRTY – (AHU-A1154-101) – T1 09A 41 |  | FM008 |  | 2023-08-30 19:41 | 2023-08-30 20:42 | 2023-08-31 20:42 | 24 | 2023-08-30 19:50 | 2023-08-30 22:50 | 180 | 540 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 132112 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12202609 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | FILTER DIRTY - AHU-A1154-101 – T1-09A-41 |  | FM008 |  | 2023-09-20 16:11 | 2023-09-20 17:11 | 2023-09-21 17:11 | 24 | 2023-09-20 16:15 | 2023-09-20 18:45 | 150 | 450 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 87807 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12422169 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AHU-A1154-101 AM5 FILTER DIRTY |  | FM008 |  | 2023-11-27 19:16 | 2023-11-27 20:16 | 2023-11-28 20:16 | 24 | 2023-11-27 19:25 | 2023-11-27 21:00 | 95 | 190 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12515764 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | DUCT INSOLATION DAMAGED, AHU-A1154-101, T1-09A-41 |  | FM008 |  | 2023-12-31 07:54 | 2023-12-31 08:54 | 2024-01-01 08:54 | 24 | 2023-12-31 08:00 | 2023-12-31 11:45 | 225 | 365 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 124475 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-11247671 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AC TOO COLD - AM5 ENTIRE AREA |  | FM008 |  | 2022-12-04 21:45 | 2022-12-04 22:45 | 2022-12-05 22:45 | 24 | 2022-12-04 21:50 | 2022-12-04 22:50 | 60 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | NOT WORKING | TOO COLD | ADJUSTED TEMPERATURE SETTING | 17573 | 17053 |  |  | 100072 | Singh, Mr. Kuldeep | N - - - |  | Voice Communication
| CM-2023-12018244 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AHU-A1154-101 AHU FILTER DIRTY AM5 |  | FM008 |  | 2023-07-29 19:48 | 2023-07-29 20:48 | 2023-07-30 20:48 | 24 | 2023-07-29 19:55 | 2023-07-29 22:55 | 180 | 360 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 87807 | 17053 |  |  | FM11766 | Mohammad Tajeem, Mr. | N - - - |  | Voice Communication
| CM-2023-12130178 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | LIGHTING SWITCH DAMAGED |  | FM008 |  | 2023-08-30 03:47 | 2023-08-30 04:47 | 2023-08-31 04:47 | 24 | 2023-08-30 03:55 | 2023-08-30 06:40 | 165 | 330 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | PARTS DAMAGED | REPLACED/REPAIRED THE PARTS | 95216 | 17053 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2023-12232707 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER DIRTY - AIR HANDLING UNIT01-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE (AM5) |  | FM008 |  | 2023-09-29 20:28 | 2023-09-29 21:28 | 2023-09-30 21:28 | 24 | 2023-09-29 20:35 | 2023-09-29 23:00 | 145 | 290 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 119320 | 87807 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2023-12513523 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AHU-A1154-101 FILTER DIRTY T1-09A-41 |  | FM008 |  | 2023-12-30 01:06 | 2023-12-30 02:06 | 2023-12-31 02:06 | 24 | 2023-12-30 01:10 | 2023-12-30 05:00 | 230 | 365 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 138627 | 17053 |  |  | FM11937 | Kabui, Mr. Albert | N - - - |  | Voice Communication
| CM-2024-12768072 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | Water leakage from fresh air handling unit FAHU-A1154-101 at T1-09A-41 |  | FM008 |  | 2024-03-25 14:26 | 2024-03-25 15:26 | 2024-03-26 15:26 | 24 | 2024-03-25 14:35 | 2024-03-25 18:20 | 225 | 125 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | LEAKAGE | AIR LEAKAGE | REPAIRED AND FIXED | 89127 | 17053 |  |  | 63817 | Ntale, Mr. Henry | N - - - |  | E-mail
| CM-2024-12850023 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AHU FILTER IS DIRTY |  | FM008 |  | 2024-04-25 00:03 | 2024-04-25 01:03 | 2024-04-26 01:03 | 24 | 2024-04-25 00:10 | 2024-04-25 02:10 | 120 | 240 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 17053 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2022-11267335 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AC TOO COLD - AM5 ENTIRE AREA |  | FM008 |  | 2022-12-13 05:15 | 2022-12-13 06:15 | 2022-12-14 06:15 | 24 | 2022-12-13 05:20 | 2022-12-13 06:00 | 40 | 40 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 17573 | 17053 |  |  | 103922 | Istiak, Mr. Shamim | N - - - |  | Voice Communication
| CM-2023-12205182 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | SUPPLY AIR HUMIDITY HI LEVEL ALARM - AIR HANDLING UNIT01-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE (AM5) |  | FM008 |  | 2023-09-20 12:01 | 2023-09-20 13:01 | 2023-09-21 13:01 | 24 | 2023-09-20 12:10 | 2023-09-20 18:05 | 355 | 710 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | NOT WORKING | AHU SHUTDOWN DUE TO FIRE ALARM ACTIVATION | RESET UNIT | 106914 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2024-12770948 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | AHU-A1154-101 FILTER DIRTY T1-09A-41 |  | FM008 |  | 2024-03-25 02:45 | 2024-03-25 03:45 | 2024-03-26 03:45 | 24 | 2024-03-25 02:50 | 2024-03-25 05:15 | 145 | 245 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1218 | Manappurath Parambil Haneefa, Mr. Faisal | N - - - |  | Voice Communication
| CM-2022-10343970 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-04-10 07:38 | 2022-04-10 08:38 | 2022-04-11 08:38 | 24 | 2022-04-10 07:47 | 2022-04-10 18:09 | 622 | 123 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 95216 | 17053 |  |  | FM7343 | Azad Hussain Ansari, | N - - - |  | Voice Communication
| CM-2022-10325970 | ASD-COB-AM5-AHU01 | AIR HANDLING UNIT-05 | T1-09A-41 FILTER DIRTY |  | FM008 |  | 2022-04-05 10:03 | 2022-04-05 11:03 | 2022-04-06 11:03 | 24 | 2022-04-05 10:10 | 2022-04-05 12:00 | 110 | 220 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-11526716 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | IN FAHU-A1154-101, DUCT INSULATION DAMAGED AT DIFFERENT LOCATION AM5 : MECHANICAL ROOM (T1-09A-41) |  | FM008 |  | 2023-03-07 15:53 | 2023-03-07 16:53 | 2023-03-08 16:53 | 24 | 2023-03-07 16:00 | 2023-03-07 22:40 | 400 | 185 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DAMAGED | INSULATION DAMAGED | REPLACED/REPAIRED | 68485 | 95217 |  |  | 79794 | Naseer, Mr. Tahir | N - - - |  | E-mail
| CM-2023-12134155 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | FILTER DIRTY – (FAHU-A1154-101) – T1 09A 41 |  | FM008 |  | 2023-08-30 19:44 | 2023-08-30 20:44 | 2023-08-31 20:44 | 24 | 2023-08-30 19:50 | 2023-08-31 00:55 | 305 | 365 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 132112 | 17053 |  |  | FM5373 | Pakshi Rajan, Mr. Murugan | N - - - |  | Voice Communication
| CM-2023-12422170 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | FAHU-A1154-101 AM5 FILTER DIRTY |  | FM008 |  | 2023-11-27 19:17 | 2023-11-27 20:17 | 2023-11-28 20:17 | 24 | 2023-11-27 19:25 | 2023-11-27 22:00 | 155 | 125 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 89127 | 95217 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11077723 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | FILTER DIRTY |  | FM008 |  | 2022-10-05 20:57 | 2022-10-05 21:57 | 2022-10-06 21:57 | 24 | 2022-10-05 21:05 | 2022-10-05 23:05 | 120 | 360 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 95216 | 87807 |  |  | FM5385 | Mr. Prem Sankar Yadav, | N - - - |  | Voice Communication
| CM-2023-11350585 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | WATER DRIPPING FROM AC |  | FM008 |  | 2023-01-07 10:46 | 2023-01-07 11:46 | 2023-01-08 11:46 | 24 | 2023-01-07 10:50 | 2023-01-07 13:50 | 180 | 720 | 4 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | WATER LEAKAGE | BLOCKED DRAIN LINE | CLEANED DRAIN LINE | 95216 | 17053 |  |  | 17904 | Mohammed Esa, Mr. Kamil Basha | N - - - |  | Voice Communication
| CM-2022-10325976 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | AIR FILTER DIRTY |  | FM008 |  | 2022-04-05 10:13 | 2022-04-05 11:13 | 2022-04-06 11:13 | 24 | 2022-04-05 10:20 | 2022-04-05 17:00 | 400 | 130 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106972 | 17053 |  |  | FM0018 | Hoda Baig, Mr. Shamsul | N - - - |  | Voice Communication
| CM-2023-12134561 | ASD-COB-AM5-AHU02 | AIR HANDLING UNIT-05 | CABIN LAMP NOT WORKING -FRESH AIR HANDLING UNIT |  | FM008 |  | 2023-08-31 03:31 | 2023-08-31 04:31 | 2023-09-01 04:31 | 24 | 2023-08-31 03:40 | 2023-08-31 06:40 | 180 | 360 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE B-AL MAHA LOUNGE 5 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17336 | 17053 |  |  | FM7367 | Mr. Eugene Velasco Advincula, | N - - - |  | Voice Communication
| CM-2023-11823219 | ASD-COA-FFL1-AHU101 | AIR HANDLING UNIT-05 | AHU-A1153-101 DP3 DUST FILTER STATUS T1-08A-08 |  | FM008 |  | 2023-05-25 16:21 | 2023-05-25 17:21 | 2023-05-26 17:21 | 24 | 2023-05-25 16:28 | 2023-05-25 21:10 | 282 | 247 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 1 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2024-12632278 | ASD-COA-FFL1-AHU101 | AIR HANDLING UNIT-05 | A/C IS TOO COLD AT RECEPTION |  | FM008 |  | 2024-02-07 20:08 | 2024-02-07 21:08 | 2024-02-08 21:08 | 24 | 2024-02-07 20:15 | 2024-02-07 21:30 | 75 | 60 | 1 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 1 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 77496 | Falul, Mrs. Fathima Shazra | N - - - |  | Voice Communication
| CM-2024-12651705 | ASD-COA-FFL1-AHU101 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS MECHANICAL ROOM T1-08A-08 |  | FM008 |  | 2024-02-15 18:31 | 2024-02-15 19:31 | 2024-02-16 19:31 | 24 | 2024-02-15 18:40 | 2024-02-15 20:00 | 80 | 115 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 1 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 106972 | 95217 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-11269166 | ASD-COA-FFL1-AHU101 | AIR HANDLING UNIT-05 | A/C IS TOO COLD IN FREQUENT FLYER LOUNGE 1 |  | FM008 |  | 2022-12-12 11:04 | 2022-12-12 12:04 | 2022-12-13 12:04 | 24 | 2022-12-12 11:12 | 2022-12-12 12:10 | 58 | 116 | 2 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 1 | N | NOT WORKING | TEMP COLD IN SERVING AREA | ADJUSTED THE TEMPERATURE SETPOINT | 68060 | 17053 |  |  | 103886 | Hossain, Mr. Md Al-Ekram | N - - - |  | Voice Communication
| CM-2023-11581545 | ASD-COA-FFL1-AHU101 | AIR HANDLING UNIT-05 | DP3 DUST FILTER STATUS-PROJECT8.LOGICALVIEW:LOGICAL.MTCONALP.A1153.1STFLRP1.DDC001.AHU101.SYSALM.DP3 / -T1-08A-08 |  | FM008 |  | 2023-03-20 17:41 | 2023-03-20 18:41 | 2023-03-21 18:41 | 24 | 2023-03-20 17:50 | 2023-03-20 22:30 | 280 | 165 | 3 | HVAC |  | Closed | Normal | HAMAD INTERNATIONAL AIRPORT-AIRSIDE-CONCOURSE A-FREQUENT FLYER LOUNGE 1 | N | NOT WORKING | BLOCKAGE OF AIR FLOW | REPAIR/REPLACE | 106914 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10085559 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FAHU-A1110-HTR-401 DP2 FILTER ALARM |  | FM008 |  | 2022-01-30 07:41 | 2022-01-30 08:41 | 2022-01-31 08:41 | 24 | 2022-01-30 07:50 | 2022-01-30 10:30 | 160 | 179 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68485 | 55709 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | Voice Communication
| CM-2022-10224554 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU206 – BELT DAMAGED & LIGHT NOT WORKING |  | FM008 |  | 2022-03-09 07:17 | 2022-03-09 08:17 | 2022-03-10 08:17 | 24 | 2022-03-09 07:27 | 2022-03-09 08:30 | 63 | 189 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106976 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10224565 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | MARINE LIGHT NOT WORKING -MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-03-09 07:46 | 2022-03-09 08:46 | 2022-03-10 08:46 | 24 | 2022-03-09 07:55 | 2022-03-09 12:30 | 275 | 75 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10568003 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | DP2 FILTER ALARM |  | FM008 |  | 2022-04-24 03:08 | 2022-04-24 04:08 | 2022-04-25 04:08 | 24 | 2022-04-24 03:17 | 2022-04-24 05:50 | 153 | 188 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68485 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10696046 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM |  | FM008 |  | 2022-05-28 19:06 | 2022-05-28 20:06 | 2022-05-29 20:06 | 24 | 2022-05-28 19:16 | 2022-05-28 20:45 | 89 | 178 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 55709 |  |  | FM10473 | Sreenivasan, Mr. Sribin | N - - - |  | BMS
| CM-2022-10780862 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | DP3 FILTER ALARM T4-08-04 |  | FM008 |  | 2022-06-27 07:53 | 2022-06-27 08:53 | 2022-06-28 08:53 | 24 | 2022-06-27 08:00 | 2022-06-27 10:20 | 140 | 175 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10780863 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU BELT IS DAMAGE T4-08-04 |  | FM008 |  | 2022-06-27 07:53 | 2022-06-27 08:53 | 2022-06-28 08:53 | 24 | 2022-06-27 08:00 | 2022-06-27 11:25 | 205 | 124 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 95217 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10815822 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - T4-08-04 |  | FM008 |  | 2022-07-03 19:53 | 2022-07-03 20:53 | 2022-07-04 20:53 | 24 | 2022-07-03 20:00 | 2022-07-03 23:15 | 195 | 127 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | DUST ACCUMULATION | CLEANED THE SYSTEM | 17053 | 95217 |  |  | FM5381 | JOSEPH THOMAS, Mr. | N - - - |  | Voice Communication
| CM-2022-11064421 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FILTER ALARM |  | FM008 |  | 2022-09-28 10:41 | 2022-09-28 11:41 | 2022-09-29 11:41 | 24 | 2022-09-28 10:50 | 2022-09-28 15:30 | 280 | 105 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 106972 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-11181887 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | V-BELT DAMAGED- T4-08-04 |  | FM008 |  | 2022-11-13 15:24 | 2022-11-13 16:24 | 2022-11-14 16:24 | 24 | 2022-11-13 15:30 | 2022-11-13 17:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106914 | 87807 |  |  | FM5828 | JAYAKRISHNAN GOPALAKRISHNANNAIR, | N - - - |  | Voice Communication
| CM-2023-11825741 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU BELT DAMAGED – T4-08-04 (MECHANICAL ROOM) |  | FM008 |  | 2023-05-27 10:33 | 2023-05-27 11:33 | 2023-05-28 11:33 | 24 | 2023-05-27 10:40 | 2023-05-27 13:00 | 140 | 278 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12040674 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | V BELT DAMAGED, FAHU-A1110-HTR-401, T4-08-04 |  | FM008 |  | 2023-08-01 13:47 | 2023-08-01 14:47 | 2023-08-02 14:47 | 24 | 2023-08-01 13:50 | 2023-08-01 15:20 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 17053 |  |  | FM12342 | Egambaram, Mr. Manikandan | N - - - |  | Voice Communication
| CM-2023-12111116 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS ALARM - FAHU-A1110-HTR-401 T4-08-04 (MECHANICAL ROOM) |  | FM008 |  | 2023-08-24 09:28 | 2023-08-24 10:28 | 2023-08-25 10:28 | 24 | 2023-08-24 09:35 | 2023-08-24 14:00 | 265 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 133396 | 17053 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2022-10988316 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU-A1110-HFT-401 DP2 FILTER ALARM |  | FM008 |  | 2022-08-31 15:10 | 2022-08-31 16:10 | 2022-09-01 16:10 | 24 | 2022-08-31 15:20 | 2022-08-31 15:45 | 25 | 50 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 68060 | 55709 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11065412 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY MOTOR BELT DAMAGED |  | FM008 |  | 2022-09-30 19:11 | 2022-09-30 20:11 | 2022-10-01 20:11 | 24 | 2022-09-30 19:20 | 2022-09-30 20:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68485 | 95217 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-11064228 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY V-BELT DAMAGED -AIR HANDLING UNIT 206-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-09-30 10:32 | 2022-09-30 11:32 | 2022-10-01 11:32 | 24 | 2022-09-30 10:40 | 2022-09-30 13:15 | 155 | 155 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 95217 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-11226556 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY MORTAR BELT DAMAGED – T4-08-04 |  | FM008 |  | 2022-11-29 00:22 | 2022-11-29 01:22 | 2022-11-30 01:22 | 24 | 2022-11-29 00:30 | 2022-11-29 02:30 | 120 | 240 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 17053 |  |  | FM7396 | Biswajit Chowdhury, | N - - - |  | Voice Communication
| CM-2023-12015257 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FAHU-A1110-HTR-401 PDIS1- DUST FILTER STATUS ALARM |  | FM008 |  | 2023-07-28 11:16 | 2023-07-28 12:16 | 2023-07-29 12:16 | 24 | 2023-07-28 11:20 | 2023-07-28 13:35 | 135 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 68485 | 17053 |  |  | FM10302 | Thomas J K | N - - - |  | BMS
| CM-2023-12067030 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS ALARM - T4-08-04 (MECHANICAL ROOM) |  | FM008 |  | 2023-08-12 14:07 | 2023-08-12 15:07 | 2023-08-13 15:07 | 24 | 2023-08-12 14:15 | 2023-08-12 17:50 | 215 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 132112 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2023-12115229 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY BELT DAMAGED, FAHU-A1110-HTR-401, T4-08-04 |  | FM008 |  | 2023-08-26 08:30 | 2023-08-26 09:30 | 2023-08-27 09:30 | 24 | 2023-08-26 08:35 | 2023-08-26 09:35 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 124475 | 17053 |  |  | FM10649 | Dhanesh Arvindbhai Khalasi, Mr. | N - - - |  | Voice Communication
| CM-2023-12210905 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | BELT DAMAGED |  | FM008 |  | 2023-09-23 00:15 | 2023-09-23 01:15 | 2023-09-24 01:15 | 24 | 2023-09-23 00:20 | 2023-09-23 02:40 | 140 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 95216 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12298875 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 206--FILTER DIRTY t4-08-04 |  | FM008 |  | 2023-10-18 11:05 | 2023-10-18 12:05 | 2023-10-19 12:05 | 24 | 2023-10-18 11:10 | 2023-10-18 12:40 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 77406 | 87807 |  |  | FM12549 | Mr. Manikandan Veera Sundaram, | N - - - |  | Voice Communication
| CM-2023-12363729 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | BELT DAMAGED -AIR HANDLING UNIT 206-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2023-11-07 09:14 | 2023-11-07 10:14 | 2023-11-08 10:14 | 24 | 2023-11-07 09:20 | 2023-11-07 10:40 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | FM12241 | Sathik Ali, Mr. Sameer | N - - - |  | Voice Communication
| CM-2024-12749061 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 206--BELT DAMAGE (T4-08-04) |  | FM008 |  | 2024-03-19 07:53 | 2024-03-19 08:53 | 2024-03-20 08:53 | 24 | 2024-03-19 08:00 | 2024-03-19 12:00 | 240 | 170 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 77406 | 95217 |  |  | FM11231 | Anto Sam Daniel Maria Thayalan, Mr. | N - - - |  | Voice Communication
| CM-2022-11039936 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU FILTER DIRTY - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-09-23 01:54 | 2022-09-23 02:54 | 2022-09-24 02:54 | 24 | 2022-09-23 02:00 | 2022-09-23 04:20 | 140 | 185 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 121959 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-11298511 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FILTER DIRTY - FAHU-A1110-HTR-401 - T4-08-04 |  | FM008 |  | 2022-12-23 01:41 | 2022-12-23 02:41 | 2022-12-24 02:41 | 24 | 2022-12-23 01:45 | 2022-12-23 04:10 | 145 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106973 | 17053 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | BMS
| CM-2023-11353398 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY V BELT DAMAGED – T4-08-04 |  | FM008 |  | 2023-01-07 22:19 | 2023-01-07 23:19 | 2023-01-08 23:19 | 24 | 2023-01-07 22:25 | 2023-01-07 23:55 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 106973 | 17053 |  |  | FM5381 | Thomas, Mr. Joseph | N - - - |  | Voice Communication
| CM-2023-11822562 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS - T4-08-04 |  | FM008 |  | 2023-05-23 10:14 | 2023-05-23 11:14 | 2023-05-24 11:14 | 24 | 2023-05-23 10:21 | 2023-05-23 15:15 | 294 | 187 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 132112 | 17053 |  |  | 10302 | Thomas J K | N - - - |  | BMS
| CM-2023-11842312 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS ALARM - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4THFLR.DDC001.FAHU401.SYSALM.DP2 / |  | FM008 |  | 2023-06-01 14:19 | 2023-06-01 15:19 | 2023-06-02 15:19 | 24 | 2023-06-01 14:25 | 2023-06-01 16:10 | 105 | 130 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | BLOWER FAN FAULTY | REPLACED THE FAN | 95216 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2023-11878604 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | DP1 FILTER ALARM - T4-08-04 (MECHANICAL ROOM) |  | FM008 |  | 2023-06-13 09:59 | 2023-06-13 10:59 | 2023-06-14 10:59 | 24 | 2023-06-13 10:05 | 2023-06-13 16:40 | 395 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17573 | 87807 |  |  | FM10036 | Ali, Mr. Md Lucky | N - - - |  | Voice Communication
| CM-2023-11916671 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU BELT DAMAGED - T4-08-04 |  | FM008 |  | 2023-06-23 21:37 | 2023-06-23 22:37 | 2023-06-24 22:37 | 24 | 2023-06-23 21:41 | 2023-06-23 23:10 | 89 | 267 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 105233 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12200335 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY AIR HUMIDITY HI LEVEL ALARM - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4THFLR.DDC001.FAHU401.SYSALM.RHAL2 / |  | FM008 |  | 2023-09-20 11:59 | 2023-09-20 12:59 | 2023-09-21 12:59 | 24 | 2023-09-20 12:05 | 2023-09-20 17:05 | 300 | 115 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | BMS COMMUNICATION ERROR | REPAIRED | 95216 | 87807 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2024-12570988 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FAHU-HTR-A1110-401 FILTER DIRTY - T4-08-04 |  | FM008 |  | 2024-01-18 10:42 | 2024-01-18 11:42 | 2024-01-19 11:42 | 24 | 2024-01-18 10:50 | 2024-01-18 14:20 | 210 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 106914 | 17053 |  |  | FM12342 | Manikandan Egambaram, | N - - - |  | Voice Communication
| CM-2023-12256308 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS ALARM - T4-08-04 (MECHANICAL ROOM) - PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4THFLR.DDC001.FAHU401.SYSALM.DP2 / |  | FM008 |  | 2023-10-07 13:32 | 2023-10-07 14:32 | 2023-10-08 14:32 | 24 | 2023-10-07 13:40 | 2023-10-07 20:00 | 380 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | WARNING | FILTER STATUS ALARM | REPLACED FILTER | 119320 | 87807 |  |  | FM11814 | Arunachalam, Mr. Ayyappan | N - - - |  | BMS
| CM-2024-12849713 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | BELT DAMAGE - AIR HANDLING UNIT 206-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2024-04-24 03:12 | 2024-04-24 04:12 | 2024-04-25 04:12 | 24 | 2024-04-24 03:20 | 2024-04-24 05:50 | 150 | 276 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 119320 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-12250381 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU CABIN LAMP FAULTY - T4-08-04 (MECHANICAL ROOM) |  | FM008 |  | 2023-10-02 12:58 | 2023-10-02 13:58 | 2023-10-03 13:58 | 24 | 2023-10-02 13:05 | 2023-10-02 15:35 | 150 | 300 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 105233 | 87807 |  |  | FM10039 | Kothandapani, Mr. Perumalraja | N - - - |  | Voice Communication
| CM-2022-10225315 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS FAHU-A1110-HTR-401 |  | FM008 |  | 2022-03-08 13:39 | 2022-03-08 14:39 | 2022-03-09 14:39 | 24 | 2022-03-08 13:47 | 2022-03-08 14:30 | 43 | 86 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 68060 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10107678 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU BELT IS DAMAGED - FAHU-A1110-HTR-401 - T4-08-04 |  | FM008 |  | 2022-02-04 19:19 | 2022-02-04 20:19 | 2022-02-05 20:19 | 24 | 2022-02-04 19:29 | 2022-02-04 22:30 | 181 | 170 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17573 | 17053 |  |  | FM3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2022-10325710 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS FAHU-A1110-HTR-401 T4-08-04 PROJECT8.LOGICALVIEW:LOGICAL.BAC3.A1110.4THFLR.DDC001.FAHU401.SYSALM.DP2 / Apr/04/2022 9:10:58 AM |  | FM008 |  | 2022-04-04 14:55 | 2022-04-04 15:55 | 2022-04-05 15:55 | 24 | 2022-04-04 15:05 | 2022-04-04 16:05 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | AIR FILTER DAMAGED | REPLACED THE AIR FILTER | 94953 | 17053 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | E-mail
| CM-2022-11181864 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FAHU-A1110-HTR-401- AHU CABIN LAMP NOT FUNCTIONING |  | FM008 |  | 2022-11-13 13:21 | 2022-11-13 14:21 | 2022-11-14 14:21 | 24 | 2022-11-13 13:30 | 2022-11-13 17:20 | 230 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | MARINE LIGHT NOT WORKING | REPLACED THE LIGHT | 94953 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-11298388 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | BELT DAMAGED-AIR HANDLING UNIT 206-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-12-22 13:36 | 2022-12-22 14:36 | 2022-12-23 14:36 | 24 | 2022-12-22 13:40 | 2022-12-22 15:00 | 80 | 160 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17336 | 17053 |  |  | fm3093 | Rafeeq, Mr. Mohamed | N - - - |  | Voice Communication
| CM-2023-11958342 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FILTER ALARM - FAHU-A1110-HTR-401 - HARRODS TEA |  | FM008 |  | 2023-07-07 12:56 | 2023-07-07 13:56 | 2023-07-08 13:56 | 24 | 2023-07-07 13:05 | 2023-07-07 18:00 | 295 | 185 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOT WORKING | AIR FILTER BLOCKED | CLEANED/REPLACED THE FILTER | 17573 | 87807 |  |  | FM7367 | Advincula, Mr. Eugene Velasco | N - - - |  | Voice Communication
| CM-2022-10032939 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY FAN BELT DAMAGED - HARRODS TEA |  | FM008 |  | 2022-01-09 02:24 | 2022-01-09 03:24 | 2022-01-10 03:24 | 24 | 2022-01-09 02:33 | 2022-01-09 03:33 | 60 | 180 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17053 | 55709 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2022-10276085 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | PDIS1- DUST FILTER STATUS -T4-08-04 |  | FM008 |  | 2022-03-24 14:29 | 2022-03-24 15:29 | 2022-03-25 15:29 | 24 | 2022-03-24 14:35 | 2022-03-24 17:50 | 195 | 65 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 17333 | 55709 |  |  | FM10302 | Kuriyalasheri, Mr. Thomas Joseph | N - - - |  | BMS
| CM-2022-10653440 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT 206-AIRSIDE-MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 BELT DAMAGED - T4-08-04 |  | FM008 |  | 2022-05-12 00:13 | 2022-05-12 01:13 | 2022-05-13 01:13 | 24 | 2022-05-12 00:20 | 2022-05-12 01:50 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17154 | 17053 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | Voice Communication
| CM-2022-10655748 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | DP2 & DP3 FILTER ALARM |  | FM008 |  | 2022-05-13 19:15 | 2022-05-13 20:15 | 2022-05-14 20:15 | 24 | 2022-05-13 19:20 | 2022-05-13 21:15 | 115 | 230 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | LOW AIR PRESSURE | SENSOR FAULTY | REPAIRED/REPLACED | 68060 | 17053 |  |  | FM10118 | Puthiyaveettil Beeran, Mr. Shabeer | N - - - |  | BMS
| CM-2022-10669901 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | DP2 FILTER ALARM |  | FM008 |  | 2022-05-19 09:34 | 2022-05-19 10:34 | 2022-05-20 10:34 | 24 | 2022-05-19 09:43 | 2022-05-19 12:30 | 167 | 125 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | NOISY | ABNORMAL VIBRATION OF EQUIPMENT DUE TO LOOSE PART OR SYSTEM COMPONENT | RESTORE AN ITEM TO ITS ORIGINAL APPEARANCE OR STATE | 68060 | 55709 |  |  | FM9970 | Ansari, Mr. Mohammad Shakir Asif | N - - - |  | Voice Communication
| CM-2022-10737806 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | SUPPLY FAN MOTOR BELT IS DAMAGED |  | FM008 |  | 2022-06-12 14:55 | 2022-06-12 15:55 | 2022-06-13 15:55 | 24 | 2022-06-12 15:00 | 2022-06-12 16:05 | 65 | 130 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 68060 | 87807 |  |  | FM10162 | Janakiram, Mr. Puvaneshwar | N - - - |  | BMS
| CM-2022-10826127 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU BELT CRACKED - MAIN TERMINAL BUILDING-FOURTH FLOOR AREA 008 |  | FM008 |  | 2022-07-10 11:07 | 2022-07-10 12:07 | 2022-07-11 12:07 | 24 | 2022-07-10 11:15 | 2022-07-10 12:15 | 60 | 120 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 121959 | 95217 |  |  | FM5829 | SUNDAR JOHN BOSCO SOOSAI MANICKAM, | N - - - |  | Voice Communication
| CM-2023-11606083 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AHU V -BELT DAMAGED -T4-08-04 |  | FM008 |  | 2023-03-28 19:23 | 2023-03-28 20:23 | 2023-03-29 20:23 | 24 | 2023-03-28 19:30 | 2023-03-28 21:00 | 90 | 180 | 2 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DAMAGED | BELT DAMAGE | REPLACED THE BELT | 17333 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11603432 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | AIR HANDLING UNIT FILTER IS DIRTY |  | FM008 |  | 2023-03-29 03:44 | 2023-03-29 04:44 | 2023-03-30 04:44 | 24 | 2023-03-29 03:50 | 2023-03-29 05:50 | 120 | 185 | 3 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 68060 | 87807 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication
| CM-2023-11933335 | ASD-MTB-FOF008-AHU206 | AIR HANDLING UNIT-05 | FILTER DIRTY -T4-08-04 |  | FM008 |  | 2023-06-27 18:57 | 2023-06-27 19:57 | 2023-06-28 19:57 | 24 | 2023-06-27 19:05 | 2023-06-27 22:10 | 185 | 277 | 4 | HVAC |  | Closed | Normal | FOURTH FLOOR AREA 008 | N | DIRTY | AIR FILTER IS DIRTY | CLEANED THE FILTER | 106914 | 17053 |  |  | FM1227 | Mathramkode Chandran , Mr. Binesh | N - - - |  | Voice Communication